## Chart Summary
Chart Summary
Boiler Size | Fuel | NOx | PM | SO2 | CO | VOC | Status
>250 mmbtu | Solid | Done | Done | Done | Done | Done | Done
| Liquid | [5 empty] | Not Done
| Gas | Done |  |  |  |  | Don't Do
100-250 mmbtu | Solid | Done
Liquid
| Gas | Done (2)
<100 mmbtu | Solid | Done
| Liquid | Done
| Gas | Done (2)
Boiler Size | Fuel | NOx | PM | SO2 | CO | VOC | Trend
>250 mmbtu | Solid | Down | Down | Up | Down | Down | Up
| Liquid | [5 empty] | Down
| Gas | Down |  |  |  |  | Flat
100-250 mmbtu | Solid | Up
Liquid
| Gas | Down
<100 mmbtu | Solid | Flat
| Liquid | Down
| Gas | Flat

## Data->250 MMBTU Gas Boilers
RBLCID | FACILITYNAME | CORPORATEORCOMPANYNAME | FACILITYSTATE | AGENCYNAME | PERMITDATE | FACILITYDESCRIPTION | PROCESSNAME | PROCTYPE | FUEL | THRUPUT | THRUPUTUNIT | PROCESSNOTES | POLLUTANT | CONTROLCOD | CTRLDESC | EMISLIMIT1 | EMISLIMIT1UNIT | EMISLIMIT1AVGTIMECONDITION | PCTEFFIC | EMISLIMIT2 | EMISLIMIT2UNIT | EMISLIMIT2AVGTIMECONDITION | STDEMISSLIMIT | STDUNITLIMIT | STDLIMITAVGTIMECONDITION | POLLUTANTCOMPLIANCENOTES
MO-0051 | PROCTOR & GAMBLE PAPER PRODUCTS | Proctor & Gamble Paper Products | MO | MISSOURI DNR, AIR POLL CONTROL PROGRAM | 1998-01-01 | SANITARY TISSUE & TOWEL BUSINESS, EXPANSION TO EXISTING DIAPER MANUFACTURING PLANT | TISSUE / PAPER MACHINES, (4), PROCESS HEATER | 11.31 |  | 2286.4 | MMCF/YR | ADDITIONAL THROUGHPUT INFORMATION: 261 MMBTU/HR, EACH LOW NOX NATURAL GAS FIRED-BURNERS, GOOD COMBUSTION - P2 APPLIES TO ALL POLL. LIMITS FOR CO AND NOX ONLY. | Nitrogen Oxides (NOx) | P | LOW NOX NATURAL GAS FIRED BURNERS, GOOD COMBUSTION. | 0.115 | LB/MMBTU | [5 empty] | 0.115 | LB/MMBTU
TX-0259 | FREEPORT COGENERATION FACILITY | BASF CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-06-26 | CONSTRUCTION OF A COGENERATION UNIT | BOILER, B-20C | 11.39 | H2-WASTE & NAT GAS | 325 | MMBTU/H |  | Nitrogen Oxides (NOx) | N | NONE INDICATED | 24.38 | LB/H | COMBINATION H2 & NAT GAS |  | 106.76 | T/YR |  | 0.06 | LB/MMBTU | WHEN FIRING NAT GAS | THE EMISSION LIMIT WHEN FIRING A COMBINATION H2- WASTE AND NAT GAS IS 0.075 LB/MMBTU.
LA-0119 | LAKE CHARLES REFINERY | CONOCO INC. | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1999-08-12 | PERMIT TO IMPLEMENT THE PETROZUATA SYNCRUDE PROJECT, ALLOWING REFINERY TO PROCESS A MIXTURE OF VIRGIN CRUDE AND CUTTER STOCK. SECURES A GUARANTEED CRUDE SUPPLY AND INCREASE PRODUCTION OF HEAVY PRODUCTS. MODIFICATION TO VARIOUS PROCESS UNITS WILL BE REQUIR | NO. 3 CTU HEATER (H-1101) | 11.39 | FUEL GAS | 264 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 25.7 | LB/H* | HOURLY MAXIMUM |  | 93.7 | T/YR* | ANNUAL MAXIMUM | 0.081 | LB/MMBTU* |  | *AS SET BY PSD-LA-584(M-3), DATED SEPTEMBER 20, 2002. PSD-LA-584(M-2) ORIGINALLY ESTABLISHED LIMITS AT 0.06 LB/MMBTU, 15.8 LB/H (HOURLY MAXIMUM), AND 69.2 T/YR (ANNUAL MAXIMUM).
LA-0119 | LAKE CHARLES REFINERY | CONOCO INC. | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1999-08-12 | PERMIT TO IMPLEMENT THE PETROZUATA SYNCRUDE PROJECT, ALLOWING REFINERY TO PROCESS A MIXTURE OF VIRGIN CRUDE AND CUTTER STOCK. SECURES A GUARANTEED CRUDE SUPPLY AND INCREASE PRODUCTION OF HEAVY PRODUCTS. MODIFICATION TO VARIOUS PROCESS UNITS WILL BE REQUIR | NO. 3 CTU HEATER (H-1101) | 11.39 | FUEL GAS | 264 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 25.7 | LB/H* | HOURLY MAXIMUM |  | 93.7 | T/YR* | ANNUAL MAXIMUM | 0.081 | LB/MMBTU* |  | *AS SET BY PSD-LA-584(M-3), DATED SEPTEMBER 20, 2002. PSD-LA-584(M-2) ORIGINALLY ESTABLISHED LIMITS AT 0.06 LB/MMBTU, 15.8 LB/H (HOURLY MAXIMUM), AND 69.2 T/YR (ANNUAL MAXIMUM).
TX-0429 | VALERO REFINING CO. - TEXAS CITY | VALERO REFINING CO. - TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-02-23 | SITE IS A PETROLEUM REFINERY DESIGNED TO PROCESS CRUDE OIL INTO A VARIETY OF GASOLINES, DIESELS (INCLUDING LOW-S), AND DISTILLATE OILS | DUCT BURNERS | 11.39 | NATURAL GAS | 251 | mmbtu/h | FRESH AIR FIRING MODE AT 251 MMBTU/H OR 112 MMBTU/H WITH TURBINE EXHAUST FIRING MODE. | Nitrogen Oxides (NOx) | N |  | 0.1 | LB/MMBTU | [5 empty] | 0.1 | LB/MMBTU
NM-0042 | DEMING ENERGY FACILITY | DUKE ENERGY LUNA | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2000-12-29 | THIS FACILITY WILL GENERATE APPROXIMATELY 640 MW (NOMINAL). IT WILL BE A COMBINED CYCLE FACILITY CONSISTING OF 2 GENERAL ELECTRIC PG7241 (FA) COMBUSTION TURBINES, 2 DUCT BURNERS, AN AUXILIARY BOILER, AND A COOLING TOWER. THE NOX FROM THE COMBUSTION TURBIN | DB-1 & DB-2 DUCT BURNER | 11.31 | NATURAL GAS | 517 | MMBTU/H | DB-1 AND DB-2 EMISSION LIMITS ARE FOR COMBINED DUCT BURNER/TURBINE OPERATION (LIMITS APPLY TO EACH BURNER) The DUCT BURNERS USED TO GENERATE MORE HEAT IN THE TURBINE EXHAUST STREAM. | Nitrogen Oxides (NOx) | P | SELECTIVE CATALYTIC REDUCTION (SCR) AND DLN COMBUSTION | 7.3 | LB/H |  | 62 |  |  |  | 0.007 | LB/MMBTU
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORI | COMBINED ANNUAL EMISSIONS, AF-01, CF-01 THRU GF-01 | 11.39 |  |  |  | THE BURNING RATE OF THE FOLLOWING FURNACES SHALL NOT EXCEED 350 MMBTU/H AVERAGED OVER AN OPERATING DAY: AF-01, CF-01, DF-01, EF-01, FF-01, AND GF-01. THE COMBINED BURNING RATE OF FURNACE AF-01 AND FURNACES CF-01 THRU GF-01 SHALL NOT EXCEED 1518 MMBTU/H AV | Nitrogen Oxides (NOx) | N | NONE INDICATED | 268.7 | LB/H | COMBINED |  | 650 | T/YR | COMBINED |  |  | SEE ENTRIES FOR EACH UNIT
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORI | FURNACE AF-01 | 11.39 | ETHANE | 350 | MMBTU/H | FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% ETHANE/PROPANE MIXTURE. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 62 | LB/H |  |  | 133.8 | T/YR |  | 0.177 | LB/MMBTU | HOURLY AV, SEE NOTES | FROM FURNACES AF-01, CF-01, DF-01, EF-01, FF-01, GF-01: NOX EMISSIONS SHALL BE LIMITED TO 0.1 LB/MMBTU WHEN CRACKING LIQUID FEEDSTOCKS AND 0.13 LB/MMBTU WHEN CRACKING GASEOUS FEEDSTOCKS AS A ROLLING 12 MO AVE. NOX LIMITS ARE NOT APPLICABLE WHEN THE CRACKI
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORI | FURNACE BF-01 | 11.39 | ETHANE | 339 | MMBTU/H | 280 MMBTU/H AV. FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% ETHANE/PROPANE MIXTURE. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 33.9 | LB/H |  |  | 98.2 | T/YR |  | 0.1 | LB/MMBTU | HOURLY AV, SEE NOTES | FROM FURNACES AF-01, CF-01, DF-01, EF-01, FF-01, GF-01: NOX EMISSIONS SHALL BE LIMITED TO 0.1 LB/MMBTU WHEN CRACKING LIQUID FEEDSTOCKS AND 0.13 LB/MMBTU WHEN CRACKING GASEOUS FEEDSTOCKS AS A ROLLING 12 MO AVE. NOX LIMITS ARE NOT APPLICABLE WHEN THE CRACKI
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORI | FURNACE CF-01 | 11.39 | ETHANE | 350 | MMBTU/H | FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% ETHANE/PROPANE MIXTURE. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 62 | LB/H |  |  | 143.5 | T/YR |  | 0.177 | LB/MMBTU | HOURLY AV, SEE NOTES | FROM FURNACES AF-01, CF-01, DF-01, EF-01, FF-01, GF-01: NOX EMISSIONS SHALL BE LIMITED TO 0.1 LB/MMBTU WHEN CRACKING LIQUID FEEDSTOCKS AND 0.13 LB/MMBTU WHEN CRACKING GASEOUS FEEDSTOCKS AS A ROLLING 12 MO AVE. NOX LIMITS ARE NOT APPLICABLE WHEN THE CRACKI
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORI | FURNACE DF-01 | 11.39 | ETHANE | 350 | MMBTU/H | FEEDSTOCK FOR THE FURNACE IS USUALLY ETHANE OR A 70%/30% ETHANE/PROPANE MIXTURE. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 62 | LB/H |  |  | 125.8 | T/YR |  | 0.177 | LB/MMBTU | HOURLY AV, SEE NOTES | FROM FURNACES AF-01, CF-01, DF-01, EF-01, FF-01, GF-01: NOX EMISSIONS SHALL BE LIMITED TO 0.1 LB/MMBTU WHEN CRACKING LIQUID FEEDSTOCKS AND 0.13 LB/MMBTU WHEN CRACKING GASEOUS FEEDSTOCKS AS A ROLLING 12 MO AVE. NOX LIMITS ARE NOT APPLICABLE WHEN THE CRACKI
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORI | FURNACE EF-01 | 11.39 | ETHANE | 350 | MMBTU/H | FEEDSTOCK FOR THE FURNACES IS USALLY ETHANE OR A 70%/30% ETHANE/PROPANE MIXTURE. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 62 | LB/H |  |  | 123.6 | T/YR |  | 0.177 | LB/MMBTU | HOURLY AV | FROM FURNACES AF-01, CF-01, DF-01, EF-01, FF-01, GF-01: NOX EMISSIONS SHALL BE LIMITED TO 0.1 LB/MMBTU WHEN CRACKING LIQUID FEEDSTOCKS AND 0.13 LB/MMBTU WHEN CRACKING GASEOUS FEEDSTOCKS AS A ROLLING 12 MO AVE. NOX LIMITS ARE NOT APPLICABLE WHEN THE CRACKI
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORI | FURNACE FF-01 | 11.39 | ETHANE | 350 | MMBTU/H | FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% ETHANE/PROPANE MIXTURE. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 62 | LB/H |  |  | 161.1 | T/YR |  | 0.177 | LB/MMBTU | HOURLY AVERAGE | FROM FURNACES AF-01, CF-01, DF-01, EF-01, FF-01, GF-01: NOX EMISSIONS SHALL BE LIMITED TO 0.1 LB/MMBTU WHEN CRACKING LIQUID FEEDSTOCKS AND 0.13 LB/MMBTU WHEN CRACKING GASEOUS FEEDSTOCKS AS A ROLLING 12 MO AVE. NOX LIMITS ARE NOT APPLICABLE WHEN THE CRACKI
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORI | FURNACE GF-01 | 11.39 | ETHANE | 350 | MMBTU/H | FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% ETHANE/PROPANE MIXTURE. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 62 | LB/H |  |  | 161.1 | T/YR |  | 0.177 | LB/MMBTU | HOURLY AV | FROM FURNACES AF-01, CF-01, DF-01, EF-01, FF-01, GF-01: NOX EMISSIONS SHALL BE LIMITED TO 0.1 LB/MMBTU WHEN CRACKING LIQUID FEEDSTOCKS AND 0.13 LB/MMBTU WHEN CRACKING GASEOUS FEEDSTOCKS AS A ROLLING 12 MO AVE. NOX LIMITS ARE NOT APPLICABLE WHEN THE CRACKI
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORI | (2) FURNACES, IF-01 & JF-01 | 11.39 | ETHANE | 341 | MMBTU/H, MAXIMUM | 299 MMBTU/H HOURLY AV THROUGHPUT. FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% ETHANE/PROPANE MIXTURE. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 40.9 | LB/H | EACH |  | 78.5 | T/YR | EACH | 0.06 | LB/MMBTU | ROLLING 12 MO. AV, EACH, SEE NOTES | ADDITIONAL LIMITS OF: 0.12 LB/MMBTU ON AN HOURLY AVERAGE, AND 0.06 LB/MMBTU ROLLING 12 MO AVE. NOX LIMITS ARE NOT APPLICABLE WHEN THE CRACKING FURNACE IS IN ITS DECOKING CYCLE; HOWEVER THE NOX MASS EMISSIONS RATES SPECIFIED SHALL NOT BE EXCEEDED WHEN THE
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORI | FURNACE OF-01 | 11.39 | ETHANE | 300 | MMBTU/H | FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% ETHANE/PROPANE MIXTURE. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 24 | LB/H |  |  | 78.8 | T/YR |  | 0.08 | LB/MMBTU | HOURLY BASIS | ADDITIONAL LIMITS OF: 0.065 LB/MMBTU 12 MO ROLLING AV. NOX LIMITS ARE NOT APPLICABLE WHEN THE CRACKING FURNACE IS IN ITS DECOKING CYCLE; HOWEVER THE NOX MASS EMISSIONS RATES SPECIFIED SHALL NOT BE EXCEEDED WHEN THE FURNACE IS IN ITS DECOKING CYCLE.
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORI | FURNACE QF-01 | 11.39 | ETHANE | 300 | MMBTU/H | 265 MMBTU/H AV. FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% ETHANE/PROPANE MIXTURE. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 24 | LB/H |  |  | 78.8 | T/YR |  | 0.08 | LB/MMBTU | HOURLY BASIS | ADDITIONAL LIMITS OF 0.068 LB/MMBTU ROLLING 12- MO AV. NOX LIMITS ARE NOT APPLICABLE WHEN THE CRACKING FURNACE IS IN ITS DECOKING CYCLE; HOWEVER THE NOX MASS EMISSIONS RATES SPECIFIED SHALL NOT BE EXCEEDED WHEN THE FURNACE IS IN ITS DECOKING CYCLE.
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORI | (6) FURNACES, XAF-01 THRU XFF-01 | 11.39 | ETHANE | 333 | MMBTU/H | FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% ETHANE/PROPANE MIXTURE. THE COMBINED BURNING RATE SHALL NOT EXCEED 1822 MMBTU/H ON A ROLLING 12-MO AV. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 26.64 | LB/H | EACH |  | 399.1 | T/YR | COMBINED | 0.08 | LB/MMBTU | EACH, SEE NOTES | ADDITONAL LIMITS OF 0.08 LB/MMBTU AS AN HOURLY AVERAGE AND 0.05 LB/MMBTU ROLLING 12-MO AV. NOX LIMITS ARE NOT APPLICABLE WHEN THE CRACKING FURNACE IS IN ITS DECOKING CYCLE; HOWEVER THE NOX MASS EMISSIONS RATES SPECIFIED SHALL NOT BE EXCEEDED WHEN THE FURN
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORI | FURNACE XGF-01 | 11.39 | ETHANE | 502 | MMBTU/H | 481 MMBUT/H IS THE HOURLY AVERAGE THROUGHPUT. FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% ETHANE/PROPANE MIXTURE. | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS, STAGED AIR COMBUSTION, FLUE GAS RECIRCULATION, STEAM INJECTION | 40.1 | LB/H |  |  | 126.4 | T/YR |  | 0.08 | LB/MMBTU | HOURLY BASIS | ADDITONAL LIMITS OF 0.06 LB/MMBTU AS A 12-MO ROLLING AV. NOX LIMITS ARE NOT APPLICABLE WHEN THE CRACKING FURNACE IS IN ITS DECOKING CYCLE; HOWEVER THE NOX MASS EMISSIONS RATES SPECIFIED SHALL NOT BE EXCEEDED WHEN THE FURNACE IS IN ITS DECOKING CYCLE.
SC-0061 | COLUMBIA ENERGY LLC | COLUMBIA ENERGY LLC | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 2001-04-09 | ELECTRIC COGENERATION POWER PLANT SUPPLYING STEAM AND ENERGY, A EASTMAN CHEMICAL CO. | BOILERS, NATURAL GAS (2) | 11.31 | NATURAL GAS | 350 | MMBTU/H (EACH) |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS, FLUE GAS RECIRCULATION, GOOD COMBUSTION PRACTICES | 14 | LB/H | [5 empty] | 0.04 | LB/MMBTU
LA-0166 | ORION REFINING CORP (NOW VALERO) | ORION REFINING CORP (NOW VALERO) | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-01-10 | PETROLEUM REFINERY, 190,000 BARRELS PER DAY TOTAL DESIGN THROUGHPUT. REFINERY OPTIMIZATION PROJECT INCLUDING NEW EQUIPMENT, PHYSICAL MODIFICATIONS, CHANGES IN THE METHOD OF OPERATIONS, CAPACITY INCREASES DUE TO DEBOTTLENECKING AND THE INCORPORATION OF 86 | HEATER F-72-703 | 11.39 | REFINERY FUEL GAS | 528 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNER | 41.7 | LB/H |  |  | 183 | T/YR |  | 0.079 | LB/MMBTU
LA-0174 | PORT HUDSON OPERATIONS | GEORGIA-PACIFIC CORPORATION | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-01-25 | PULP MILL | POWER BOILER NO. 5 | 11.31 | NATURAL GAS | 987 | MMBTU/H | EMISSION POINT NO. 27. | Nitrogen Oxides (NOx) | P | LOW-NOX BURNERS | 127.19 | LB/H |  |  | 230.24 | T/YR |  | 0.1 | LB/MMBTU
LA-0174 | PORT HUDSON OPERATIONS | GEORGIA-PACIFIC CORPORATION | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-01-25 | PULP MILL | COMBINATION BOILER NO. 1 | 11.9 | WOOD WASTE / NAT GAS | 459.5 | MMBTU/H | EMISSION POINT NO. 5. FUEL CAN BE EITHER WOOD WASTE OR NATURAL GAS. | Nitrogen Oxides (NOx) | P | LOW-NOX BURNERS | 128.7 | LB/H |  |  | 235.74 | T/YR |  | 0.1 | LB/MMBTU | WHEN FIRING NATURAL GAS | BACT, USING LOW-NOX BURNERS, IS 0.10 LB/MMBTU WHEN FIRING NATURAL GAS AND 0.30 LB/MMBTU WHEN FIRING WOOD WASTE.
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF TH | BOILER NO. 13 | 11.39 |  | 366.83 | MMBTU/H | EMISSION POINT NO. BOILER-13. UNIT WILL BE SHUTDOWN. | Nitrogen Oxides (NOx) | N |  | 29.3 | LB/H |  |  | 128.5 | T/YR |  | 0.08 | LB/MMBTU | CALCULATED
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF TH | BOILERS 14 AND 15 | 11.39 | PETRO REFIN GAS | 586 | MMBTU/H EA | BOTH BOILERS WILL BE SHUT DOWN. | Nitrogen Oxides (NOx) | N |  | 46.9 | LB/H | EACH |  | 205.3 | T/YR | EACH | 0.08 | LB/MMBTU | EACH, CALCULATED
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF TH | BOILER NO. 13 | 11.39 |  | 366.83 | MMBTU/H | EMISSION POINT NO. BOILER-13. UNIT WILL BE SHUTDOWN. | Nitrogen Oxides (NOx) | N |  | 29.3 | LB/H |  |  | 128.5 | T/YR |  | 0.08 | LB/MMBTU | CALCULATED
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF TH | BOILERS 14 AND 15 | 11.39 | PETRO REFIN GAS | 586 | MMBTU/H EA | BOTH BOILERS WILL BE SHUT DOWN. | Nitrogen Oxides (NOx) | N |  | 46.9 | LB/H | EACH |  | 205.3 | T/YR | EACH | 0.08 | LB/MMBTU | EACH, CALCULATED
VA-0255 | VA POWER - POSSUM POINT | Virginia Power | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-11-18 | THIE PERMIT WAS AMENDED AND APPROVED ON 11/18/2002 FROM THE PERMIT THAT WAS DATED 10/05/2001. | BOILER, TANGENTIALLY-FIRED, UNIT 4 | 11.31 | NATURAL GAS | 2350 | MMBTU/H | Tangentially-fired boiler (unit 4) converted from coal to natural gas only. | Nitrogen Dioxide (NO2) | P | LOW NITROGEN CONTENT FUEL AND GOOD COMBUSTION PRACTICES. | 3066 | T/YR | [5 empty] | 0.3 | LB/MMBTU
VA-0255 | VA POWER - POSSUM POINT | Virginia Power | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-11-18 | THIE PERMIT WAS AMENDED AND APPROVED ON 11/18/2002 FROM THE PERMIT THAT WAS DATED 10/05/2001. | DUCT BURNERS | 11.31 | NATURAL GAS | 385 | MMBTU/H | DUCT BURNERS IN THE HEAT RECOVERY STEAM GENERATOR OF EACH GE 7F1 COMBUSTION TURBINE. | Nitrogen Dioxide (NO2) | N |  | 0.2 | LB/MMBTU |  |  | 1.6 | LB/MW | GROSS ENERGY OUTPUT | 0.2 | LB/MMBTU
VA-0255 | VA POWER - POSSUM POINT | Virginia Power | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-11-18 | THIE PERMIT WAS AMENDED AND APPROVED ON 11/18/2002 FROM THE PERMIT THAT WAS DATED 10/05/2001. | BOILER, TANGENTIALLY-FIRED, UNIT 3 | 11.31 | NATURAL GAS | 1150 | MMBTU/H | Tangentially-fired boiler (unit 3)converted from coal to natural gas only. | Nitrogen Oxides (NOx) | P | LOW NOX CONTENT FUEL AND LOW NOX BURNERS. | 3066 | T/YR | [5 empty] | 0.61 | LB/MMBTU
MN-0054 | MANKATO ENERGY CENTER |  | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2003-12-04 | COMBINED CYCLE GAS TURBINE ELECTRIC POWER PLANT. TWO IDENTICAL GE FRAME F7A GAS TURBINES EACH WITH HRSG W/DUCT BURNERS FEEDING STEAM TO COMMON STEAM TURBINES. PRIMARY FUEL IS NG, NO. 2 VERY LOW SULFUR DISTILLATE OIL FOR BACKUP. ALSO, AUX. BOILER, DIESEL E | DUCT BURNER, 2 EACH | 11.31 | NATURAL GAS | 800 | MMBTU/H | RESTRICTED TO NG ONLY | Nitrogen Oxides (NOx) | A | SCR | 3 | PPMVD @15% 02 | 3-HOUR AVG | [6 empty] | NOT AVAILABLE | LIMIT APPLIES TO COMBINED EMISSIONS FROM GAS FIRED TURBINE AND DUCT BURNER
OR-0039 | COB ENERGY FACILITY, LLC | Peoples Energy Resources | OR | OREGON DEPT OF ENVIRONMENTAL QUALITY | 2003-12-30 | POWER GENERATION FACILITY | DUCT BURNERS, NATURAL GAS, (4) | 11.31 | NATURAL GAS | 654 | MMBTU/H | Throughput for each. | Nitrogen Dioxide (NO2) | B | DLN COMBUSTORS AND SCR | 200 | NG/J | [5 empty] | 0.47 | LB/MMBTU | calculated
OH-0269 | BIOMASS ENERGY, LLC-SOUTH POINT POWER | BIOMASS ENERGY | OHIO ENVIRONMENTAL PROTECTION AGENCY |  | 2004-01-05 | SEVEN BOILERS PURCHASED FROM AN ETHANOL PLANT, REBUILT TO BURN WOOD AND TO GENERATE POWER, USING WOOD WASTE. | AUXILIARY BOILER, NATURAL GAS | 11.31 | NATURAL GAS | 247 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 14.82 | LB/H | WITH NATURAL GAS |  | 27.02 | T/YR | WITH NATURAL GAS AND FUEL OIL | 0.06 | LB/MMBTU | WITH NATURAL GAS | LIMITS ARE FOR NATURAL GAS, EXCEPT: 27.02 T/YR IS TOTAL FOR AUXILIARY BOILER, ALL FUELS
NE-0026 | NUCOR STEEL DIVISION | NUCOR STEEL CORP. | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2004-06-22 |  | NNI REHEAT FURNACE | 11.31 | NATURAL GAS | 133 | MMBTU/H |  | Nitrogen Oxides (NOx) | A | ULTRA-LOW NOX BURNERS | 0.096 | LB/MMBTU | [5 empty] | 0.096 | LB/MMBTU
TX-0481 | AIR PRODUCTS BAYTOWN I I | AIR PRODUCTS LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2004-11-02 | THIS FACILITY GETS RAW SYNTHESIS GAS FROM EXXON’S SYNTHESIS GAS MANUFACTURING UNIT. THE RAW SYNGAS STREAM FROM THE EXXON PLANT, CONSISTING OF CO2, CO, H2, H2S, COS, HCN, NH3 AND METHANE, IS PIPED TO THE AIR PRODUCTS PLANT WHERE THE ACID GASES AND AMMONIA | BOILER STACK | 11.39 | NATURAL GAS |  |  | CO EMISSIONS ARE ELIGIBLE FOR PSD | Nitrogen Oxides (NOx) | N |  | 6 | LB/H |  |  | 9.21 | T/YR
TX-0481 | AIR PRODUCTS BAYTOWN I I | AIR PRODUCTS LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2004-11-02 | THIS FACILITY GETS RAW SYNTHESIS GAS FROM EXXON’S SYNTHESIS GAS MANUFACTURING UNIT. THE RAW SYNGAS STREAM FROM THE EXXON PLANT, CONSISTING OF CO2, CO, H2, H2S, COS, HCN, NH3 AND METHANE, IS PIPED TO THE AIR PRODUCTS PLANT WHERE THE ACID GASES AND AMMONIA | BOILER STACK (HIGH BTU FUEL) | 11.39 |  |  |  |  | Nitrogen Oxides (NOx) | N |  | 21 | LB/H
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | OIL REFINERY | STEAM BOILERS NOS. 1 AND 2 | 11.31 | NATURAL GAS | 419 | MMBTU/H | EQUIPMENT IDENTIFIED BY ID #S S-20110 AND S-20120 | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 0.0125 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.0125 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | OIL REFINERY | STEAM BOILERS NOS. 1 AND 2 | 11.31 | NATURAL GAS | 419 | MMBTU/H | EQUIPMENT IDENTIFIED BY ID #S S-20110 AND S-20120 | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 0.0125 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.0125 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | OIL REFINERY | ATMOSPHERIC CRUDE CHARGE HEATER | 11.39 | NATURAL GAS OR REFINERY FUEL GAS | 346 | MMBTU/H | THIS UNIT IS IDENTIFIED AS EQUIPMENT # B-01300 | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS AND SELECTIVE CATALYTIC REDUCTION | 0.0125 | LB/MMBTU | THREE-HOUR ROLLING AVERAGE |  |  |  |  | 0.0125 | LB/MMBTU | THREE-HOUR ROLLING AVERAGE | THE INITIAL LIMIT FOR NOX IS 0.0125 LB PER MMBTU HEAT INPUT (HHV). AFTER THE FIRST 24 MONTHS, A NEW LIMIT IS TO BE ESTABLISHED BASED ON THE PERFORMANCE OF THE UNIT. A LIMIT OF 0.006 LB PER MMBTU MAY BE TAKEN WITHOUT REGARD TO THE UNIT PERFORMANCE.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | OIL REFINERY | BUTANE CONVERSION UNIT DEHYDROGENATION REACTOR CHARGE HEATER | 11.39 | REFINERY FUEL GAS OR NATURAL GAS | 311 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY ID # B-15310 | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS AND SELECTIVE CATALYTIC REDUCTION | 0.0125 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.0125 | LB/MMBTU |  | THE INITIAL LIMIT FOR NOX IS 0.0125 LB PER MMBTU HEAT INPUT (HHV). AFTER THE FIRST 24 MONTHS, A NEW LIMIT IS TO BE ESTABLISHED BASED ON THE PERFORMANCE OF THE UNIT. A LIMIT OF 0.006 LB PER MMBTU MAY BE TAKEN WITHOUT REGARD TO THE UNIT PERFORMANCE.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | OIL REFINERY | BUTANE CONVERSION UNIT DEHYDROGENATION REACTOR INTERHEATER | 11.39 | REFINERY FULE GAS OR NATURAL GAS | 328 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY ID # B-15320 | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS AND SELECTIVE CATALYTIC REDUCTION | 0.0125 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.0125 | LB/MMBTU |  | THE INITIAL LIMIT FOR NOX IS 0.0125 LB PER MMBTU HEAT INPUT (HHV). AFTER THE FIRST 24 MONTHS, A NEW LIMIT IS TO BE ESTABLISHED BASED ON THE PERFORMANCE OF THE UNIT. A LIMIT OF 0.006 LB PER MMBTU MAY BE TAKEN WITHOUT REGARD TO THE UNIT PERFORMANCE.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | OIL REFINERY | HYDROGEN REFORMER HEATER | 11.39 | REFINERY FUEL GAS OR NATURAL GAS | 1435 | MMBTU/H | EQUIPMENT IDENTIFIED BY ID # B-07200 | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS AND SELECTIVE CATALYTIC REDUCTION | 0.0125 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.0125 | LB/MMBTU |  | THE INITIAL LIMIT FOR NOX IS 0.0125 LB PER MMBTU HEAT INPUT (HHV). AFTER THE FIRST 24 MONTHS, A NEW LIMIT IS TO BE ESTABLISHED BASED ON THE PERFORMANCE OF THE UNIT. A LIMIT OF 0.006 LB PER MMBTU MAY BE TAKEN WITHOUT REGARD TO THE UNIT PERFORMANCE.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | OIL REFINERY | ATMOSPHERIC CRUDE CHARGE HEATER | 11.39 | NATURAL GAS OR REFINERY FUEL GAS | 346 | MMBTU/H | THIS UNIT IS IDENTIFIED AS EQUIPMENT # B-01300 | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS AND SELECTIVE CATALYTIC REDUCTION | 0.0125 | LB/MMBTU | THREE-HOUR ROLLING AVERAGE |  |  |  |  | 0.0125 | LB/MMBTU | THREE-HOUR ROLLING AVERAGE | THE INITIAL LIMIT FOR NOX IS 0.0125 LB PER MMBTU HEAT INPUT (HHV). AFTER THE FIRST 24 MONTHS, A NEW LIMIT IS TO BE ESTABLISHED BASED ON THE PERFORMANCE OF THE UNIT. A LIMIT OF 0.006 LB PER MMBTU MAY BE TAKEN WITHOUT REGARD TO THE UNIT PERFORMANCE.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | OIL REFINERY | BUTANE CONVERSION UNIT DEHYDROGENATION REACTOR CHARGE HEATER | 11.39 | REFINERY FUEL GAS OR NATURAL GAS | 311 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY ID # B-15310 | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS AND SELECTIVE CATALYTIC REDUCTION | 0.0125 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.0125 | LB/MMBTU |  | THE INITIAL LIMIT FOR NOX IS 0.0125 LB PER MMBTU HEAT INPUT (HHV). AFTER THE FIRST 24 MONTHS, A NEW LIMIT IS TO BE ESTABLISHED BASED ON THE PERFORMANCE OF THE UNIT. A LIMIT OF 0.006 LB PER MMBTU MAY BE TAKEN WITHOUT REGARD TO THE UNIT PERFORMANCE.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | OIL REFINERY | BUTANE CONVERSION UNIT DEHYDROGENATION REACTOR INTERHEATER | 11.39 | REFINERY FULE GAS OR NATURAL GAS | 328 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY ID # B-15320 | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS AND SELECTIVE CATALYTIC REDUCTION | 0.0125 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.0125 | LB/MMBTU |  | THE INITIAL LIMIT FOR NOX IS 0.0125 LB PER MMBTU HEAT INPUT (HHV). AFTER THE FIRST 24 MONTHS, A NEW LIMIT IS TO BE ESTABLISHED BASED ON THE PERFORMANCE OF THE UNIT. A LIMIT OF 0.006 LB PER MMBTU MAY BE TAKEN WITHOUT REGARD TO THE UNIT PERFORMANCE.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | OIL REFINERY | HYDROGEN REFORMER HEATER | 11.39 | REFINERY FUEL GAS OR NATURAL GAS | 1435 | MMBTU/H | EQUIPMENT IDENTIFIED BY ID # B-07200 | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS AND SELECTIVE CATALYTIC REDUCTION | 0.0125 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.0125 | LB/MMBTU |  | THE INITIAL LIMIT FOR NOX IS 0.0125 LB PER MMBTU HEAT INPUT (HHV). AFTER THE FIRST 24 MONTHS, A NEW LIMIT IS TO BE ESTABLISHED BASED ON THE PERFORMANCE OF THE UNIT. A LIMIT OF 0.006 LB PER MMBTU MAY BE TAKEN WITHOUT REGARD TO THE UNIT PERFORMANCE.
WA-0301 | BP CHERRY POINT REFINERY | BRITISH PETROLEUM | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2005-04-20 | BRITISH PETROLEUM (BP), FORMERLY KNOWN AS ARCO PRODUCTS COMPANY OPERATES A REFINERY AT CHERRY POINT NEAR BLAINE, WASHINGTON. THE REFINERY IS LOCATED IN A RURAL SETTING NEAR BLAINE AND BIRCH BAY WASHINGTON. THE SURROUNDING LAND USE IS ZONED HEAVY IMPACT IN | BOILER, NATURAL GAS | 11.31 | NATURAL GAS | 363 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULNB + FGR | 10.1 | LB/H | CALENDAR DAY | 75 |  |  |  | 0.028 | LB/MMBTU | CALCULATED | ORIGINAL PERMIT LIMITED NOX EMISSIONS TO 11 PPMVD, 24-HR AVG, @ 7% O2. ORIGINAL PERMIT LIMITED NOX EMISSIONS TO 0.018 LB/MMBTU, 24-HR AVG. THE AMENDED PERMIT HAS ELIMINATED THESE CONCENTRATION & MASS PER UNIT OF HEAT INPUT-BASED BACT LIMITS.
TX-0478 | CITGO CORPUS CHRISTI REFINERY - WEST PLANT | CITGO REFINING AND CHEMICALS COMAPNY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-04-20 |  | DHT STRIPPER REBOILER | 11.39 | REFINERY FUEL GAS |  |  | THE MDH UNIT REMOVES ORGANIC NITROGEN AND SULFUR FROM THE FEED STREAMS. FEEDSTOCK IS MIXED WITH HYDROGEN , HEATED, AND FED TO A REACTOR. A CATALYTIC REACTION CONVERTS THE ORGANIC SULFUR TO HYDROGEN SULFIDE AND THE NITROGEN COMPOUNDS TO AMMONIA. THE EFFLUE | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS | 3 | LB/H |  |  | 12.2 | T/YR |  |  | LB/MMBTU
TX-0478 | CITGO CORPUS CHRISTI REFINERY - WEST PLANT | CITGO REFINING AND CHEMICALS COMAPNY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-04-20 |  | NO.3 BOILER | 11.39 | REFINERY FUEL GAS | 99 | MMBTU/H | UTILITY BOILER 3 PRODUCES IS A 99 MMBTU/H HEAT INPUT BOILER FIRING REFINERY FUEL GAS WHICH IS USED TO PRODUCE STEAM FOR USE IN A NUMBER OF REFINERY PROCESSES. | Nitrogen Oxides (NOx) | N |  | 11.9 | LB/H |  |  | 52 | T/YR |  | 0.1202 | LB/MMBTU
TX-0475 | FORMOSA POINT COMFORT PLANT | FORMOSA PLASTICS CORPORATION TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-09 |  | PYROLYSIS FURNACES (1001-1008, 1009 B) | 11.39 | FUEL GAS | 250 | MMBtu/h | EMISSIONS ARE BASED ON EACH FURNANCE | Nitrogen Oxides (NOx) | B | THE PYROLYSIS FURNACES WILL USE INTERNAL FLUE GAS RECIRCULATION (IFGR) AND STAGED FUEL GAS ULTRA LOW-NOX BURNERS TO CONTROL NOX EMISSIONS. THE BURNER TECHNOLOGY INSTALLED WILL USE THE FUEL GAS MOMENTUM TO INSPIRATE HOT FLUE | 30.3 | LB/H |  |  | 132.71 | T/YR |  | 0.1212 | LB/MMBTU
TX-0475 | FORMOSA POINT COMFORT PLANT | FORMOSA PLASTICS CORPORATION TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-09 |  | PYROLYSIS FURNACE (1054-1056) | 11.39 | FUEL GAS | 250 | mmbtu/h |  | Nitrogen Oxides (NOx) | B | THE PYROLYSIS FURNACES WILL USE INTERNAL FLUE GAS RECIRCULATION (IFGR) AND STAGED FUEL GAS ULTRA LOW-NOX BURNERS TO CONTROL NOX EMISSIONS. THE BURNER TECHNOLOGY INSTALLED WILL USE THE FUEL GAS MOMENTUM TO INSPIRATE HOT FLUE | 20.02 | LB/H |  |  | 720.54 | T/YR |  | 0.08008 | LB/MMBTU
TX-0475 | FORMOSA POINT COMFORT PLANT | FORMOSA PLASTICS CORPORATION TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-09 |  | PYROLYSIS FURNACE (1057-1062, 1091) | 11.39 | FUEL GAS | 250 | MMBTU/h |  | Nitrogen Oxides (NOx) | B | THE PYROLYSIS FURNACES WILL USE INTERNAL FLUE GAS RECIRCULATION (IFGR) AND STAGED FUEL GAS ULTRA LOW-NOX BURNERS TO CONTROL NOX EMISSIONS. THE BURNER TECHNOLOGY INSTALLED WILL USE THE FUEL GAS MOMENTUM TO INSPIRATE HOT FLUE | 19.29 | LB/H |  |  | 720.54 | T/YR |  | 0.07716 | LB/MMBTU
TX-0475 | FORMOSA POINT COMFORT PLANT | FORMOSA PLASTICS CORPORATION TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-09 |  | PYROLYSIS FURNACE (N1011-1012) | 11.39 |  | 250 | MMBTU/H |  | Nitrogen Oxides (NOx) | B | THE PYROLYSIS FURNACES WILL USE INTERNAL FLUE GAS RECIRCULATION (IFGR) AND STAGED FUEL GAS ULTRA LOW-NOX BURNERS TO CONTROL NOX EMISSIONS. THE BURNER TECHNOLOGY INSTALLED WILL USE THE FUEL GAS MOMENTUM TO INSPIRATE HOT FLUE | 18.75 | LB/H |  |  | 65.7 | T/YR |  | 0.075 | LB/MMBTU
LA-0192 | CRESCENT CITY POWER | CRESENT CITY POWER, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-06-06 | NEW 600 MW NATURAL GAS-FIRED COMBINED CYCLE POWER PLANT | DUCT BURNERS (2) | 11.31 |  | 759 | MMBTU/H |  | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS AND SELECTIVE CATLYTIC REDUCTION (SCR) ADD-ON CONTROLS | 8.2 | LB/H | HOURLY MAXIMUM |  | 35.9 | T/YR | ANNUAL MAXIMUM | 0.010804 | LB/MMBTU | NOT AVAILABLE | STARTUP/SHUTDOWN (SU/SD) RATES HAVE ALSO BEEN ESTABLISHED FOR THE COMBINED TURBINE/DUCT BURNER STREAM. NOX IS LIMITED TO 220 LB/HR DURING SU. FACILITY-WIDE SU/SD EMISSIONS OF NOX (FROM 2 TURBINES AND 2 DUCT BURNERS) ARE ALSO LIMITED TO 74.33 TPY.
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | A & B CRUDE HEATERS (1-08 & 2-08) & COKER CHARGE HEATER (15-08) | 11.39 | REFINERY FUEL GAS |  |  | 1-08: 368.40 MM BTU/H 2-08: 368.40 MM BTU/H 15-08: 480.1 MM BTU/H | Nitrogen Oxides (NOx) | B | ULTRA LOW NOX BURNERS (ULNB) AND SELECTIVE CATALYTIC REDUCTION (SCR VOLUNTARY) | [7 empty] | 0.0125 | LB/MMBTU | ANNUAL AV
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | HYDROGEN REFORMER FURNACE FLUE GAS VENT (48-08) | 11.39 | PURGE GAS | 1412.5 | MMBTU/H | AVG. HEAT INPUT: 1130.0 MM BTU/H PURGE GAS: 813.6 MMBTU/H TRIM GAS: 316.4 MMBTU/H | Nitrogen Oxides (NOx) | B | ULTRA LOW NOX BURNERS (ULNB) AND SELECTIVE CATALYTIC REDUCTION (SCR VOLUNTARY) | [7 empty] | 0.0125 | LB/MMBTU | ANNUAL AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | PLATFORMER HEATER CELLS NO. 1-3 (7A-08, 7B-08, & 7C-08) & HCU FRACTIONATOR HEATER (13-08) | 11.39 | REFINERY FUEL GAS |  |  | 7A-08: 474 MM BTU/H 7B-08: 542.4 MM BTU/H 7C-08: 333.8 MM BTU/H 13-08: 361.26 MM BTU/H | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS (ULNB) WITHOUT AIR PREHEAT | [7 empty] | 0.03 | LB/MMBTU | ANNUAL AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | BOILER NO. 1 (16-08) | 11.39 | REFINERY FUEL GAS | 525.7 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS (ULNB) & FLUE GAS RECIRCULATION (FGR) | [7 empty] | 0.2 | LB/MMBTU | ANNUAL AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | A & B CRUDE HEATERS (1-08 & 2-08) & COKER CHARGE HEATER (15-08) | 11.39 | REFINERY FUEL GAS |  |  | 1-08: 368.40 MM BTU/H 2-08: 368.40 MM BTU/H 15-08: 480.1 MM BTU/H | Nitrogen Oxides (NOx) | B | ULTRA LOW NOX BURNERS (ULNB) AND SELECTIVE CATALYTIC REDUCTION (SCR VOLUNTARY) | [7 empty] | 0.0125 | LB/MMBTU | ANNUAL AV
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | HYDROGEN REFORMER FURNACE FLUE GAS VENT (48-08) | 11.39 | PURGE GAS | 1412.5 | MMBTU/H | AVG. HEAT INPUT: 1130.0 MM BTU/H PURGE GAS: 813.6 MMBTU/H TRIM GAS: 316.4 MMBTU/H | Nitrogen Oxides (NOx) | B | ULTRA LOW NOX BURNERS (ULNB) AND SELECTIVE CATALYTIC REDUCTION (SCR VOLUNTARY) | [7 empty] | 0.0125 | LB/MMBTU | ANNUAL AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | PLATFORMER HEATER CELLS NO. 1-3 (7A-08, 7B-08, & 7C-08) & HCU FRACTIONATOR HEATER (13-08) | 11.39 | REFINERY FUEL GAS |  |  | 7A-08: 474 MM BTU/H 7B-08: 542.4 MM BTU/H 7C-08: 333.8 MM BTU/H 13-08: 361.26 MM BTU/H | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS (ULNB) WITHOUT AIR PREHEAT | [7 empty] | 0.03 | LB/MMBTU | ANNUAL AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | BOILER NO. 1 (16-08) | 11.39 | REFINERY FUEL GAS | 525.7 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS (ULNB) & FLUE GAS RECIRCULATION (FGR) | [7 empty] | 0.2 | LB/MMBTU | ANNUAL AVERAGE
*LA-0213 | ST. CHARLES REFINERY | VALERO REFINING - NEW ORLEANS, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2007-02-08 | PETROLEUM REFINERY. PROJECT INVOLVES INCREASE IN CAPACITY FROM 220,000 TO 380,000 BARRELS PER DAY. | HEATERS 2004-7 & 8, 2005-1, 2, 3, 15, 16, 19, 20, 22, 30, 31, 33, 34; REBOILERS 2005-10, 11, 13, 25, 26, 28; BOILERS 2004-11 & 2005-21 | 11.39 | REFINERY FUEL GAS |  |  | 2004-7: 885 MM BTU/HR 2004-8: 885 MM BTU/HR 2004-11: 525 MM BTU/HR 2005-1: 1274 MM BTU/HR 2005-2: 744 MM BTU/HR 2005-3: 555 MM BTU/HR 2005-10: 308 MM BTU/HR 2005-11: 393 MM BTU/HR 2005-13: 255 MM BTU/HR 2005-15: 479 MM BTU/HR 2005-16: 278 MM BTU/HR 2005-1 | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 0.04 | LB/MMBTU | THREE 1-HOUR TEST AVERAGE |  |  |  |  | 0.04 | LB/MMBTU
*LA-0213 | ST. CHARLES REFINERY | VALERO REFINING - NEW ORLEANS, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2007-02-08 | PETROLEUM REFINERY. PROJECT INVOLVES INCREASE IN CAPACITY FROM 220,000 TO 380,000 BARRELS PER DAY. | BOILERS B-401C & D (94-43 & 94-45) | 11.39 | REFINERY FUEL GAS | 461 | MM BTU/H EA. | SOURCES ALSO BURN NATURAL GAS. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 36.84 | LB/H | HOURLY MAXIMUM |  | 107.57 | T/YR | ANNUAL MAXIMUM | 0.08 | LB/MMBTU
*LA-0213 | ST. CHARLES REFINERY | VALERO REFINING - NEW ORLEANS, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2007-02-08 | PETROLEUM REFINERY. PROJECT INVOLVES INCREASE IN CAPACITY FROM 220,000 TO 380,000 BARRELS PER DAY. | BOILERS B-401C & D (94-43 & 94-45) | 11.39 | REFINERY FUEL GAS | 461 | MM BTU/H EA. | SOURCES ALSO BURN NATURAL GAS. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 36.84 | LB/H | HOURLY MAXIMUM |  | 107.57 | T/YR | ANNUAL MAXIMUM | 0.08 | LB/MMBTU
*LA-0213 | ST. CHARLES REFINERY | VALERO REFINING - NEW ORLEANS, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2007-02-08 | PETROLEUM REFINERY. PROJECT INVOLVES INCREASE IN CAPACITY FROM 220,000 TO 380,000 BARRELS PER DAY. | HEATERS 2004-7 & 8, 2005-1, 2, 3, 15, 16, 19, 20, 22, 30, 31, 33, 34; REBOILERS 2005-10, 11, 13, 25, 26, 28; BOILERS 2004-11 & 2005-21 | 11.39 | REFINERY FUEL GAS |  |  | 2004-7: 885 MM BTU/HR 2004-8: 885 MM BTU/HR 2004-11: 525 MM BTU/HR 2005-1: 1274 MM BTU/HR 2005-2: 744 MM BTU/HR 2005-3: 555 MM BTU/HR 2005-10: 308 MM BTU/HR 2005-11: 393 MM BTU/HR 2005-13: 255 MM BTU/HR 2005-15: 479 MM BTU/HR 2005-16: 278 MM BTU/HR 2005-1 | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 0.04 | LB/MMBTU | THREE 1-HOUR TEST AVERAGE |  |  |  |  | 0.04 | LB/MMBTU
*MS-0086 | CHEVRON PRODUCTS COMPANY, PASCAGOULA REFINERY | CHEVRON PRODUCTS COMPANY | MS | MISSISSIPPI DEPT OF ENV QUALITY | 2007-05-08 | PETROLEUM REFINERY AND PETROCHEMICALS | FOUR PLATFORMER FEED/INTERSTAGE HEATER WITH A COMMON STACK | 11.39 | REFINERY FUEL GAS | 850 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW-NOX BURNERS | 38.25 | LB/H | 3-HR AVERAGE |  | 111.69 | T/YR | 12-MONTH ROLLING AVERAGE | 0.03 | LB/MMBTU | 12-MONTH ROLLING AVERAGE
IA-0088 | ADM CORN PROCESSING - CEDAR RAPIDS | ARCHER DANIELS MIDLAND | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-06-29 | CONSISTS OF THREE DISTINCT OPERATIONS: CORN WET MILL, CORN DRY MILL AND BOILERHOUSE | NATURAL GAS BOILER (292.5 MMBTU/H) | 11.31 | NATURAL GAS | 292.5 | MMBTU/H | THE PROJECT INCLUDES THE CONSTRUCTION OF TWO IDENTICAL 292.5 MMBTU/HR NATURAL GAS FIRED BOILERS. PERMITS 07-A-579-P AND 07-A-580-P. | Nitrogen Oxides (NOx) | B | ADVANCED ULTRA LOW NOX BURNERS WITH FLUE GAS RECIRCULATIONS AND GOOD COMBUSTION PRACTICES. | 0.02 | LB/MMBTU | 30-DAY ROLLING AVERAGE/ EXCEPT SSM |  | 25.62 | T/Y | 12-MONTH ROLLING TOTAL/ ALL TIMES | 0.02 | LB/MMBTU

## Data- >250 MMBTU Solid Fuel
RBLCID | FACILITYNAME | CORPORATEORCOMPANYNAME | FACILITYSTATE | AGENCYNAME | PERMITDATE | FACILITYDESCRIPTION | PROCESSNAME | PROCTYPE | FUEL | THRUPUT | THRUPUTUNIT | PROCESSNOTES | POLLUTANT | CONTROLCOD | CTRLDESC | EMISLIMIT1 | EMISLIMIT1UNIT | EMISLIMIT1AVGTIMECONDITION | PCTEFFIC | EMISLIMIT2 | EMISLIMIT2UNIT | EMISLIMIT2AVGTIMECONDITION | STDEMISSLIMIT | STDUNITLIMIT | STDLIMITAVGTIMECONDITION | POLLUTANTCOMPLIANCENOTES
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, JTA | 11.12 | HULLS | 280 | MMBTU/H |  | Particulate Matter (PM) | A | ESP | 0.24 | LB/MMBTU | [5 empty] | 0.24 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | NORTH DAKOTA STATE DEPARTMENT OF HEALTH |  | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, JTA | 11.12 | HULLS | 280 | MMBTU/H |  | Particulate Matter (PM) | A | ESP | 0.24 | LB/MMBTU | [5 empty] | 0.24 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND |  | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, JTA | 11.12 | HULLS | 280 | MMBTU/H |  | Particulate Matter (PM) | A | ESP | 0.24 | LB/MMBTU | [5 empty] | 0.24 | LB/MMBTU
PR-0007 | COGENERATION PLANT (AES-PRCP) | AES PUERTO RICO | PR | PUERTO RICO ENV QUALITY BOARD, AIR PROGRAM | 2001-10-29 | COGENERATION UNIT | 2 COAL-FIRED CIRCULATING FLUIDIZED BED BOILERS | 11.11 | BITUMINOUS COAL | 454 | MW (NET) | COMBINED MAX HEAT INPUT 4922.7 MMBTU/H @ 105% MAX CONTINUOUS RATING (MCR) AND CAPABLE OF GENERATING 1.8 E 6 LB/H OF STEAM @ 2400 PSIG AND 1000 DEGREES F. WILL SUPPLY SUPERHEATED STEAM TO 2 EXTRACTION CONDENSING TURBINES AND SUPPLY PROCESS STEAM OF UP TO 290000 LB/H | Particulate Matter < 10 μ (PM10) | A | ELECTROSTATIC PRECIPITATOR | 73.8 | LB/H | SEE POLLUTANT NOTES |  |  |  |  | 0.03 | LB/MMBTU | SEE POLLUTANT NOTES | THE NEW PM10 LIMITS INDICATED ABOVE BECAME EFFECTIVE ON AUGUST 10, 2004. PREVIOUS LIMITS WERE 36.9 LB/H AND 0.015 LB/MMBTU. THE LIMITS WERE CHANGED BASED ON STACK TEST RESULTS.
VA-0268 | THERMAL VENTURES | MARTINSVILLE THERMAL, LLC | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. |  | 2002-02-15 | STEAM PRODUCTION FACILITY | BOILER, STEAM | 11.11 | COAL | 120 | MMBTU/H | In order to meet the annual emission limitations included in this permit, the wood/coal mixture shall not exceed 30% coal by BTU content on an annual basis. Average annual heat content 13,000 Btu/lb HHV. Average sulfur content per shipment 0.9% and averag | Particulate Matter (PM) | P | GOOD COMBUSTION PRACTICES, CLEAN BURNING FUEL, AND CONTINUOUS EMISSION MONITORING DEVICE. | 0.15 | LB/MMBTU |  |  | 78.8 | T/YR |  | 0.15 | LB/MMBTU
VA-0268 | THERMAL VENTURES | MARTINSVILLE THERMAL, LLC | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. |  | 2002-02-15 | STEAM PRODUCTION FACILITY | BOILER, STEAM | 11.11 | COAL | 120 | MMBTU/H | In order to meet the annual emission limitations included in this permit, the wood/coal mixture shall not exceed 30% coal by BTU content on an annual basis. Average annual heat content 13,000 Btu/lb HHV. Average sulfur content per shipment 0.9% and averag | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES, CLEAN BURNING FUEL, AND CONTINUOUS EMISSION MONITORING DEVICE. | 0.14 | LB/MMBTU |  |  | 73.6 | T/YR |  | 0.14 | LB/MMBTU
MT-0022 | BULL MOUNTAIN, NO. 1, LLC - ROUNDUP POWER PROJECT | BULL MOUNTAIN DEV. COMPANY | MT |  | 2003-07-21 | COAL FIRED POWER PLANT | BOILER, PC NO. 1 | 11.11 | COAL | 390 | MW | Additional throughput: 4013 mmbtu/h - full load heat input. Stack tests & inspections are required by the permit after construction/operation of the facility. Calculations will be used in the future also . Calculations were the primary factor considered d | Particulate Matter < 10 μ (PM10) | A | FABRIC FILTERS | 60.2 | LB/H |  | 99.82 | 0.015 | LB/MMBTU |  | 0.015 | LB/MMBTU |  | Based on testing, Roundup Power is required to determine the feasibility of changing this limit to 48.2 lb/h (0.012 lb/mmbtu) based on a rolling 24-h average
MT-0022 | BULL MOUNTAIN, NO. 1, LLC - ROUNDUP POWER PROJECT | BULL MOUNTAIN DEV. COMPANY | MT |  | 2003-07-21 | COAL FIRED POWER PLANT | BOILER, PC NO. 2 | 11.11 | COAL | 390 | MW | Stack tests and inspections are required by the permit after construction/operation of the facility. Calculations will be used in the future also. Calculations were the primary factor considered during the permitting process. | Particulate Matter < 10 μ (PM10) | A | FABRIC FILTERS | 60.2 | LB/H |  | 99.82 | 0.015 | LB/MMBTU |  | 0.015 | LB/MMBTU
AR-0074 | PLUM POINT ENERGY | PLUM POINT ASSOCIATES, LLC | AR |  | 2003-08-20 |  | BOILER , UNIT 1 - SN-01 | 11.11 | SUB-BITUMINOUS COAL | 800 | MW | THE BOILER IS A 550-800 MW PULVERIZED COAL FIRED BOILER. | Particulate Matter < 10 μ (PM10) | A | BAGHOUSE | 0.018 | LB/MMBTU | [5 empty] | 0.018 | LB/MMBTU
AR-0079 | PLUM POINT ENERGY | PLUM POINT ASSOCIATES, LLC | AR |  | 2003-08-20 | PLUM POINT ENERGY ASSOCIATES, LLC (PERMITTEE) PROPOSES TO CONSTRUCT AND OPERATE A NOMINAL 550-800 MW COAL FIRED GENERATING STATION | BOILER - SN-01 | 11.11 | SUB-BITUMINOUS COAL | 800 | MW | THE BOILER IS A 550-800 MW PULVERIZED COAL FIRED BOILER. | Particulate Matter < 10 μ (PM10) | A | BAGHOUSE | 0.018 | LB/MMBTU | [5 empty] | 0.018 | LB/MMBTU
GA-0114 | INLAND PAPERBOARD AND PACKAGING, INC. - ROME LINERBOARD MILL | TEMPLE INLAND, INC. | GA |  | 2004-10-13 | THIS FACILITY MANUFACTURES UNBLEACHED KRAFT LINERBOARD. | BOILER, COAL FIRED | 11.11 | COAL | 565 | MMBTU/H | MODIFICATION TO A 1962 BOILER | Particulate Matter < 10 μ (PM10) | A | ESP | 0.05 | LB/MMBTU | [5 empty] | 0.05 | LB/MMBTU
GA-0114 | INLAND PAPERBOARD AND PACKAGING, INC. - ROME LINERBOARD MILL | TEMPLE INLAND, INC. | GA |  | 2004-10-13 | THIS FACILITY MANUFACTURES UNBLEACHED KRAFT LINERBOARD. | BOILER, SOLID FUEL | 11.12 | BARK | 856 | MMBTU/H | BARK, WASTEWATER SLUDGE, TDF, FUEL OIL; MAY BE USED TO INCIENRATE NCG GASES; NEW BOILER | Particulate Matter < 10 μ (PM10) | A | ESP | 0.025 | LB/MMBTU | [5 empty] | 0.025 | LB/MMBTU
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | ELECTRICAL UTILITY | SUPER CRITICAL PULVERIZED COAL ELECTRIC STEAM BOILER (S04, P04) | 11.11 | PRB COAL | 5173.07 | MMBTU/H | 500 MW CAPACITY, BASE LOAD OPERATION (30% TO 100% CAPACITY) BACKUP / STARTUP FUEL, NATURAL GAS (5.07 CF6) PRB COAL (~0.5 WT. % S MAX., 5.5 WT % ASH); ~ 8100 BTU / LB; 319.3 TPH | Particulate Matter (PM) | B | FABRIC FILTER BAGHOUSE (WHEN FIRING COAL). NATURAL GAS USE (W/O BAGHOUSE) IS LIMITED TO 500 MMBTU/HR. | 0.02 | LB/MMBTU | 3 HR. AVG |  | 103.52 | LB/H | 3 HR. AVG. | 0.02 | LB/MMBTU | NOT AVAILABLE | POLLUTANT MEASUREMENT INCLUDES BACKHALF (METHOD 5 OR 5B + METHOD 202)
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | ELECTRICAL UTILITY | SUPER CRITICAL PULVERIZED COAL ELECTRIC STEAM BOILER (S04, P04) | 11.11 | PRB COAL | 5173.07 | MMBTU/H | 500 MW CAPACITY, BASE LOAD OPERATION (30% TO 100% CAPACITY) BACKUP / STARTUP FUEL, NATURAL GAS (5.07 CF6) PRB COAL (~0.5 WT. % S MAX., 5.5 WT % ASH); ~ 8100 BTU / LB; 319.3 TPH | Particulate Matter < 10 μ (PM10) | B | FABRIC FILTER BAGHOUSE (WHEN FIRING COAL) NATURAL GAS USE (W/O BAGHOUSE) LIMITED TO 500 MMBTU/HR | 0.018 | LB/MMBTU | 3 HOUR AVG. |  |  |  |  | 0.018 | LB/MMBTU | NOT AVAILABLE | INCLUDES BACKHALF
*TX-0499 | SANDY CREEK ENERGY STATION | SANDY CREEK ENERGY ASSOCIATES | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-07-24 | THE PROPOSED SCES IS A GRASSROOTS NEW, 860 MW GROSS (800 MW NET) ELECTRIC OUTPUT, PC BOILER STEAM ELECTRIC GENERATING FACILITY. THE MAXIMUM HEAT INPUT IS 8,185 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTU/HR). ONLY PRELIMINARY ENGINEERING DESIGN HAS BEEN COMPLETED AT THIS TIME AND THE PERMIT APPLICATION NET PLANT EFFICIENCY OF 10,231 BTU/KWHR (HEAT ENERGY INPUT DIVIDED BY NET ELECTRIC ENERGY OUTPUT) WILL NOT BE FINALIZED UNTIL PROJECT FUNDING IS COMPLETE. THE BOILER MAY BE DESIGNED AS A SUBCRITICAL STEAM PRESSURE UNIT, OR A MORE EFFICIENT, HIGHER PRESSURE, SUPERCRITICAL STEAM UNIT. THE ELECTRIC GENERATING PROCESS IS THE STANDARD RANKINE CLOSED CYCLE: BOILER FEEDWATER IS PUMPED, CONVERTED TO STEAM IN THE BOILER, PASSED THROUGH STEAM TURBINES WHICH TURN ELECTRIC GENERATORS, AND CONDENSED IN WATER-COOLED CONDENSERS TO AGAIN BECOME BOILER FEEDWATER. HEAT IS REMOVED FROM THE TURBINE CONDENSERS VIA A WET COOLING TOWER WHICH EVAPORATES TO THE ATMOSPHERE WATER OBTAINED FROM WACO’S MUNICIPAL WASTE WATER TREATMENT FACILITY. | PULVERIZED CAOL BOILER | 11.11 | COAL | 8185 | MMBTU/H | COAL (TYPICALLY 72% CARBON, 0.4% SULFUR, 6% ASH; REMAINDER HYDROGEN, OXYGEN AND NITROGEN) IS RECEIVED FROM RAILCAR, UNLOADED AND STORED IN A LARGE OPEN PILE FOR LONG-TERM STORAGE (INACTIVE PILE), OR IN ONE OF TWO SMALLER PILES FOR MORE IMMEDIATE USE (ACTIVE PILES). FROM THE ACTIVE PILE, COAL IS FED TO SILOS IN THE UPPER BOILER STRUCTURE. THE COAL IS THEN PULVERIZED, BLOWN THROUGH BURNERS, AND COMBUSTED IN THE FIREBOX. | Particulate Matter < 10 μ (PM10) | N |  | 123 | LB/H | 1-HR |  | 327 | LB/H | 30-DAY | 0.015027 | LB/MMBTU
WA-0336 | GRAYS HARBOR PAPER LP |  | WASHINGTON STATE DEPARTMENT OF ECOLOGY |  | 2006-11-17 | GHP IS AN EXISTING PAPER MILL. THE PULP SIDE OF THE MILL WAS SHUT DOWN IN ABOUT 1992 AND LATER REMOVED. EXISTING UNITS INCLUDE WOOD WASTE HOG FUEL BOILERS #6 AND #8, GAS FIRED BOILER #9, AND TWO PAPER MACHINES. THE PROJECT IS TO INSTALL A STEAM TURBINE DR | UTILITY-AND LARGE INDUSTRIAL SIZED BOILERS | 11.12 | WOOD WASTE | 379 | MMBTU/H | RILEY TYPE VO INSTALLED IN 1974. FUELS MOSTLY WOOD WASTE, WITH SOME #6 FUEL OIL. | Particulate Matter < 10 μ (PM10) | A | 1. MULTICLONES WITH 80 14 DIAMETER TUBES. 2. TWO PARALLEL IMPRINGEMENT WET SCRUBBER WITH 6 TOP AND 6 BOTTOM SHOWERS" | 52.5 | LB/H | CALENDAR DAY |  |  |  |  | 0.13852 | LB/MMBTU |  | AREA IS IN ATTAINMENT. THIS PROJECT DID NOT TRIGGER BACT ON THIS GRANDFATHERED HOG FUEL BOILER. INCREASED UTILIZATION TRIGGERED SOME IMPACTS ANALYSIS REQUIREMENT OF PSD FOR NOX, CO, AND PM10. PM10 WAS ONLY POLLUTANT THAT EVEN CAME CLOSE TO CHALLENGING ANY
PA-0204 | KIMBERLY CLARK/CHESTER PLANT | KIMBERLY-CLARK TISSUE COMPANY | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 1998-06-24 | OP INCORPORATES THE EXISTING OP # 23- 306-018 | BOILER, CIRCULATING FLUIDIZED BED | 11.11 | COAL | 799 | MMBTU/H | BOILER LIMITED TO 8400 H/YR OPERATION AND FUEL OIL USAGE OF 170,000 GAL/YR. RACT OP ISSUED FOR NOX AND VOC SOURCES. | Nitrogen Oxides (NOx) | N |  | 1090 | T/YR | Total, 3 Boilers |  |  |  |  | 0.2 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, JTA | 11.12 | HULLS | 280 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 0.2 | LB/MMBTU | [5 empty] | 0.2 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | NORTH DAKOTA STATE DEPARTMENT OF HEALTH |  | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, JTA | 11.12 | HULLS | 280 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 0.2 | LB/MMBTU | [5 empty] | 0.2 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND |  | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, JTA | 11.12 | HULLS | 280 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 0.2 | LB/MMBTU | [5 empty] | 0.2 | LB/MMBTU
PR-0007 | COGENERATION PLANT (AES-PRCP) | AES PUERTO RICO | PR | PUERTO RICO ENV QUALITY BOARD, AIR PROGRAM | 2001-10-29 | COGENERATION UNIT | 2 COAL-FIRED CIRCULATING FLUIDIZED BED BOILERS | 11.11 | BITUMINOUS COAL | 454 | MW (NET) | COMBINED MAX HEAT INPUT 4922.7 MMBTU/H @ 105% MAX CONTINUOUS RATING (MCR) AND CAPABLE OF GENERATING 1.8 E 6 LB/H OF STEAM @ 2400 PSIG AND 1000 DEGREES F. WILL SUPPLY SUPERHEATED STEAM TO 2 EXTRACTION CONDENSING TURBINES AND SUPPLY PROCESS STEAM OF UP TO 290000 LB/H | Nitrogen Oxides (NOx) | A | SELECTIVE NON-CATALYTIC REDUCTION (SNCR) SYSTEM (UREA INJECTION) | 57 | PPMVD @ 7% O2 | [5 empty] | 0.1 | LB/MMBTU
VA-0268 | THERMAL VENTURES | MARTINSVILLE THERMAL, LLC | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. |  | 2002-02-15 | STEAM PRODUCTION FACILITY | BOILER, STEAM | 11.11 | COAL | 120 | MMBTU/H | In order to meet the annual emission limitations included in this permit, the wood/coal mixture shall not exceed 30% coal by BTU content on an annual basis. Average annual heat content 13,000 Btu/lb HHV. Average sulfur content per shipment 0.9% and averag | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICES, CLEAN BURNING FUEL, AND CONTINUOUS EMISSION MONITORING DEVICE. | 0.4 | LB/MMBTU |  |  | 210.2 | T/YR |  | 0.4 | LB/MMBTU
MT-0022 | BULL MOUNTAIN, NO. 1, LLC - ROUNDUP POWER PROJECT | BULL MOUNTAIN DEV. COMPANY | MT |  | 2003-07-21 | COAL FIRED POWER PLANT | BOILER, PC NO. 1 | 11.11 | COAL | 390 | MW | Additional throughput: 4013 mmbtu/h - full load heat input. Stack tests & inspections are required by the permit after construction/operation of the facility. Calculations will be used in the future also . Calculations were the primary factor considered d | Nitrogen Oxides (NOx) | B | LOW NOX BURNER, OVERFIRE AIR, AND SCR. | 280.9 | LB/H | rolling 24 h avg | 90 | 0.07 | LB/MMBTU | rolling 24 h avg | 0.07 | LB/MMBTU |  | incremental cost effectiveness: $1332/t pollutant removed
MT-0022 | BULL MOUNTAIN, NO. 1, LLC - ROUNDUP POWER PROJECT | BULL MOUNTAIN DEV. COMPANY | MT |  | 2003-07-21 | COAL FIRED POWER PLANT | BOILER, PC NO. 2 | 11.11 | COAL | 390 | MW | Stack tests and inspections are required by the permit after construction/operation of the facility. Calculations will be used in the future also. Calculations were the primary factor considered during the permitting process. | Nitrogen Oxides (NOx) | B | LOW NOX BURNER, OVERFIRE AIR, SCR | 280.9 | LB/H | rolling 24 h avg | 90 | 0.07 | LB/MMBTU | rolling 24 h avg | 0.07 | LB/MMBTU |  | Incremental cost effectiveness: $1332/t pollutant removed.
AR-0074 | PLUM POINT ENERGY | PLUM POINT ASSOCIATES, LLC | AR |  | 2003-08-20 |  | BOILER , UNIT 1 - SN-01 | 11.11 | SUB-BITUMINOUS COAL | 800 | MW | THE BOILER IS A 550-800 MW PULVERIZED COAL FIRED BOILER. | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS | 0.09 | LB/MMBTU | [5 empty] | 0.09 | LB/MMBTU
AR-0079 | PLUM POINT ENERGY | PLUM POINT ASSOCIATES, LLC | AR |  | 2003-08-20 | PLUM POINT ENERGY ASSOCIATES, LLC (PERMITTEE) PROPOSES TO CONSTRUCT AND OPERATE A NOMINAL 550-800 MW COAL FIRED GENERATING STATION | BOILER - SN-01 | 11.11 | SUB-BITUMINOUS COAL | 800 | MW | THE BOILER IS A 550-800 MW PULVERIZED COAL FIRED BOILER. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.09 | LB/MMBTU | [5 empty] | 0.09 | LB/MMBTU
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | ELECTRICAL UTILITY | SUPER CRITICAL PULVERIZED COAL ELECTRIC STEAM BOILER (S04, P04) | 11.11 | PRB COAL | 5173.07 | MMBTU/H | 500 MW CAPACITY, BASE LOAD OPERATION (30% TO 100% CAPACITY) BACKUP / STARTUP FUEL, NATURAL GAS (5.07 CF6) PRB COAL (~0.5 WT. % S MAX., 5.5 WT % ASH); ~ 8100 BTU / LB; 319.3 TPH | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS, GOOD COMBUSTION PRACTICES SELECTIVE CATALYTIC REDUCTION (SCR) | 0.07 | LB/MMBTU | 30 DAY AVG. EXCL. STARTUP/SHUTDOWN |  | 0.06 | LB/MMBTU | 12 MO. AVG. INCL. STARTUP / SHUTDOWN | 0.07 | LB/MMBTU |  | COST EFFECTIVENESS BASED ON 30 DAY AVG. VALUE.
*TX-0499 | SANDY CREEK ENERGY STATION | SANDY CREEK ENERGY ASSOCIATES | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-07-24 | THE PROPOSED SCES IS A GRASSROOTS NEW, 860 MW GROSS (800 MW NET) ELECTRIC OUTPUT, PC BOILER STEAM ELECTRIC GENERATING FACILITY. THE MAXIMUM HEAT INPUT IS 8,185 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTU/HR). ONLY PRELIMINARY ENGINEERING DESIGN HAS BEEN COMPLETED AT THIS TIME AND THE PERMIT APPLICATION NET PLANT EFFICIENCY OF 10,231 BTU/KWHR (HEAT ENERGY INPUT DIVIDED BY NET ELECTRIC ENERGY OUTPUT) WILL NOT BE FINALIZED UNTIL PROJECT FUNDING IS COMPLETE. THE BOILER MAY BE DESIGNED AS A SUBCRITICAL STEAM PRESSURE UNIT, OR A MORE EFFICIENT, HIGHER PRESSURE, SUPERCRITICAL STEAM UNIT. THE ELECTRIC GENERATING PROCESS IS THE STANDARD RANKINE CLOSED CYCLE: BOILER FEEDWATER IS PUMPED, CONVERTED TO STEAM IN THE BOILER, PASSED THROUGH STEAM TURBINES WHICH TURN ELECTRIC GENERATORS, AND CONDENSED IN WATER-COOLED CONDENSERS TO AGAIN BECOME BOILER FEEDWATER. HEAT IS REMOVED FROM THE TURBINE CONDENSERS VIA A WET COOLING TOWER WHICH EVAPORATES TO THE ATMOSPHERE WATER OBTAINED FROM WACO’S MUNICIPAL WASTE WATER TREATMENT FACILITY. | PULVERIZED CAOL BOILER | 11.11 | COAL | 8185 | MMBTU/H | COAL (TYPICALLY 72% CARBON, 0.4% SULFUR, 6% ASH; REMAINDER HYDROGEN, OXYGEN AND NITROGEN) IS RECEIVED FROM RAILCAR, UNLOADED AND STORED IN A LARGE OPEN PILE FOR LONG-TERM STORAGE (INACTIVE PILE), OR IN ONE OF TWO SMALLER PILES FOR MORE IMMEDIATE USE (ACTIVE PILES). FROM THE ACTIVE PILE, COAL IS FED TO SILOS IN THE UPPER BOILER STRUCTURE. THE COAL IS THEN PULVERIZED, BLOWN THROUGH BURNERS, AND COMBUSTED IN THE FIREBOX. | Nitrogen Oxides (NOx) | A | AT THIS POINT, THE FLUE GAS HAS BEEN COOLED TO THE APPROPRIATE TEMPERATURE FOR SCR, SO IT NEXT PASSES THROUGH THE SCR REACTOR, WHERE NOX IS REDUCED TO FORM NITROGEN. | 1637 | LB/H | 1-HR |  | 573 | LB/H | 30-DAY | 0.070006 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, JTA | 11.12 | HULLS | 280 | MMBTU/H |  | Sulfur Dioxide (SO2) | N |  | 0.002 | LB/MMBTU | [5 empty] | 0.002 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | NORTH DAKOTA STATE DEPARTMENT OF HEALTH |  | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, JTA | 11.12 | HULLS | 280 | MMBTU/H |  | Sulfur Dioxide (SO2) | N |  | 0.002 | LB/MMBTU | [5 empty] | 0.002 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND |  | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, JTA | 11.12 | HULLS | 280 | MMBTU/H |  | Sulfur Dioxide (SO2) | N |  | 0.002 | LB/MMBTU | [5 empty] | 0.002 | LB/MMBTU
PR-0007 | COGENERATION PLANT (AES-PRCP) | AES PUERTO RICO | PR | PUERTO RICO ENV QUALITY BOARD, AIR PROGRAM | 2001-10-29 | COGENERATION UNIT | 2 COAL-FIRED CIRCULATING FLUIDIZED BED BOILERS | 11.11 | BITUMINOUS COAL | 454 | MW (NET) | COMBINED MAX HEAT INPUT 4922.7 MMBTU/H @ 105% MAX CONTINUOUS RATING (MCR) AND CAPABLE OF GENERATING 1.8 E 6 LB/H OF STEAM @ 2400 PSIG AND 1000 DEGREES F. WILL SUPPLY SUPERHEATED STEAM TO 2 EXTRACTION CONDENSING TURBINES AND SUPPLY PROCESS STEAM OF UP TO 290000 LB/H | Sulfur Dioxide (SO2) | B | LOW-SULFUR COAL (MAX 1% S) AND DISTILLATE OIL (MAX 0.05% S)AND A LIMESTONE INJECTION SYSTEM AND CIRCULATING DRY SCRUBBER | 9 | PPMVD @ 7% O2 |  |  | 54.1 | LB/H | 3 H AV | 0.022 | LB/MMBTU
VA-0268 | THERMAL VENTURES | MARTINSVILLE THERMAL, LLC | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. |  | 2002-02-15 | STEAM PRODUCTION FACILITY | BOILER, STEAM | 11.11 | COAL | 120 | MMBTU/H | In order to meet the annual emission limitations included in this permit, the wood/coal mixture shall not exceed 30% coal by BTU content on an annual basis. Average annual heat content 13,000 Btu/lb HHV. Average sulfur content per shipment 0.9% and averag | Sulfur Dioxide (SO2) | P | GOOD COMBUSTION PRACTICES, CLEAN BURNING FUEL, AND CONTINUOUS EMISSION MONITORING DEVICE. | 0.47 | LB/MMBTU |  |  | 247 | T/YR |  | 0.47 | LB/MMBTU
MT-0022 | BULL MOUNTAIN, NO. 1, LLC - ROUNDUP POWER PROJECT | BULL MOUNTAIN DEV. COMPANY | MT |  | 2003-07-21 | COAL FIRED POWER PLANT | BOILER, PC NO. 1 | 11.11 | COAL | 390 | MW | Additional throughput: 4013 mmbtu/h - full load heat input. Stack tests & inspections are required by the permit after construction/operation of the facility. Calculations will be used in the future also . Calculations were the primary factor considered d | Sulfur Dioxide (SO2) | A | DRY FLUE GAS DESULFURIZATION (FGD) | 481.6 | LB/H | rolling 24 h avg | 94.5 | 0.12 | LB/MMBTU | rolling 24 h avg | 0.12 | LB/MMBTU
MT-0022 | BULL MOUNTAIN, NO. 1, LLC - ROUNDUP POWER PROJECT | BULL MOUNTAIN DEV. COMPANY | MT |  | 2003-07-21 | COAL FIRED POWER PLANT | BOILER, PC NO. 2 | 11.11 | COAL | 390 | MW | Stack tests and inspections are required by the permit after construction/operation of the facility. Calculations will be used in the future also. Calculations were the primary factor considered during the permitting process. | Sulfur Dioxide (SO2) | A | DRY FLUE GAS DESULFURIZATION (FGD) | 481.6 | LB/H | rolling 24 h avg | 94.5 | 0.12 | LB/MMBTU | rolling 24 h avg | 0.12 | LB/MMBTU
AR-0074 | PLUM POINT ENERGY | PLUM POINT ASSOCIATES, LLC | AR |  | 2003-08-20 |  | BOILER , UNIT 1 - SN-01 | 11.11 | SUB-BITUMINOUS COAL | 800 | MW | THE BOILER IS A 550-800 MW PULVERIZED COAL FIRED BOILER. | Sulfur Dioxide (SO2) | A | DRY FLUE GAS DESULFURIZATION | 0.16 | LB/MMBTU | [5 empty] | 0.16 | LB/MMBTU
AR-0079 | PLUM POINT ENERGY | PLUM POINT ASSOCIATES, LLC | AR |  | 2003-08-20 | PLUM POINT ENERGY ASSOCIATES, LLC (PERMITTEE) PROPOSES TO CONSTRUCT AND OPERATE A NOMINAL 550-800 MW COAL FIRED GENERATING STATION | BOILER - SN-01 | 11.11 | SUB-BITUMINOUS COAL | 800 | MW | THE BOILER IS A 550-800 MW PULVERIZED COAL FIRED BOILER. | Sulfur Dioxide (SO2) | A | DRY FLUE GAS DESULFURIZATION | 0.16 | LB/MMBTU | [5 empty] | 0.16 | LB/MMBTU
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | ELECTRICAL UTILITY | SUPER CRITICAL PULVERIZED COAL ELECTRIC STEAM BOILER (S04, P04) | 11.11 | PRB COAL | 5173.07 | MMBTU/H | 500 MW CAPACITY, BASE LOAD OPERATION (30% TO 100% CAPACITY) BACKUP / STARTUP FUEL, NATURAL GAS (5.07 CF6) PRB COAL (~0.5 WT. % S MAX., 5.5 WT % ASH); ~ 8100 BTU / LB; 319.3 TPH | Sulfur Dioxide (SO2) | B | DRY FGD, LIMIT ON EMISSIONS ENTERING CONTROL SYSTEM: 1.23 LBS/MMBTU 30 DAY AVG. | 0.1 | LB/MMBTU | 30 DAY AVG. | 92 | 0.09 | LB/MMBTU | 12 MO. ROLLING AVG. | 0.1 | LB/MMBTU |  | POLLUTANT LIMITS INCLUDE STARTUP / SHUTDOWN AND ATOMIZER CHANGEOUT. PERMITTEE MAY ONLY USE ACTUAL HOURS OF OPERATION WHEN DETERMINING TIME AVERAGED EMISSIONS. WHEN CONDUCTING MAINTENANCE ON CONTROL SYSTEM (ROUTINE ATOMIZER CHANGEOUT): 3491.8 POUNDS PER HOUR ON A 3-HOUR AVERAGE AND 1508.9 POUNDS PER HOUR ON A 24-HOUR AVERAGE. CONTROLLED EMISSIONS: SULFUR DIOXIDE EMISSIONS SHALL BE LIMITED TO 621 POUNDS PER HOUR AVERAGED OVER ANY CONSECUTIVE 3-HOUR PERIOD AND SULFUR DIOXIDE EMISSIONS SHALL BE LIMITED TO 589 POUNDS PER HOUR AVERAGED OVER ANY CONSECUTIVE 24-HOUR PERIOD
*TX-0499 | SANDY CREEK ENERGY STATION | SANDY CREEK ENERGY ASSOCIATES | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-07-24 | THE PROPOSED SCES IS A GRASSROOTS NEW, 860 MW GROSS (800 MW NET) ELECTRIC OUTPUT, PC BOILER STEAM ELECTRIC GENERATING FACILITY. THE MAXIMUM HEAT INPUT IS 8,185 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTU/HR). ONLY PRELIMINARY ENGINEERING DESIGN HAS BEEN COMPLETED AT THIS TIME AND THE PERMIT APPLICATION NET PLANT EFFICIENCY OF 10,231 BTU/KWHR (HEAT ENERGY INPUT DIVIDED BY NET ELECTRIC ENERGY OUTPUT) WILL NOT BE FINALIZED UNTIL PROJECT FUNDING IS COMPLETE. THE BOILER MAY BE DESIGNED AS A SUBCRITICAL STEAM PRESSURE UNIT, OR A MORE EFFICIENT, HIGHER PRESSURE, SUPERCRITICAL STEAM UNIT. THE ELECTRIC GENERATING PROCESS IS THE STANDARD RANKINE CLOSED CYCLE: BOILER FEEDWATER IS PUMPED, CONVERTED TO STEAM IN THE BOILER, PASSED THROUGH STEAM TURBINES WHICH TURN ELECTRIC GENERATORS, AND CONDENSED IN WATER-COOLED CONDENSERS TO AGAIN BECOME BOILER FEEDWATER. HEAT IS REMOVED FROM THE TURBINE CONDENSERS VIA A WET COOLING TOWER WHICH EVAPORATES TO THE ATMOSPHERE WATER OBTAINED FROM WACO’S MUNICIPAL WASTE WATER TREATMENT FACILITY. | PULVERIZED CAOL BOILER | 11.11 | COAL | 8185 | MMBTU/H | COAL (TYPICALLY 72% CARBON, 0.4% SULFUR, 6% ASH; REMAINDER HYDROGEN, OXYGEN AND NITROGEN) IS RECEIVED FROM RAILCAR, UNLOADED AND STORED IN A LARGE OPEN PILE FOR LONG-TERM STORAGE (INACTIVE PILE), OR IN ONE OF TWO SMALLER PILES FOR MORE IMMEDIATE USE (ACTIVE PILES). FROM THE ACTIVE PILE, COAL IS FED TO SILOS IN THE UPPER BOILER STRUCTURE. THE COAL IS THEN PULVERIZED, BLOWN THROUGH BURNERS, AND COMBUSTED IN THE FIREBOX. | Sulfur Dioxide (SO2) | N |  | 2456 | LB/H | 1-HR |  | 982 | LB/H | 30-DAY | 0.11998 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, JTA | 11.12 | HULLS | 280 | MMBTU/H |  | Carbon Monoxide | N |  | 0.63 | LB/MMBTU | [5 empty] | 0.63 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | NORTH DAKOTA STATE DEPARTMENT OF HEALTH |  | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, JTA | 11.12 | HULLS | 280 | MMBTU/H |  | Carbon Monoxide | N |  | 0.63 | LB/MMBTU | [5 empty] | 0.63 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND |  | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, JTA | 11.12 | HULLS | 280 | MMBTU/H |  | Carbon Monoxide | N |  | 0.63 | LB/MMBTU | [5 empty] | 0.63 | LB/MMBTU
PR-0007 | COGENERATION PLANT (AES-PRCP) | AES PUERTO RICO | PR | PUERTO RICO ENV QUALITY BOARD, AIR PROGRAM | 2001-10-29 | COGENERATION UNIT | 2 COAL-FIRED CIRCULATING FLUIDIZED BED BOILERS | 11.11 | BITUMINOUS COAL | 454 | MW (NET) | COMBINED MAX HEAT INPUT 4922.7 MMBTU/H @ 105% MAX CONTINUOUS RATING (MCR) AND CAPABLE OF GENERATING 1.8 E 6 LB/H OF STEAM @ 2400 PSIG AND 1000 DEGREES F. WILL SUPPLY SUPERHEATED STEAM TO 2 EXTRACTION CONDENSING TURBINES AND SUPPLY PROCESS STEAM OF UP TO 290000 LB/H | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 246.1 | LB/H |  |  | 94 | PPMVD @7%O2 |  | 0.1 | LB/MMBTU | 8 H BASIS
VA-0268 | THERMAL VENTURES | MARTINSVILLE THERMAL, LLC | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. |  | 2002-02-15 | STEAM PRODUCTION FACILITY | BOILER, STEAM | 11.11 | COAL | 120 | MMBTU/H | In order to meet the annual emission limitations included in this permit, the wood/coal mixture shall not exceed 30% coal by BTU content on an annual basis. Average annual heat content 13,000 Btu/lb HHV. Average sulfur content per shipment 0.9% and averag | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES, CLEAN BURNING FUEL, AND CONTINUOUS EMISSION MONITORING DEVICE. | 0.44 | LB/MMBTU |  |  | 231.3 | T/YR |  | 0.44 | LB/MMBTU
MT-0022 | BULL MOUNTAIN, NO. 1, LLC - ROUNDUP POWER PROJECT | BULL MOUNTAIN DEV. COMPANY | MT |  | 2003-07-21 | COAL FIRED POWER PLANT | BOILER, PC NO. 1 | 11.11 | COAL | 390 | MW | Additional throughput: 4013 mmbtu/h - full load heat input. Stack tests & inspections are required by the permit after construction/operation of the facility. Calculations will be used in the future also . Calculations were the primary factor considered d | Carbon Monoxide | N |  | 602 | LB/H |  |  | 0.15 | LB/MMBTU |  | 0.15 | LB/MMBTU
MT-0022 | BULL MOUNTAIN, NO. 1, LLC - ROUNDUP POWER PROJECT | BULL MOUNTAIN DEV. COMPANY | MT |  | 2003-07-21 | COAL FIRED POWER PLANT | BOILER, PC NO. 2 | 11.11 | COAL | 390 | MW | Stack tests and inspections are required by the permit after construction/operation of the facility. Calculations will be used in the future also. Calculations were the primary factor considered during the permitting process. | Carbon Monoxide | N |  | 602 | LB/H |  |  | 0.15 | LB/MMBTU |  | 0.15 | LB/MMBTU
AR-0074 | PLUM POINT ENERGY | PLUM POINT ASSOCIATES, LLC | AR |  | 2003-08-20 |  | BOILER , UNIT 1 - SN-01 | 11.11 | SUB-BITUMINOUS COAL | 800 | MW | THE BOILER IS A 550-800 MW PULVERIZED COAL FIRED BOILER. | Carbon Monoxide | P | COMBUSTION CONTROLS | 0.16 | LB/MMBTU | [5 empty] | 0.16 | LB/MMBTU
AR-0079 | PLUM POINT ENERGY | PLUM POINT ASSOCIATES, LLC | AR |  | 2003-08-20 | PLUM POINT ENERGY ASSOCIATES, LLC (PERMITTEE) PROPOSES TO CONSTRUCT AND OPERATE A NOMINAL 550-800 MW COAL FIRED GENERATING STATION | BOILER - SN-01 | 11.11 | SUB-BITUMINOUS COAL | 800 | MW | THE BOILER IS A 550-800 MW PULVERIZED COAL FIRED BOILER. | Carbon Monoxide | P | COMBUSTION CONTROLS | 0.16 | LB/MMBTU | [5 empty] | 0.16 | LB/MMBTU
GA-0114 | INLAND PAPERBOARD AND PACKAGING, INC. - ROME LINERBOARD MILL | TEMPLE INLAND, INC. | GA |  | 2004-10-13 | THIS FACILITY MANUFACTURES UNBLEACHED KRAFT LINERBOARD. | BOILER, COAL FIRED | 11.11 | COAL | 565 | MMBTU/H | MODIFICATION TO A 1962 BOILER | Carbon Monoxide | P | STAGED COMBUSTION AND GOOD COMBUSTION PRACTICES | 300 | PPM @ 3% O2 | [7 empty] | NOT AVAILABLE, SEE NOTE | PERMITTED LIMIT IS 300 PPM. EMISSION RATE LIMIT AS LB/MMBTU NOT AVAILABLE.
GA-0114 | INLAND PAPERBOARD AND PACKAGING, INC. - ROME LINERBOARD MILL | TEMPLE INLAND, INC. | GA |  | 2004-10-13 | THIS FACILITY MANUFACTURES UNBLEACHED KRAFT LINERBOARD. | BOILER, SOLID FUEL | 11.12 | BARK | 856 | MMBTU/H | BARK, WASTEWATER SLUDGE, TDF, FUEL OIL; MAY BE USED TO INCIENRATE NCG GASES; NEW BOILER | Carbon Monoxide | P | STAGED COMBUSTION AND GOOD COMBUSTION PRACTICES | 368 | PPM @ 3% O2 | [7 empty] | NOT AVAILABLE, SEE NOTE | PERMIT LIMIT IS 368 PPM. EMISSION LIMIT AS LB/MMBTU IS NOT AVAILABLE.
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | ELECTRICAL UTILITY | SUPER CRITICAL PULVERIZED COAL ELECTRIC STEAM BOILER (S04, P04) | 11.11 | PRB COAL | 5173.07 | MMBTU/H | 500 MW CAPACITY, BASE LOAD OPERATION (30% TO 100% CAPACITY) BACKUP / STARTUP FUEL, NATURAL GAS (5.07 CF6) PRB COAL (~0.5 WT. % S MAX., 5.5 WT % ASH); ~ 8100 BTU / LB; 319.3 TPH | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES; LOW NOX BURNERS | 0.15 | LB/MMBTU | CALENDAR DAY AVG. |  | 3399 | T/YR | 12 MO. ROLLING INCL. STARTUP / SHUTDOWN | 0.15 | LB/MMBTU
*TX-0499 | SANDY CREEK ENERGY STATION | SANDY CREEK ENERGY ASSOCIATES | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-07-24 | THE PROPOSED SCES IS A GRASSROOTS NEW, 860 MW GROSS (800 MW NET) ELECTRIC OUTPUT, PC BOILER STEAM ELECTRIC GENERATING FACILITY. THE MAXIMUM HEAT INPUT IS 8,185 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTU/HR). ONLY PRELIMINARY ENGINEERING DESIGN HAS BEEN COMPLETED AT THIS TIME AND THE PERMIT APPLICATION NET PLANT EFFICIENCY OF 10,231 BTU/KWHR (HEAT ENERGY INPUT DIVIDED BY NET ELECTRIC ENERGY OUTPUT) WILL NOT BE FINALIZED UNTIL PROJECT FUNDING IS COMPLETE. THE BOILER MAY BE DESIGNED AS A SUBCRITICAL STEAM PRESSURE UNIT, OR A MORE EFFICIENT, HIGHER PRESSURE, SUPERCRITICAL STEAM UNIT. THE ELECTRIC GENERATING PROCESS IS THE STANDARD RANKINE CLOSED CYCLE: BOILER FEEDWATER IS PUMPED, CONVERTED TO STEAM IN THE BOILER, PASSED THROUGH STEAM TURBINES WHICH TURN ELECTRIC GENERATORS, AND CONDENSED IN WATER-COOLED CONDENSERS TO AGAIN BECOME BOILER FEEDWATER. HEAT IS REMOVED FROM THE TURBINE CONDENSERS VIA A WET COOLING TOWER WHICH EVAPORATES TO THE ATMOSPHERE WATER OBTAINED FROM WACO’S MUNICIPAL WASTE WATER TREATMENT FACILITY. | PULVERIZED CAOL BOILER | 11.11 | COAL | 8185 | MMBTU/H | COAL (TYPICALLY 72% CARBON, 0.4% SULFUR, 6% ASH; REMAINDER HYDROGEN, OXYGEN AND NITROGEN) IS RECEIVED FROM RAILCAR, UNLOADED AND STORED IN A LARGE OPEN PILE FOR LONG-TERM STORAGE (INACTIVE PILE), OR IN ONE OF TWO SMALLER PILES FOR MORE IMMEDIATE USE (ACTIVE PILES). FROM THE ACTIVE PILE, COAL IS FED TO SILOS IN THE UPPER BOILER STRUCTURE. THE COAL IS THEN PULVERIZED, BLOWN THROUGH BURNERS, AND COMBUSTED IN THE FIREBOX. | Carbon Monoxide | N |  | 2456 | LB/H | 1-HR |  | 1228 | LB/H | 30-DAY | 0.15003 | LB/MMBTU
PA-0204 | KIMBERLY CLARK/CHESTER PLANT | KIMBERLY-CLARK TISSUE COMPANY | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 1998-06-24 | OP INCORPORATES THE EXISTING OP # 23- 306-018 | BOILER, CIRCULATING FLUIDIZED BED | 11.11 | COAL | 799 | MMBTU/H | BOILER LIMITED TO 8400 H/YR OPERATION AND FUEL OIL USAGE OF 170,000 GAL/YR. RACT OP ISSUED FOR NOX AND VOC SOURCES. | Volatile Organic Compounds (VOC) | N |  | 30 | T/YR | Rolling Avg Total From 3 Boilers |  |  |  |  | 0.006 | LB/MMBTU
PR-0007 | COGENERATION PLANT (AES-PRCP) | AES PUERTO RICO | PR | PUERTO RICO ENV QUALITY BOARD, AIR PROGRAM | 2001-10-29 | COGENERATION UNIT | 2 COAL-FIRED CIRCULATING FLUIDIZED BED BOILERS | 11.11 | BITUMINOUS COAL | 454 | MW (NET) | COMBINED MAX HEAT INPUT 4922.7 MMBTU/H @ 105% MAX CONTINUOUS RATING (MCR) AND CAPABLE OF GENERATING 1.8 E 6 LB/H OF STEAM @ 2400 PSIG AND 1000 DEGREES F. WILL SUPPLY SUPERHEATED STEAM TO 2 EXTRACTION CONDENSING TURBINES AND SUPPLY PROCESS STEAM OF UP TO 290000 LB/H | Volatile Organic Compounds (VOC) | P | COMBUSTION CONTROLS | 7.7 | PPMVD @ 7% O2 |  |  | 11.6 | LB/H |  |  |  |  | ADDITIONAL EMISSION LIMIT: 0.0047 LB/MMBTU
VA-0268 | THERMAL VENTURES | MARTINSVILLE THERMAL, LLC | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. |  | 2002-02-15 | STEAM PRODUCTION FACILITY | BOILER, STEAM | 11.11 | COAL | 120 | MMBTU/H | In order to meet the annual emission limitations included in this permit, the wood/coal mixture shall not exceed 30% coal by BTU content on an annual basis. Average annual heat content 13,000 Btu/lb HHV. Average sulfur content per shipment 0.9% and averag | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES, CLEAN BURNING FUEL, AND CONTINUOUS EMISSION MONITORING DEVICE. | 0.18 | LB/MMBTU |  |  | 94.6 | T/YR |  | 0.18 | LB/MMBTU
MT-0022 | BULL MOUNTAIN, NO. 1, LLC - ROUNDUP POWER PROJECT | BULL MOUNTAIN DEV. COMPANY | MT |  | 2003-07-21 | COAL FIRED POWER PLANT | BOILER, PC NO. 1 | 11.11 | COAL | 390 | MW | Additional throughput: 4013 mmbtu/h - full load heat input. Stack tests & inspections are required by the permit after construction/operation of the facility. Calculations will be used in the future also . Calculations were the primary factor considered d | Volatile Organic Compounds (VOC) | N |  | 12 | LB/H |  |  | 0.003 | LB/MMBTU |  | 0.003 | LB/MMBTU
MT-0022 | BULL MOUNTAIN, NO. 1, LLC - ROUNDUP POWER PROJECT | BULL MOUNTAIN DEV. COMPANY | MT |  | 2003-07-21 | COAL FIRED POWER PLANT | BOILER, PC NO. 2 | 11.11 | COAL | 390 | MW | Stack tests and inspections are required by the permit after construction/operation of the facility. Calculations will be used in the future also. Calculations were the primary factor considered during the permitting process. | Volatile Organic Compounds (VOC) | N |  | 12 | LB/H |  |  | 0.003 | LB/MMBTU |  | 0.003 | LB/MMBTU
AR-0074 | PLUM POINT ENERGY | PLUM POINT ASSOCIATES, LLC | AR |  | 2003-08-20 |  | BOILER , UNIT 1 - SN-01 | 11.11 | SUB-BITUMINOUS COAL | 800 | MW | THE BOILER IS A 550-800 MW PULVERIZED COAL FIRED BOILER. | Volatile Organic Compounds (VOC) | P | COMBUSTION CONTROLS | 0.02 | LB/MMBTU | [5 empty] | 0.02 | LB/MMBTU
AR-0079 | PLUM POINT ENERGY | PLUM POINT ASSOCIATES, LLC | AR |  | 2003-08-20 | PLUM POINT ENERGY ASSOCIATES, LLC (PERMITTEE) PROPOSES TO CONSTRUCT AND OPERATE A NOMINAL 550-800 MW COAL FIRED GENERATING STATION | BOILER - SN-01 | 11.11 | SUB-BITUMINOUS COAL | 800 | MW | THE BOILER IS A 550-800 MW PULVERIZED COAL FIRED BOILER. | Volatile Organic Compounds (VOC) | P | COMBUSTION CONTROLS | 0.02 | LB/MMBTU | [5 empty] | 0.02 | LB/MMBTU
GA-0114 | INLAND PAPERBOARD AND PACKAGING, INC. - ROME LINERBOARD MILL | TEMPLE INLAND, INC. | GA |  | 2004-10-13 | THIS FACILITY MANUFACTURES UNBLEACHED KRAFT LINERBOARD. | BOILER, COAL FIRED | 11.11 | COAL | 565 | MMBTU/H | MODIFICATION TO A 1962 BOILER | Volatile Organic Compounds (VOC) | P | STAGED COMBUSTION AND GOOD COMBUSTION PRACTICES. | 0.01 | LB/MMBTU | [5 empty] | 0.01 | LB/MMBTU
GA-0114 | INLAND PAPERBOARD AND PACKAGING, INC. - ROME LINERBOARD MILL | TEMPLE INLAND, INC. | GA |  | 2004-10-13 | THIS FACILITY MANUFACTURES UNBLEACHED KRAFT LINERBOARD. | BOILER, SOLID FUEL | 11.12 | BARK | 856 | MMBTU/H | BARK, WASTEWATER SLUDGE, TDF, FUEL OIL; MAY BE USED TO INCIENRATE NCG GASES; NEW BOILER | Volatile Organic Compounds (VOC) | P | STAGED COMBUSTION AND GOOD COMBUSTION PRACTICES | 0.05 | LB/MMBTU | [5 empty] | 0.05 | LB/MMBTU
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | ELECTRICAL UTILITY | SUPER CRITICAL PULVERIZED COAL ELECTRIC STEAM BOILER (S04, P04) | 11.11 | PRB COAL | 5173.07 | MMBTU/H | 500 MW CAPACITY, BASE LOAD OPERATION (30% TO 100% CAPACITY) BACKUP / STARTUP FUEL, NATURAL GAS (5.07 CF6) PRB COAL (~0.5 WT. % S MAX., 5.5 WT % ASH); ~ 8100 BTU / LB; 319.3 TPH | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES, LOW NOX BURNERS | 0.0036 | LB/MMBTU |  |  | 81.6 | T/YR | 12 MO. ROLLING, INCL. STARTUP / SHUTDOWN | 0.0036 | LB/MMBTU
*TX-0499 | SANDY CREEK ENERGY STATION | SANDY CREEK ENERGY ASSOCIATES | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-07-24 | THE PROPOSED SCES IS A GRASSROOTS NEW, 860 MW GROSS (800 MW NET) ELECTRIC OUTPUT, PC BOILER STEAM ELECTRIC GENERATING FACILITY. THE MAXIMUM HEAT INPUT IS 8,185 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTU/HR). ONLY PRELIMINARY ENGINEERING DESIGN HAS BEEN COMPLETED AT THIS TIME AND THE PERMIT APPLICATION NET PLANT EFFICIENCY OF 10,231 BTU/KWHR (HEAT ENERGY INPUT DIVIDED BY NET ELECTRIC ENERGY OUTPUT) WILL NOT BE FINALIZED UNTIL PROJECT FUNDING IS COMPLETE. THE BOILER MAY BE DESIGNED AS A SUBCRITICAL STEAM PRESSURE UNIT, OR A MORE EFFICIENT, HIGHER PRESSURE, SUPERCRITICAL STEAM UNIT. THE ELECTRIC GENERATING PROCESS IS THE STANDARD RANKINE CLOSED CYCLE: BOILER FEEDWATER IS PUMPED, CONVERTED TO STEAM IN THE BOILER, PASSED THROUGH STEAM TURBINES WHICH TURN ELECTRIC GENERATORS, AND CONDENSED IN WATER-COOLED CONDENSERS TO AGAIN BECOME BOILER FEEDWATER. HEAT IS REMOVED FROM THE TURBINE CONDENSERS VIA A WET COOLING TOWER WHICH EVAPORATES TO THE ATMOSPHERE WATER OBTAINED FROM WACO’S MUNICIPAL WASTE WATER TREATMENT FACILITY. | PULVERIZED CAOL BOILER | 11.11 | COAL | 8185 | MMBTU/H | COAL (TYPICALLY 72% CARBON, 0.4% SULFUR, 6% ASH; REMAINDER HYDROGEN, OXYGEN AND NITROGEN) IS RECEIVED FROM RAILCAR, UNLOADED AND STORED IN A LARGE OPEN PILE FOR LONG-TERM STORAGE (INACTIVE PILE), OR IN ONE OF TWO SMALLER PILES FOR MORE IMMEDIATE USE (ACTIVE PILES). FROM THE ACTIVE PILE, COAL IS FED TO SILOS IN THE UPPER BOILER STRUCTURE. THE COAL IS THEN PULVERIZED, BLOWN THROUGH BURNERS, AND COMBUSTED IN THE FIREBOX. | Volatile Organic Compounds (VOC) | N |  | 29 | LB/H | [5 empty] | 0.0035431 | LB/MMBTU

## Data - 100-250 MMBTU Solid Fuel
RBLCID | FACILITYNAME | CORPORATEORCOMPANYNAME | FACILITYSTATE | AGENCYNAME | PERMITDATE | FACILITYDESCRIPTION | PROCESSNAME | PROCTYPE | FUEL | THRUPUT | THRUPUTUNIT | PROCESSNOTES | POLLUTANT | CONTROLCOD | CTRLDESC | EMISLIMIT1 | EMISLIMIT1UNIT | EMISLIMIT1AVGTIMECONDITION | PCTEFFIC | EMISLIMIT2 | EMISLIMIT2UNIT | EMISLIMIT2AVGTIMECONDITION | STDEMISSLIMIT | STDUNITLIMIT | STDLIMITAVGTIMECONDITION | POLLUTANTCOMPLIANCENOTES
ND-0016 | AMERICAN CRYSTAL SUGAR COMPANY | AMERICAN CRYSTAL SUGAR COMPANY | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1997-06-11 |  | PULP DRYER | 12.11 | COAL | 230.3 | MMBTU/H | PARTICULATE EMISSIONS ARE DUE TO CONTACT DRYING OF PULP AND COAL COMBUSTION. NOX, SO2, CO AND VOC EMISSIONS ARE DUE TO COAL (SUBBITUMINOUS) COMBUSTION. | Nitrogen Oxides (NOx) | N |  | 100 | LB/H |  | 0 |  |  |  | 0.43 | LB/MMBTU
PA-0204 | KIMBERLY CLARK/CHESTER PLANT | KIMBERLY-CLARK TISSUE COMPANY | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 1998-06-24 | OP INCORPORATES THE EXISTING OP # 23- 306-018 | BOILER, VERTICAL | 12.11 | COAL | 249 | MMBTU/H | BOILER LIMITED TO FUEL OIL USAGE OF 170,000 GAL/YR. RACT OP ISSUED FOR NOX AND VOC SOURCES. | Nitrogen Oxides (NOx) | N |  | 1090 | T/YR | Total, 3 Boilers |  |  |  |  | 0.2 | LB/MMBTU
PA-0204 | KIMBERLY CLARK/CHESTER PLANT | KIMBERLY-CLARK TISSUE COMPANY | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 1998-06-24 | OP INCORPORATES THE EXISTING OP # 23- 306-018 | BOILER, VERTICAL | 12.11 | COAL | 198 | MMBTU/H | BOILER LIMITED TO FUEL OIL USAGE OF 170,000 GAL/YR. RACT OP ISSUED FOR NOX AND VOC SOURCES. | Nitrogen Oxides (NOx) | N |  | 1090 | T/YR | Total, 3 Boilers |  |  |  |  | 0.2 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | VEGETABLE OIL PLANT | BOILERS, 2 , WELLONS | 12.12 | HULLS | 200 | MMBTU/H | THROUGHPUT FOR 2 BOILERS, COMBINED. | Nitrogen Oxides (NOx) | N |  | 0.2 | LB/MMBTU | [5 empty] | 0.2 | LB/MMBTU
NC-0092 | RIEGELWOOD MILL | INTERNATIONAL PAPER COMPANY | NC | NORTH CAROLINA DIV OF ENV MGMT | 2001-05-10 | PAPER MILL | BOILER, POWER, COAL-FIRED | 12.11 | COAL | 249 | MMBTU/H | POWER BOILER CAN FIRE COAL, NO. 6 FUEL OIL, OR BARK/WOOD FIBER SLUDGE. | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICE | 0.4 | LB/MMBTU | [5 empty] | 0.4 | LB/MMBTU
NC-0092 | RIEGELWOOD MILL | INTERNATIONAL PAPER COMPANY | NC | NORTH CAROLINA DIV OF ENV MGMT | 2001-05-10 | PAPER MILL | BOILER, POWER, COAL-FIRED | 12.11 | COAL | 249 | MMBTU/H | POWER BOILER CAN FIRE COAL, NO. 6 FUEL OIL, OR BARK/WOOD FIBER SLUDGE. | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICE | 0.4 | LB/MMBTU | [5 empty] | 0.4 | LB/MMBTU
NC-0092 | RIEGELWOOD MILL | INTERNATIONAL PAPER COMPANY | NC | NORTH CAROLINA DIV OF ENV MGMT | 2001-05-10 | PAPER MILL | BOILER, POWER, WOODWASTE-FIRED | 12.12 | WOODWASTE | 600 | MMBTU/H | THROUGHPUT IS MAXIMUM PERMITTED HEAT INPUT RATE FOR BARK/WOOD FIBER SLUDGE/FOSSIL FUEL FIRING. | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICE | 0.35 | LB/MMBTU | [5 empty] | 0.35 | LB/MMBTU
NC-0092 | RIEGELWOOD MILL | INTERNATIONAL PAPER COMPANY | NC | NORTH CAROLINA DIV OF ENV MGMT | 2001-05-10 | PAPER MILL | BOILER, POWER, WOODWASTE-FIRED | 12.12 | WOODWASTE | 600 | MMBTU/H | THROUGHPUT IS MAXIMUM PERMITTED HEAT INPUT RATE FOR BARK/WOOD FIBER SLUDGE/FOSSIL FUEL FIRING. | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICE | 0.35 | LB/MMBTU | [5 empty] | 0.35 | LB/MMBTU
VA-0267 | VPI POWER STATION | VPI UNIVERSITY | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2001-08-30 | COAL-FIRED BOILER THAT PRODUCES STEAM TO GENERATE ELECTRICITY. | BOILER, OVERFEED STOKER | 12.11 | COAL | 146.7 | MMBTU/H | No. 11 boiler. Boiler produces steam for generation of electricity. | Nitrogen Oxides (NOx) | P | LOW EXCESS AIR/STAGED COMBUSTION AND A CONTINUOUS EMISSION MONITORING SYSTEM. | 36.1 | LB/H |  |  | 136.9 | T/YR |  | 0.25 | LB/MMBTU
OH-0241 | MILLER BREWING COMPANY - TRENTON | MILLER BREWING COMPANY | OH | HAMILTON CO-SOUTHWESTERN OH APCA | 2004-05-27 | BEER BREWING AND PACKAGING. | BOILER (2), COAL FIRED | 12.11 | COAL | 238 | MMBTU/H | TWO BOILERS, CAPABLE OF BURNING AND WITH LIMITS FOR COAL, NATURAL GAS, NUMBERS 2 AND 6 FUEL OILS. POUND PER HOUR LIMITS ARE FOR EACH BOILER; AND EXCEPT FOR VOC AND CO, ALL T/YR LIMITS ARE FOR BOTH BOILERS COMBINED. COAL USAGE FOR BOTH BOILERS TOGETHER NOT TO EXCEED 125,682 TONS/ROLLING 12 MONTHS. THESE LIMITS FOR THE COAL. | Nitrogen Oxides (NOx) | P | OVERFIRE AND SIDE FIRE AIR TO REDUCE FLAME TEMERATURE | 0.7 | LB/MMBTU |  |  | 1375.9 | T/YR | BOTH BOILERS TOGETHER, PER ROLLING 12-MO | 0.7 | LB/MMBTU
OH-0241 | MILLER BREWING COMPANY - TRENTON | MILLER BREWING COMPANY | OH | HAMILTON CO-SOUTHWESTERN OH APCA | 2004-05-27 | BEER BREWING AND PACKAGING. | BOILER (2), COAL FIRED | 12.11 | COAL | 238 | MMBTU/H | TWO BOILERS, CAPABLE OF BURNING AND WITH LIMITS FOR COAL, NATURAL GAS, NUMBERS 2 AND 6 FUEL OILS. POUND PER HOUR LIMITS ARE FOR EACH BOILER; AND EXCEPT FOR VOC AND CO, ALL T/YR LIMITS ARE FOR BOTH BOILERS COMBINED. COAL USAGE FOR BOTH BOILERS TOGETHER NOT TO EXCEED 125,682 TONS/ROLLING 12 MONTHS. THESE LIMITS FOR THE COAL. | Nitrogen Oxides (NOx) | P | OVERFIRE AND SIDE FIRE AIR TO REDUCE FLAME TEMERATURE | 0.7 | LB/MMBTU |  |  | 1375.9 | T/YR | BOTH BOILERS TOGETHER, PER ROLLING 12-MO | 0.7 | LB/MMBTU
ND-0020 | RICHARDTON PLANT | RED TRAIL ENERGY, LLC | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 2004-08-04 | ETHANOL PRODUCTION PLANT RATED AT 65 MILLION GALLONS PER YEAR. | BOILER, COAL-FIRED | 12.11 | LIGNITE | 250 | MMBTU/H | BOILER ACTS AS A CONTROL DEVICE FOR THE DISTILLER'S GRAIN DRYERS , DISTILLATION COLUMNS AND BIOMETHANATOR (I.E. GASES FROM THESE PROCESSES ARE ROUTED TO THE BOILER FOR COMBUSTION). | Nitrogen Oxides (NOx) | A | SNCR | 0.1 | LB/MMBTU | 30 DAY ROLLING AVERAGE | 76 |  |  |  | 0.1 | LB/MMBTU
NE-0037 | CARGILL, INC. | CARGILL, INC. | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2006-09-08 | A WET CORN MILLING AND ETHANOL PRODUCTION FACILITY | CIRCULATING FLUIDIZED BED BOILER | 12.11 | COAL | 1500 | MMBTU/H | ALLOWED TO COMBUST UP TO 20% BIOMASS BY HEAT CONTENT. | Nitrogen Oxides (NOx) | A | COMBUSTION CONTROL PLUS SNCR | 0.08 | LB/MMBTU | 30-DAY ROLLING AVERAGE |  | 120 | LB/H | 30-DAY ROLLING AVERAGE/<70% LOAD | 0.08 | LB/MMBTU

## Data - 100-250 MMBTU Gas
RBLCID | FACILITYNAME | CORPORATEORCOMPANYNAME | FACILITYSTATE | AGENCYNAME | PERMITDATE |  | YEAR | FACILITYDESCRIPTION | PROCESSNAME | PROCTYPE | FUEL | THRUPUT | THRUPUTUNIT | PROCESSNOTES | POLLUTANT | CONTROLCOD | CTRLDESC | EMISLIMIT1 | EMISLIMIT1UNIT | EMISLIMIT1AVGTIMECONDITION | PCTEFFIC | EMISLIMIT2 | EMISLIMIT2UNIT | EMISLIMIT2AVGTIMECONDITION | STDEMISSLIMIT | STDUNITLIMIT | STDLIMITAVGTIMECONDITION | POLLUTANTCOMPLIANCENOTES
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BTU-NO. 1 REACTOR FEED HEATER | 12.39 |  | 121.74 | MMBTU/H | EMISSION POINT NO. BTU-HF103. |  | Ammonia (NH3) | P | LEAK DETECTION AND REPAIR PROGRAM | 0.5 | LB/H | SEE NOTES |  | 2.17 | T/YR | SEE NOTES |  |  |  | ADDITIONAL EMISSION LIMIT: 10 PPMVD @ 3% O2. EMISSION LIMITS ARE POST-INSTALLATION OF SCR.
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ISOM II WEST REACTOR FEED HEATER | 12.39 |  | 104.25 | MMBTU/H | EMISSION POINT NO. BTU-HF106. |  | Ammonia (NH3) | P | LEAK DETECTION AND REPAIR PROGRAM | 0.42 | LB/H |  |  | 1.86 | T/YR
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ORTHOXYLENE II HEATER | 12.39 |  | 226.42 | MMBTU/H | EMISSION POINT NO.: ORTHOII-H2. |  | Ammonia (NH3) | P | LEAK DETECTION AND REPAIR PROGRAM. | 0.92 | LB/H | SEE NOTES |  | 4.04 | T/YR | SEE NOTES |  |  |  | ADDITIONAL LIMIT OF 10 PPMVD @3% O2. EMISSION LIMITS ARE APPLICABLE POST INSTALLATION OF SCR.
CA-1113 | PRAXAIR | PRAXAIR | CA | SOUTH COAST AQMD, CA | 2002-03-15 | 2002 |  | HEATER-OTHER PROCESS | 12.39 | WASTE GAS | 117.6 | MMBTU/H | EQUIP: , MFR: SELAS FLUID PROCESING CORPORATION, TYPE: HYDROGEN REFORMER, MODEL: LH 1207 B001, FUNC EQUIP: PROVIDES HEAT TO CATYST FILLED TUBES TO PRODUCE HYDROGEN-*, FUEL_TYPE: NATURAL GAS (WARM UP AND SUPPLEMENT), SCHEDULE: CONTINUOUS, H/D: 24, D/W: 7, W/Y: 52, NOTES: AMMONIA IS MIXED INTO FLUE GAS, AND THE MIXTURE IS PASSED THROUGH A CATALYST BED, IN WHICH THE AMMONIA REACTS WITH NOX REDUCING IT TO N2. SCR DESIGN OPERATING TEMPERATURE IS 760F, AND DESIGN REMOVAL EFFICIENCY IS 90%. A SOURCE TEST IS REQUIRED WITHIN 90 DAYS AFTER STARTUP FOR NOX, CO, ROG, NH3, PM, SOX. THE FACILITY IS IN RECLAIM, AND WILL HAVE CEMS FOR NOX AND O2. THE PERMIT REQUIRES CEMS FOR NH3 ALSO; HOWEVER, THE APPLICANT IS REQUESTING TO SUBSTITUTE A PARAMETRIC MONITORING METHOD. |  | Ammonia (NH3) | N |  | 5 | PPMVD@3%O2 | 1 H | N/A
CA-1024 | AES HUNTINGTON BEACH | AES HUNTINGTON BEACH | CA | SOUTH COAST AQMD, CA | 2002-08-01 | 2002 |  | BOILER: >= 50 MMBTU/HR | 12.31 | NATURAL GAS | 225 | MW | EQUIP: ELECTRIC UTILITY BOILER, MFR: BABCOCK & WILCOX, TYPE: MULTI-WALL FIRED, MODEL: , FUNC EQUIP: USE IS CURRENTLY FOR PEAK POWER DEMAND PERIODS, FUEL_TYPE: , SCHEDULE: VARIABLE, H/D: 24, D/W: 5, W/Y: 20, NOTES: FACILITY APPLIED TO BRING THIS RETIRED BOILER BACK INTO SERVICE. FACILITY IS EXPERIENCING DIFFICULTY MEETING NOX AND AMMONIA LIMITS ON ONE- HOUR AVERAGING BASIS, AND DISTRICT IS CONSIDERING REQUEST FOR LONGER AVERAGING TIME. SOURCE TEST RESULTS: PPM@3%O2, GR/DSCF: 225 MW: NOX-3.5, CO-0.0, VOC- 4.2, NH3-3.1, PM-.001. 169 MW: NOX-4.2, NH3-1.6, PM-.002. 115MW: NOX-3.8, NH3-0.5. 90 MW: NOX-4.5, NH3-0.7, PM-.004 |  | Ammonia (NH3) | N |  | 5 | PPMVD @3% O2 | 1-H | N/A | [6 empty] | POLLUTANT EMITTED IS NH3.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | VACUUM CRUDE CHARGE HEATER | 12.39 | REFINERY FUEL GAS OR NG | 101 | MMBTU/H | THIS UNIT IS IDENTIFIED BY EQUIPMENT ID # B-02100 |  | Ammonia (NH3) | N |  | 5 | PPMVD | THREE-HOUR ROLLING AVG | [7 empty] | THIS LIMIT IS 5.0 PPMVD BASED ON 0% OXYGEN
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT CHARGE HEATER | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 122 | MMBTU/H | THIS UNIT IS IDENTIFIED BY EQUIPMENT ID # B-05110 |  | Ammonia (NH3) | N |  | 5 | PPMVD | CORRECTED TO 0.0% OXYGEN ON A 3-HR AVG.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT INTERHEATER NO. 1 | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 192 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY EQUIPMENT ID # B-05120 |  | Ammonia (NH3) | N |  | 5 | PPMVD | CORRECTED TO 0.0% OXYGEN - 3-HR AVG.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT INTERHEATER NO. 2 | 12.39 | REFINERY FUEL GAS OR NATURAL GAS | 129 | MMBTU/H | THIS EQUIPMENT IS IDENTIFIED BY ID # B-05130 |  | Ammonia (NH3) | N |  | 5 | PPMVD | CORRECTED TO 0.0% OXYGEN - 3-HR AVERAGE
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | BUTANE CONVERSION UNIT ISOSTRIPPER REBOILER | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 222 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY ID # B-15110 |  | Ammonia (NH3) | N |  | 5 | PPMVD | CORRECTED TO 0.0% OXYGEN - 3-HR AVERAGE
*TX-0496 | INEOS CHOCOLATE BAYOU FACILITY | INEOS USA LLC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-08-29 | 2006 | THE NO. 1 AND NO. 2 OLEFINS UNITS USE PYROLYSIS FURNACES TO CRACK FEEDSTOCKS INTO LOW MOLECULAR WEIGHT HYDROCARBONS THAT CONTAIN OLEFINS. PRODUCTS ARE ETHYLENE, PROPYLENE, PYROLYSIS GASOLINE, CRUDE C4, FUEL OIL, AND HYDROGEN. FEED FOR THE OLEFINS CRACKING FURNACES IS EITHER GAS FEED (ETHANE-RICH OR PROPANE-RICH FEED) OR LIQUID FEED (REFINERY RAFFINATE AND DEBUTANIZED NATURAL GASOLINE (DNG). THE LIQUID FEEDSTOCKS ARE STORED PRIOR TO PROCESSING IN LARGE FLOATING-ROOF TANKS EQUIPPED WITH SECONDARY SEALS. ETHYLENE PRODUCT IS TRANSFERRED OFF-SITE BY PIPELINE. PROPYLENE IS SHIPPED VIA RAILCAR, BARGE, OR SENT TO AN EXISTING POLYPROPYLENE UNIT AT THE CHOCOLATE BAYOU PLANT FOR FURTHER PROCESSING. CRUDE C4 STOCK IS SENT TO THE BUTADIENE EXTRACTION UNIT (BEU) TO PRODUCE HIGH PURITY BUTADIENE WHICH IS SOLD. BUTADIENE PRODUCT IS SHIPPED OFF-SITE VIA RAILCAR OR BARGE. THE RAW PYROLYSIS GASOLINE IS FURTHER HYDROTREATED TO PYROLYSIS GASOLINE PRODUCT FOR SHIPMENT OFF SITE | FURNACE EMISSION CAPS | 12.39 |  |  |  | EMISSION CAPS FOR FURNACES ARE NOT CHANGED IN THIS PERMIT ACTION. SPECIAL CONDITION NO. 13 IS CHANGED TO CLARIFY BACT SHALL BE DEMONSTRATED FOR EACH NEW FURNACE (EQUIPPED WITH SCR) AND ALLOW EXCEPTION WHEN THE UNIT IS IN DECOKING. SPECIAL CONDITION NO. 51 IS CHANGED TO ALLOW BACT FOR OLD FURNACES TO BE DEMONSTRATED AT THE LEVELS WHEN THE FLEXIBLE PERMIT WAS ISSUED. COMBUSTION STAFF WAS CONSULTED AND CONCURRED WITH THE CHANGE. |  | Ammonia (NH3) | N |  | 27.47 | LB/H |  |  | 120.33 | T/YR
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BOILER NO. 12 | 12.39 |  | 245 | MMBTU/H | EMISSION PT NO: BOILER-12. SHALL BE SHUTDOWN. |  | Benzene | N | NONE INDICATED | 0.12 | LB/H |  | NESHAP | 0.53 | T/YR
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BTU-NO. 1 REACTOR FEED HEATER | 12.39 |  | 121.74 | MMBTU/H | EMISSION POINT NO. BTU-HF103. |  | Benzene | N | NONE INDICATED | 0.06 | LB/H |  | NESHAP | 0.26 | T/YR
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ISOM II WEST REACTOR FEED HEATER | 12.39 |  | 104.25 | MMBTU/H | EMISSION POINT NO. BTU-HF106. |  | Benzene | N | NONE INDICATED | 0.05 | LB/H |  | NESHAP | 0.22 | T/YR
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ORTHOXYLENE II HEATER | 12.39 |  | 226.42 | MMBTU/H | EMISSION POINT NO.: ORTHOII-H2. |  | Benzene | N |  | 0.11 | LB/H |  | NESHAP | 0.49 | T/YR
AR-0019 | QUINCY SOYBEAN COMPANY OF ARKANSAS | QUINCY SOYBEAN COMPANY OF ARKANSAS | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-03-04 | 1997 |  | BOILER, #3 | 12.31 | NATURAL GAS | 123 | MMBTU/H |  |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 24.6 | LB/H |  |  | 0 |  |  | 0 | LB/MMBTU
AL-0096 | MEAD COATED BOARD, INC. | MEAD COATED BOARD, INC. | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-03-12 | 1997 |  | DUCT BURNER, NAT GAS | 12.31 | NATURAL GAS | 170 | MMBTU/H | A SEPARATELY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING FUEL OIL. |  | Carbon Monoxide | P | PROPER DESIGN AND GOOD COMBUSTION PRACTICES. | 0.08 | LB/MMBTU |  |  | 16.1 | LB/H |  | 0.08 | LB/MMBTU
IN-0075 | GRAIN PROCESSING CORP. | GRAIN PROCESSING CORP. | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1997-06-10 | 1997 |  | BOILERS NO. 1 & 2 | 12.39 | NATURAL GAS/ALCOHOL | 244 | MMBTU/H (EACH) | STACK TEST REQUIRED BY PERMIT, NOT YET CONSTRUCTED. BOILER NO.1 (UP51A), BOILER NO.2 (UP51B). |  | Carbon Monoxide | P | GOOD COMBUSTION CONTROL | 0.04 | LB/MMBTU |  |  | 0 |  |  | 0.04 | LB/MMBTU
NJ-0031 | UNIVERSITY OF MEDICINE & DENTISTRY OF NEW JERSEY | UNIVERSITY OF MEDICINE & DENTISTRY OF NEW JERSEY | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-06-26 | 1997 |  | BOILER, NATURAL GAS FIRED, 3 | 12.31 | NATURAL GAS | 112 | MMBTU/H | SEPARATELY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING NO.6 FUEL OIL (SECONDARY FUEL). |  | Carbon Monoxide | N
NJ-0041 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-10-08 | 1997 |  | DUCT BURNER ONLY | 12.31 | NATURAL GAS | 234 | MMBTU/H | TOTAL NATURAL GAS BURNED IN THE HEAT RECOVERY BOILER SHALL NOT EXCEED 1153.2 MILLION CUBIC FEET PER CALENDAR YEAR |  | Carbon Monoxide | P | LOW NOX BURNER | 23.4 | LB/H |  |  | 43 | PPMVD @ 15% O2 |  | 0.1 | LB/MMBTU
LA-0114 | ST. JAMES STYRENE PLANT | CHEVRON CHEMICAL COMPANY | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1997-12-10 | 1997 | MODIFICATION TO THE EXISTING STYRENE PRODUCTION FACILITY | SUPERHEATER | 12.31 | NATURAL GAS | 165 | MMBTU/H |  |  | Carbon Monoxide | P | PROPER OPERATING TECHNIQUES WITH AUTOMATIC CONTROL3% EXCESS O2 | 0.04 | LB/MMBTU | [5 empty] | 0.04 | LB/MMBTU
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, NAT GAS | 12.31 | NATURAL GAS | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Carbon Monoxide | A |  | 0.17 | LB/MMBTU |  |  | 32.3 | LB/H |  | 0.17 | LB/MMBTU
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, HYDROGEN | 12.39 | HYDROGEN | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Carbon Monoxide | A |  | 0.17 | LB/MMBTU |  |  | 32.3 | LB/H |  | 0.17 | LB/MMBTU
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, COMBINED FUEL (NAT GAS/HYDROGEN) | 12.39 | NAT GAS/HYDRO COMBO | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Carbon Monoxide | A |  | 0.17 | LB/MMBTU |  |  | 32.3 | LB/H |  | 0.17 | LB/MMBTU
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | DUCT BURNER | 12.39 | NAT GAS/HYDROGEN | 260 | MMBTU/H |  |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.07 | LB/MMBTU | ABOVE 130 MMBTU/H |  | 18.2 | LB/H | ABOVE 130 MMBTU/H | 0.07 | LB/MMBTU | ABOVE 130 MMBTU/H | LIMIT WHEN OPERATING BELOW A HEAT INPUT OF 130 MMBTU/H: 0.1 LB/MMBTU
MO-0051 | PROCTOR & GAMBLE PAPER PRODUCTS | Proctor & Gamble Paper Products | MO | MISSOURI DNR, AIR POLL CONTROL PROGRAM | 1998-01-01 | 1998 | SANITARY TISSUE & TOWEL BUSINESS, EXPANSION TO EXISTING DIAPER MANUFACTURING PLANT | BOILERS, NATURAL GAS, (3) | 12.31 | NATURAL GAS | 1095 | MMCF/YR | ADDITIONAL THROUGHPUT INFORMATION: 125 MMBTU/H, EACH. |  | Carbon Monoxide | P | LOW NOX FUEL, W/O FLUE GAS RECIRC., GOOD COMBUSTION | 0.15 | LB/MMBTU | [5 empty] | 0.15 | LB/MMBTU
SC-0075 | NUCOR STEEL- DARLINGTON COUNTY | NUCOR STEEL CORPORATION | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 1998-01-08 | 1998 | STEEL MILL | REHEAT FURNACE #1 | 12.31 | NATURAL GAS | 140 | MMBTU/H | MAIN FUEL IS NATURAL GAS, PROPANE AS A BACK-UP. UTILIZES LOW NOX BURNERS. NATURAL GAS AND PROPANE USAGE IS RESTRICTED TO AN EQUIVALENT OF 1150 X MMSCF PER YEAR AT ESTABLISHED BTU CONTENTS OF 1000 BTU/CF AND 90500 BTU/GALLON RESPECTIVELY. SUBJECT TO PSD. |  | Carbon Monoxide | N |  | 27.6 | LB/H |  |  | 120.9 | T/YR |  | 0.197 | LB/MMBTU
SC-0075 | NUCOR STEEL- DARLINGTON COUNTY | NUCOR STEEL CORPORATION | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 1998-01-08 | 1998 | STEEL MILL | REHEAT FURNACE #2 | 12.31 | NATURAL GAS | 125 | MMBTU/H | NATURAL GAS IS MAIN FUEL, PROPANE AS BACK UP. UTILIZES LOW NOX BURNERS AND EXTERNAL FLUE GAS RECIRCULATION. NATURAL GAS AND PROPANE USAGE IS RESTRICTED TO AN EQUIVALENT OF 1095 MMSCF PER YEAR AS ESTABLISHED BTU CONTENTS OF 1000 BTU/CF AND 90500 BTU/GAL RESPECTIVELY. SUBJECT TO PSD. |  | Carbon Monoxide | N | NONE INDICATED | 26.2 | LB/H |  |  | 114.8 | T/YR |  | 0.187 | LB/MMBTU
PA-0152 | PEI POWER | PEI POWER | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 1998-05-22 | 1998 |  | BOILER, CFB, MODIFIED | 12.39 | LANDFILL GAS | 249 | MMBTU/H | MFG. BY DB RILEY AND FOSTER WHEELER |  | Carbon Monoxide | N |  | 0.15 | LB/MMBTU |  |  | 37 | LB/H |  | 0.15 | LB/MMBTU
TX-0259 | FREEPORT COGENERATION FACILITY | BASF CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-06-26 | 1998 | CONSTRUCTION OF A COGENERATION UNIT | BOILER, B-20A | 12.39 | H2 WASTE & NAT GAS | 213 | MMBTU/H | HYDROGEN WASTE GAS AND PIPELINE QUALITY, SWEET NAT GAS CONTAINING NO >0.25 GR H2S AND 5 GR TOTAL S/100 DSCF. SCC CODE FOR NATURAL GAS CHOSEN FOR THE PURPOSE OF THIS DATABASE. |  | Carbon Monoxide | N | NONE INDICATED | 40.7 | LB/H |  |  | 175 | T/YR |  | 0.19 | LB/MMBTU | CALCULATED | EMISSION LIMIT IN STANDARDIZED UNITS CALCULATED FROM THE HOURLY EMISSION LIMIT AND THE THROUGHPUT.
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | 1998 | VEGETABLE OIL PLANT | BOILER, TRANE MURRAY, NAT GAS | 12.31 | NATURAL GAS | 189 | MMBTU/H | No add-on controls. See separate process for backup fuel (No. 2 oil) requirements. |  | Carbon Monoxide | N |  | 0.08 | LB/MMBTU | [5 empty] | 0.08 | LB/MMBTU
IN-0104 | CON AGRA SOYBEAN PROCESSING CO. | CON AGRA SOYBEAN PROCESSING CO. | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1998-08-14 | 1998 | SOYBEAN PROCESSING | BOILER, (2) | 12.31 | NATURAL GAS | 200 | MMBTU/H | 2 main boilers, throughput for each, low sulfur fuel oil is auxilary fuel. |  | Carbon Monoxide | P | GOOD COMBUSTION | 0.074 | LB/MMBTU | [5 empty] | 0.074 | LB/MMBTU
TX-0237 | PORT ARTHUR REFINERY | FINA OIL AND CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-09-08 | 1998 | CHEMICAL AND OIL COMPANY, 2.2 BILLION LB/YR ETHYLENE CRACKING UNIT & ASSOCIATED FACILITIES. LOCATED AT INTERSECTION OF HWY 366 & 32ND ST. | DUCT BURNERS (2) | 12.31 | NATURAL GAS | 310.4 | MMBTU/H |  |  | Carbon Monoxide | P | GOOD OPERATING PRACTICES | 0.08 | LB/MMBTU | [5 empty] | 0.08 | LB/MMBTU
TX-0237 | PORT ARTHUR REFINERY | FINA OIL AND CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-09-08 | 1998 | CHEMICAL AND OIL COMPANY, 2.2 BILLION LB/YR ETHYLENE CRACKING UNIT & ASSOCIATED FACILITIES. LOCATED AT INTERSECTION OF HWY 366 & 32ND ST. | BOILER, SUPPLEMENTAL, STEAM | 12.31 | NATURAL GAS | 227 | mmbtu/h | THIS SUPPLEMENTAL STEAM BOILER IS PART OF THE COGENERATION PACKAGE INCLUDING 2 COMBINED CYCLE TURBINES AND 2 DUCT BURNERS. |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 0.069 | LB/MMBTU | [5 empty] | 0.069 | LB/MMBTU
AL-0123 | U S ALLIANCE | U S ALLIANCE | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1998-09-25 | 1998 |  | BOILER, AUX. POWER, NO.1 | 12.31 | NATURAL GAS | 0 |  |  |  | Carbon Monoxide | N |  | 0.1 | LB/MMBTU |  |  | 45.7 | LB/H |  | 0.1 | LB/MMBTU
TX-0305 | PARIS GENERATING STATION | PANDA PARIS LLC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-10-28 | 1998 | PANDA PARIS, LLC, PROPOSES TO CONSTRUCT A NATURAL GAS-FIRED COMBINED- CYCLE POWER GENERATION FACILITY TO BE KNOWN AS THE PARIS GENERATING STATION, LOCATED IN LAMAR COUNTY. THE PROPOSED FACILITY WILL CONSIST OF FOUR 170 MW GENERAL ELECTRIC 7241FA COMBUSTION TURBINES AND ASSOCIATED HEAT RECOVERY STEAM GENERATORS WITH 200 MMBTU/H DUCT BURNERS EACH. THE TURBINES AND DUCT BURNERS WILL BE FIRED WITH PIPELINE NAT GAS. PROCESS STEAM FROM THE HRSGS WILL BE USED TO GENERATE ADDITIONAL ELECTRICITY FROM TWO 160 MW STEAM TURBINES. THE COMBINED UNITS WILL HAVE A NOMINAL CAPACITY OF 1000 MW. THERE WILL BE TWO 2000 DIESEL FUEL- FIRED BLACK START EMERGENCY GENERATORS, ONE 400 KW DIESEL FUEL- FIRED EMERGENCY ELECTRICAL GENERATOR TO PROVIDE GENERAL SITE POWER, ONE 260- HP DIESEL FUEL-FIRED EMERGENCY FIRE WATER PUMP AND ANCILLARY EQUIPMENT INCLUDING RAW AND DEMINERALIZED WATER STORAGE TANKS. A LETTER DATED AUGUST 20, 1998 FROM THE COMPANY'S CONSULTANT (ECT) ALSO REQUESTED THESE DIESEL- FIRED ENGINES BE EXEMPT UNDER 30 TAC SECTION 106.511 AND 106.512 AND NOT HAVE THEM INCLUDED IN THIS PERMIT. | (4) DUCT BURNERS | 12.31 | NAT GAS | 200 | MMBTU/H, EA | THE TOTAL ANNUAL HEAT INPUT TO ALL DUCT BURNERS SHALL NOT EXCEED 3,200,000 MMBTU FOR THE FACILITY SITE. |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.1 | LB/MMBTU | EACH UNIT |  |  |  |  | 0.1 | LB/MMBTU | EACH UNIT
OH-0245 | REPUBLIC TECHNOLOGIES INTERNATIONAL | REPUBLIC TECHNOLOGIES INTERNATIONAL/CANTON | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 1999-01-27 | 1999 | STEEL MILL. THIS PLANT IS PSD FOR PM, SO2, NOX, CO, AND VOC. THIS MODIFICATION IS A SIGNIFICANT INCREASE FOR NOX. | BLOOM REHEAT FURNACE | 12.31 | NATURAL GAS | 196.2 | MMBTU/H | STACK TEST 0.0489 LB NOX/HR |  | Carbon Monoxide | N |  | 7.8 | LB/H |  | SIP | 34.3 | T/YR |  | 0.175 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 4 (NAT GAS) | 12.31 | NATURAL GAS | 118 | MMBTU/H | MFR. IS BABCOCK & WILCOX. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Carbon Monoxide | N | NONE LISTED | 4.7 | LB/H |  |  | 42 | PPMVD @ 7% O2 |  | 0.04 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 2 (NAT GAS) | 12.31 | NATURAL GAS | 134 | MMBTU/H | MFR. IS COMBUSTION ENGINEERING. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Carbon Monoxide | N | NOT LISTED | 5.4 | LB/H |  |  | 42 | PPMVD @ 7% O2 |  | 0.04 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 3 (NAT GAS) | 12.31 | NATURAL GAS | 152 | MMBTU/H | MFR. IS BABCOCK & WILCOX. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Carbon Monoxide | N | NONE LISTED | 6.1 | LB/H |  |  | 42 | PPMVD @ 7% O2 |  | 0.04 | LB/MMBTU
AL-0128 | ALABAMA POWER COMPANY - THEODORE COGENERATION | ALABAMA POWER COMPANY - THEODORE COGENERATION | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1999-03-16 | 1999 |  | BOILER | 12.31 | NATURAL GAS | 220 | MMBTU/H |  |  | Carbon Monoxide | P | EFFICIENT COMBUSTION | 0.165 | LB/MMBTU |  |  | 36.3 | LB/H |  | 0.165 | LB/MMBTU
TX-0414 | ATOFINA PETROCHEMICALS PORT ARTHUR COMPLEX | FINA OIL & CHEMICAL COPMANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1999-04-22 | 1999 | FACILITY WANTS TO INSTALL A COGENERATION FACILITY CONSISTING OF 2 TURBINES AND SUPPLEMENTAL BOILER TO SUBSTITUTE FOR 2 AUXILIARY STEAM BOILERS | SUPPLEMENTAL BOILER | 12.31 | NATURAL GAS | 227 | MMBTU/H | BOILER PRODUCES AS MUCH AS 150,000 LB/H OF STEAM. |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 15.7 | LB/H |  |  | 18.63 | T/YR |  | 0.07 | LB/MMBTU
AR-0026 | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1999-05-05 | 1999 | COMBUSTION TURBINE COMBINED CYCLE COGENERATION FACILITY | DUCT BURNER | 12.31 | NATURAL GAS | 315 | MMBTU/H | TURBINE AND DUCT BURNER EMISSIONS COMBINED IN ONE STACK. DUCT BURNER ALWAYS FIRES NATURAL GAS. |  | Carbon Monoxide | P | GOD COMBUSTION PRACTICE | 0.08 | LB/MMBTU | [5 empty] | 0.08 | LB/MMBTU
AR-0026 | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1999-05-05 | 1999 | COMBUSTION TURBINE COMBINED CYCLE COGENERATION FACILITY | BOILER, NATURAL GAS | 12.31 | NATURAL GAS | 362 | MMBTU/H | BOILER FIRES NATURAL GAS AND FUEL OIL. BOILER WILL PROVIDE STEAM FOR STEAM TURBINE AND INTERNATIONAL PAPER MILL. |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.044 | LB/MMBTU | [5 empty] | 0.044 | LB/MMBTU
LA-0119 | LAKE CHARLES REFINERY | CONOCO INC. | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1999-08-12 | 1999 | PERMIT TO IMPLEMENT THE PETROZUATA SYNCRUDE PROJECT, ALLOWING REFINERY TO PROCESS A MIXTURE OF VIRGIN CRUDE AND CUTTER STOCK. SECURES A GUARANTEED CRUDE SUPPLY AND INCREASE PRODUCTION OF HEAVY PRODUCTS. MODIFICATION TO VARIOUS PROCESS UNITS WILL BE REQUIRED TO ENABLE THE FACILITY TO PROCESS THE INCREASED SULFUR LOAD ASSOCIATED WITH REFINING THE SYNCRUDE. CONOCO WILL REMOVE AN EXISTING HEATER, CONSTRUCT A NEW HEATER, AND MODIFY EQUIPMENT AND/OR INCREASE CAPACITIES OF THE FOLLOWING PROCESS UNITS: NOS. 3 AND 4 CRUDE TOPPING UNITS; NOS. 2 AND 3 CRUDE VACUUM UNITS; NOS. 4 AND 7 HYDRODESULFURIZATION UNITS; FRACTIONATOR; NOS. 4 AND 5 HYDROGEN SYSTEMS; HYDROGEN PURIFICATION AND DISTRIBUTION; NOS. 1, 2, 3, AND 5 SOUR WATER STRIPPERS; NO. 4 SULFUR RECOVERY UNIT; MARINE TANK FARM; MARINE DOCK; TANK FARM; AND Y-5 COOLING TOWER. | HEATER, CRUDE VACUUM UNIT FEED (H-20002) | 12.39 | NATURAL GAS | 150 | MMBTU/H | HEATER BURNS NATURAL GAS AND REFINERY OFF GAS. |  | Carbon Monoxide | P | ULTRA LOW NOX BURNERS (ULNB), GOOD DESIGN, USING GASEOUS FUEL, PROPER OPERATING TECHNIQUES. | 3 | LB/H* | HOURLY MAXIMUM | OPERATING PERMIT | 13.1 | T/YR* | ANNUAL MAXIMUM |  |  |  | *AS SET BY PSD-LA-584(M-3), DATED SEPTEMBER 20, 2002. PSD-LA-584(M-2) ORIGINALLY ESTABLISHED LIMITS AT 12.6 LB/H (HOURLY MAXIMUM) AND 55.2 T/YR (ANNUAL MAXIMUM).
LA-0119 | LAKE CHARLES REFINERY | CONOCO INC. | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1999-08-12 | 1999 | PERMIT TO IMPLEMENT THE PETROZUATA SYNCRUDE PROJECT, ALLOWING REFINERY TO PROCESS A MIXTURE OF VIRGIN CRUDE AND CUTTER STOCK. SECURES A GUARANTEED CRUDE SUPPLY AND INCREASE PRODUCTION OF HEAVY PRODUCTS. MODIFICATION TO VARIOUS PROCESS UNITS WILL BE REQUIRED TO ENABLE THE FACILITY TO PROCESS THE INCREASED SULFUR LOAD ASSOCIATED WITH REFINING THE SYNCRUDE. CONOCO WILL REMOVE AN EXISTING HEATER, CONSTRUCT A NEW HEATER, AND MODIFY EQUIPMENT AND/OR INCREASE CAPACITIES OF THE FOLLOWING PROCESS UNITS: NOS. 3 AND 4 CRUDE TOPPING UNITS; NOS. 2 AND 3 CRUDE VACUUM UNITS; NOS. 4 AND 7 HYDRODESULFURIZATION UNITS; FRACTIONATOR; NOS. 4 AND 5 HYDROGEN SYSTEMS; HYDROGEN PURIFICATION AND DISTRIBUTION; NOS. 1, 2, 3, AND 5 SOUR WATER STRIPPERS; NO. 4 SULFUR RECOVERY UNIT; MARINE TANK FARM; MARINE DOCK; TANK FARM; AND Y-5 COOLING TOWER. | HEATER, NO. 4 CTU (H-4050) | 12.39 | NATURAL GAS | 237 | MMBTU/H | UNIT BURNS NATURAL GAS AND REFINERY OFF GAS. FORMERLY IDENTIFIED AS H-40001 |  | Carbon Monoxide | P | ULTRA LOW NOX BURNERS (ULNB), GOOD DESIGN, USE GASEOUS FUEL, PROPER OPERATING TECHNIQUES | 4.7 | LB/H* | HOURLY MAXIMUM | OPERATING PERMIT | 20.8 | T/YR* | ANNUAL MAXIMUM | 0.02 | LB/MMBTU | CALCULATED BY CATC | *AS SET BY PSD-LA-584(M-3), DATED SEPTEMBER 20, 2002. PSD-LA-584(M-2) ORIGINALLY ESTABLISHED LIMITS AT 19.9 LB/H (HOURLY MAXIMUM) AND 87.2 T/YR (ANNUAL MAXIMUM).
*PA-0193 | MERCK AND COMPANY - WEST POINT PLANT | MERCK AND COMPANY, INC | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 1999-08-26 | 1999 | COGEN PLANT | BOILER, NATURAL GAS, (2) | 12.31 | NATURAL GAS | 249 | MMBTU/H | LO-NOX BURNERS, FLUE GAS RECIRCULATION AND SCR SYSTEM |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 0.37 | LB/MMBTU | [5 empty] | 0.37 | LB/MMBTU
SC-0049 | SKYGEN | BROAD RIVER ENERGY, LLC | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 1999-12-02 | 1999 |  | THREE NATURAL GAS FIRED BOILERS (UTILITY) | 12.31 | NATURAL GAS | 230 | MMBTU/H | 1700 H/YR MAX OPERATION PER BOILER. |  | Carbon Monoxide | P | GOOD COMBUSTION AND CLEAN FUELS | 0.06 | LB/MMBTU | [5 empty] | 0.06 | LB/MMBTU
TX-0294 | GATEWAY POWER PROJECT | GATEWAY POWER PROJECT LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-03-20 | 2000 | THIS IS A GRASS-ROOTS ELECTRICAL GENERATION FACILITY. THE PRIMARY EQUIPMENT CONSISTS OF THREE COMBUSTION TURBINES DRIVING ELECTRICAL GENERATORS, WHERE EACH GENERATOR IS RATED NOMINALLY AT 170 MW. THE TURBINES OPERATE IN COMBINED CYCLE MODE IN WHICH A SUPPLEMENTARY FIRED HEAT RECOVERY STEAM GENERATOR (HRSG) WILL BE UTILIZED. THE ASSOCIATED DUCT BURNERS WILL EACH HAVE A MAXIMUM RATING OF 290 MMBTU/H HEAT INPUT. THE TURBINES AND DUCT BURNERS WILL BE FIRED WITH PIPELINE-QUALITY NAT GAS ONLY. PROCESS STEAM FROM THE HRSGS WILL BE USED BY THREE STEAM TURBINES TO GENERATE UP TO 90 MW ADDITIONAL ELECTRICITY EACH. THE THREE COMBINED CTG-HRSG UNITS WILL HAVE A NOMINAL CAPACITY OF 800 MW. | (3) DUCT BURNERS | 12.31 | NAT GAS | 160 | MMBTU/H, EA | PERMIT INDICATES STANDARD EMISSION LIMITS FOR NOX, CO, AND VOC SEPARATELY FOR THIS PROCESS, HOWEVER THEY ARE CONSIDERED AS A COMBINED PROCESS WITH THE TURBINES. |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.1 | LB/MMBTU | EACH UNIT |  |  |  |  | 0.1 | LB/MMBTU | EACH UNIT
AK-0037 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFIDE CONTENT TO 0.01% FROM 0.001%, AN INCREASE IN OPERATING HOURS OF P708C FROM 200 TO 600 HOURS PER YEAR, THE REMOVAL OF PERCENT EFFICIENCY REQUIREMENTS FOR AS1310 AND 1320, AND USE OF THERMAL OXIDATION TO CONTROL EMISSIONS FROM AS1320. | CRUDE HEATER, H101A | 12.39 | NATURAL GAS* | 140 | MMBTU/H | INSTALLED PRIOR TO 1975, THEREFORE NOT REQUIRED TO COMPLY WITH THE PSD PROGRAM. DESIGN CAPACITY OF 140.0 MMBTU/H AUTHORIZED RATED CAPACITY IS 1 MMBTU/H. *FUELS ARE NATURAL GAS, REFINERY GAS AND LPG. NO INDICATION IS PROVIDED AS TO WHICH IS THE PRIMARY FUEL. |  | Carbon Monoxide | N | NONE INDICATED. | 0.04 | LB/MMBTU | [5 empty] | 0.04 | LB/MMBTU |  | ESTIMATED EMISSIONS ARE 24.5 T/YR, BUT THIS IS NOT AN EMISSION LIMIT.
AK-0037 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFIDE CONTENT TO 0.01% FROM 0.001%, AN INCREASE IN OPERATING HOURS OF P708C FROM 200 TO 600 HOURS PER YEAR, THE REMOVAL OF PERCENT EFFICIENCY REQUIREMENTS FOR AS1310 AND 1320, AND USE OF THERMAL OXIDATION TO CONTROL EMISSIONS FROM AS1320. | CRUDE HEATER, H101B | 12.39 | NATURAL GAS* | 165 | MMBTU/H | DESIGN CAPACITY IS 165.0 MMBTU/H BUT AUTHORIZED RATED CAPACITY IS 1 MMBTU/H. *SOURCE BURNS COMBINATION OF REFINERY GAS, NATURAL GAS, AND LIQUID PETROLEUM GAS. IT IS NOT SPECIFIIED WHICH TYPE OF FUEL IS PRIMARY. |  | Carbon Monoxide | N | NONE INDICATED | 0.04 | LB/MMBTU | [5 empty] | 0.04 | LB/MMBTU |  | ADDITIONAL ESTIMATED EMISSIONS ARE 28.9 T/YR, BUT THIS IS NOT A LIMIT.
TX-0395 | DIAMOND SHAMROCK MCKEE PLANT | DIAMOND SHAMROCK REFINING COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-05-23 | 2000 |  | NO. 1 REFORMER CHARGE HEATER | 12.39 | REFINERY GAS | 248 | MMBTU/H |  |  | Carbon Monoxide | N |  | 6.95 | LB/H |  |  | 30.42 | T/YR |  | 0.03 | LB/MMBTU
TX-0395 | DIAMOND SHAMROCK MCKEE PLANT | DIAMOND SHAMROCK REFINING COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-05-23 | 2000 |  | NO 1 INTERHEATER | 12.39 | REFINERY GAS | 147.2 | MMBTU/H |  |  | Carbon Monoxide | N |  | 4.13 | LB/H |  |  | 18.06 | T/YR |  | 0.03 | LB/MMBTU | CALCULATED
TX-0333 | MONT BELVIEU COMPLEX | TAME ENVIRO-FUEL PARTNERS - ENTERPRISE PRODUCTS CO | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-12-05 | 2000 | TAME ENVIRO-FUELS PARTNERS (TEF) IS PROPOSING TO CONSTRUCT A NEW TERTIARY- AMYL-METHYL-ETHER (TAME) MANUFACTURING PLANT AT THE MONT BELVIEU COMPLEX, WHICH IS OWNED BY ENTERPRISE PRODUCTS COMPANY. LIKE METHYL-TERTIARY-BUTYL- ETHER (MTBE), TAME IS AN OXYGENATED ADDITIVE THAT INCREASES THE OCTANE RATING OF AUTO GASOLINE WHILE DECREASING AUTO EMISSIONS (NOX & VOC). THE EMISSIONS FROM THIS PROJECT WILL CONSIST MAINLY OF PRODUCTS OF COMBUSTION & VOC. THE PLANT''S FIREWATER ENGINE, WHICH POWERS THE WATER SPRAY SYSTEM WILL BE USED TO FIGHT FIRES. THE REVIEW OF THIS PROJECT WAS LENGTHENED CONSIDERABLY DUE TO A NUMBER OF THINGS. FIRST, IT HAS BEEN ASSIGNED (FOR VARIOUS REASONS) TO THREE ENGINEERS. SECOND, THERE WERE TWO TECHNICAL ISSUES THAT REQUIRED EXPERTISE OUTSIDE OF THE AIR PERMITS DIVISION. THIS ISSUE TOOK OVER A YEAR & THE EFFORTS OF STAFF FROM SEVERAL AGENCY DIVISIONS TO RESOLVE. THE BOTTOM LINE IS THAT WE WILL ALLOW ENTERPRISE & ALL ITS JOINT VENTURES TO BE VIEWED SEPARATELY FOR NSR, BUT AS A SINGLE ENTITY FOR TITLE V PURPOSES, HOWEVER, THIS IS THE EXCEPTION TO THE RULE. THE TNRCC POLICY IS THAT AS OF SEPTEMBER 1, 1999, ALL SOURCES AT A SITE THAT ARE OPERATED UNDER ONE OR MORE COMPANIES THAT SHARE COMMON OWNERSHIP &/OR CONTROL WILL BE REVIEWED THE SAME UNDER NSR & TITLE V. THIS MEANS ONE NSR & ONE TITLE V PERMIT FOR THE ENTIRE SITE, OR MULTIPLE NSR & MULTIPLE TITLE V PERMITS (TO EACH JOINT VENTURE). THIS FACILITY IS AUTHORIZED TO CONTAIN A MAX OF 2 TONS OF CL2 AT ANY ONE TIME. | DUCT BURNERS | 12.31 | TURBINE EXHAUST | 128 | MMBTU/H | PERMIT DOES NOT INDICATE THE USE OF SUPPLEMENTAL FUEL. THE TURBINE'S EXHAUST FEEDS INTO THE DUCT BURNER. |  | Carbon Monoxide | P | CATALYTIC OXIDATION | 0.069 | LB/MMBTU |  | NSPS |  |  |  | 0.069 | LB/MMBTU
TN-0146 | FLORIM, USA, INC. | FLORIM, USA, INC. | TN | TENNESSEE DIV OF AIR POLLUTION CONTROL | 2000-12-20 | 2000 | CERAMIC TILE MANUFACTURING PROCESS CONSISTING OF RAW MATERIAL HANDLING, SPRAY DRYING, TILE PREPARATION, AND TILE FIRING OPERATIONS. THE COMPANY APPLIED FOR A PSD PERMIT TO INCREASE THE MATERIAL INPUT RATE THROUGH THE FACILITY'S TILE KILNS. | GAS-FIRED KILNS | 12.31 | NATURAL GAS | 125 | MMBTU/H | Seven (7) gas-fired tile kilns and one (1) gas-fired trim kiln with lime injection/coated baghouse controls. |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES (E. G. BURNER MAINTENANCE, ADEQUATE EXCESS AIR, TIMELY BURNER/SYSTEM UPGRADES). | 1.47 | LB/MMBTU |  |  | 183.9 | LB/H |  | 1.47 | LB/MMBTU |  | The facility must meet compliance with production limits and recordkeeeping requirements to demonstrate compliance with emission limits.
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | 2001 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORIZED FIRING RATE WILL BE 481 MMBTU/H ON A ROLLING 12 MONTH AVERAGE, AND 502 MMBTU/H MAXIMUM HOURLY FIRING RATE. THE ADDITION OF THE NEW FURNACE TRIGGERED PSD REVIEW. | FURNACE HF-01 | 12.39 | ETHANE | 238 | MMBTU/H | 200 MMBTU/H AVE. FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% THEANE/PROPANE MIXTURE. |  | Carbon Monoxide | N | NONE INDICATED | 18.7 | LB/H |  |  | 7.3 | T/YR |  | 0.08 | LB/MMBTU | CALCULATED USING MAX THROUGHPUT
IN-0085 | PSEG LAWRENCEBURG ENERGY FACILITY | PSEG LAWRENCEBURG ENERGY FACILITY | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-06-07 | 2001 |  | AUXILIARY BOILER, NATURAL GAS | 12.31 | NATURAL GAS | 124.6 | MMBTU/H | AUXILIARY BOILER IS LIMITED TO 1000 H/YR OF OPERATION |  | Carbon Monoxide | P | GOOD COMBUSTION. NATURAL GAS ONLY | 0.082 | LB/MMBTU |  |  | 10.28 | LB/H |  | 0.082 | LB/MMBTU
OK-0045 | REDBUD POWER PLT | REDBUD ENERGY LP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-15 | 2001 | ELECTRICAL GENERATION FACILITY | BOILER, AUXILIARY | 12.31 | NATURAL GAS | 20 | MMBTU/H | boiler operates < 3000 hours per year |  | Carbon Monoxide | P | GOOD OPERATING PRACTICE | 0.082 | LB/MMBTU | [5 empty] | 0.082 | LB/MMBTU
AR-0057 | TENASKA ARKANSAS PARTNERS, LP | TENASKA ARKANSAS PARTNERS, LP | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-10-09 | 2001 | ELECTRIC POWER GENERATING STATION. FACILITY WAS NEVER CONSTRUCTED AND THE PERMIT WAS VOIDED 1/07/03. ADDITIONAL PLANTWIDE EMISSIONS: PM10 858 T/YR, AMMONIA 844 T/YR. | BOILER, NATURAL GAS, (2) | 12.31 | NATURAL GAS | 122 | MMBTU/H | Throughput for each boiler. |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES. | 0.11 | LB/MMBTU | [5 empty] | 0.11 | LB/MMBTU
AR-0055 | NUCOR YAMATO STEEL (ARMOREL) | NUCOR YAMATO STEEL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-10-10 | 2001 | STEEL MILL. | REHEAT FURNACE | 12.31 | NATURAL GAS | 225 | MMBTU/H |  |  | Carbon Monoxide | P | CLEAN FUELS | 0.0824 | LB/MMBTU | [5 empty] | 0.0824 | LB/MMBTU
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | 2001 | ELECTRICITY GENERATION | AUXILIARY BOILER | 12.31 | NATURAL GAS | 120 | MMBTU/H |  |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 6 | LB/H |  |  | 10.8 | T/YR |  | 0.05 | LB/MMBTU
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BOILER NO. 12 | 12.39 |  | 245 | MMBTU/H | EMISSION PT NO: BOILER-12. SHALL BE SHUTDOWN. |  | Carbon Monoxide | N | NONE INDICATED | 20.2 | LB/H |  |  | 88.4 | T/YR |  | 0.08 | LB/MMBTU | CALCULATED
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BTU-NO. 1 REACTOR FEED HEATER | 12.39 |  | 121.74 | MMBTU/H | EMISSION POINT NO. BTU-HF103. |  | Carbon Monoxide | N | NONE INDICATED | 10 | LB/H |  |  | 43.9 | T/YR |  | 0.082 | LB/MMBTU | CALCULATED
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ISOM II WEST REACTOR FEED HEATER | 12.39 |  | 104.25 | MMBTU/H | EMISSION POINT NO. BTU-HF106. |  | Carbon Monoxide | N | NONE INDICATED | 8.6 | LB/H |  |  | 37.6 | T/YR |  | 0.082 | LB/MMBTU | CALCULATED
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ORTHOXYLENE II HEATER | 12.39 |  | 226.42 | MMBTU/H | EMISSION POINT NO.: ORTHOII-H2. |  | Carbon Monoxide | N | NONE INDICATED | 18.6 | LB/H |  |  | 81.7 | T/YR |  | 0.082 | LB/MMBTU | CALCULATED
CA-1113 | PRAXAIR | PRAXAIR | CA | SOUTH COAST AQMD, CA | 2002-03-15 | 2002 |  | HEATER-OTHER PROCESS | 12.39 | WASTE GAS | 117.6 | MMBTU/H | EQUIP: , MFR: SELAS FLUID PROCESING CORPORATION, TYPE: HYDROGEN REFORMER, MODEL: LH 1207 B001, FUNC EQUIP: PROVIDES HEAT TO CATYST FILLED TUBES TO PRODUCE HYDROGEN-*, FUEL_TYPE: NATURAL GAS (WARM UP AND SUPPLEMENT), SCHEDULE: CONTINUOUS, H/D: 24, D/W: 7, W/Y: 52, NOTES: AMMONIA IS MIXED INTO FLUE GAS, AND THE MIXTURE IS PASSED THROUGH A CATALYST BED, IN WHICH THE AMMONIA REACTS WITH NOX REDUCING IT TO N2. SCR DESIGN OPERATING TEMPERATURE IS 760F, AND DESIGN REMOVAL EFFICIENCY IS 90%. A SOURCE TEST IS REQUIRED WITHIN 90 DAYS AFTER STARTUP FOR NOX, CO, ROG, NH3, PM, SOX. THE FACILITY IS IN RECLAIM, AND WILL HAVE CEMS FOR NOX AND O2. THE PERMIT REQUIRES CEMS FOR NH3 ALSO; HOWEVER, THE APPLICANT IS REQUESTING TO SUBSTITUTE A PARAMETRIC MONITORING METHOD. |  | Carbon Monoxide | N |  | 4000 | PPMVD @ 3% O2 | 1H | N/A | [5 empty] | NOT AVALUABLE
TX-0386 | AMELLA ENERGY CENTER | CALPINE CONSTRUCTION FINANCE CO. LP | TX | CITY OF HOUSTON BUREAU AIR QUAL CTRL, TX | 2002-03-26 | 2002 |  | AUXILIARY BOILER | 12.31 | NATURAL GAS | 155 | MMBTU/H |  |  | Carbon Monoxide | N |  | 13.9 | LB/H | [5 empty] | 0.08 | LB/MMBTU
NJ-0043 | LIBERTY GENERATING STATION | LIBERTY GENERATING STATION | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2002-03-28 | 2002 | ELECTRICITY GENERATION | AUXILIARY BOILER | 12.31 | NATURAL GAS | 200 | MMBTU/H | NATURAL GAS USAGE RESTRICTED TO 181.0 MILLION SCF/YR (EQUIVALENT TO A 10% ANNUAL CAPACITY FACTOR) |  | Carbon Monoxide | A | CO CATALYST | 100 | PPMVD @7% O2 |  |  | 17.4 | LB/H |  | 0.087 | LB/MMBTU |  | BASIS OF LIMIT IS STATE.
TN-0153 | WILLIAMS REFINING & MARKETING, L.L.C. | WILLIAMS REFINING & MARKETING, L.L.C. | TN | MEMPHIS AND SHELBY CO HEALTH DEPT, TN | 2002-04-03 | 2002 | PETROLEUM REFINERY | BOILER, NO. 10 | 12.31 | NATURAL GAS | 180 | MMBTU/H | annual capacity factor (ACF) for natural gas, coal or oil shall not exceed 10% |  | Carbon Monoxide | N |  | 0.18 | LB/MMBTU | [5 empty] | 0.18 | LB/MMBTU
CA-1024 | AES HUNTINGTON BEACH | AES HUNTINGTON BEACH | CA | SOUTH COAST AQMD, CA | 2002-08-01 | 2002 |  | BOILER: >= 50 MMBTU/HR | 12.31 | NATURAL GAS | 225 | MW | EQUIP: ELECTRIC UTILITY BOILER, MFR: BABCOCK & WILCOX, TYPE: MULTI-WALL FIRED, MODEL: , FUNC EQUIP: USE IS CURRENTLY FOR PEAK POWER DEMAND PERIODS, FUEL_TYPE: , SCHEDULE: VARIABLE, H/D: 24, D/W: 5, W/Y: 20, NOTES: FACILITY APPLIED TO BRING THIS RETIRED BOILER BACK INTO SERVICE. FACILITY IS EXPERIENCING DIFFICULTY MEETING NOX AND AMMONIA LIMITS ON ONE- HOUR AVERAGING BASIS, AND DISTRICT IS CONSIDERING REQUEST FOR LONGER AVERAGING TIME. SOURCE TEST RESULTS: PPM@3%O2, GR/DSCF: 225 MW: NOX-3.5, CO-0.0, VOC- 4.2, NH3-3.1, PM-.001. 169 MW: NOX-4.2, NH3-1.6, PM-.002. 115MW: NOX-3.8, NH3-0.5. 90 MW: NOX-4.5, NH3-0.7, PM-.004 |  | Carbon Monoxide | A | OXIDATION CATALYST | 5 | PPMVD @3% O2 | 1-H AV | N/A | [5 empty] | NOT AVAILABLE
CO-0052 | ROCKY MOUNTAIN ENERGY CENTER, LLC. | ROCKY MOUNTAIN ENERGY CENTER, LLC. | CO | COLORADO DEPT OF HEALTH - AIR POLL CTRL | 2002-08-11 | 2002 | ELECTRIC POWER | NATURAL GAS FIRED BOILER (AUXILIARY BOILER) | 12.31 | NATURAL GAS | 129 | MMBTU/H | THIS BOILER IS USED TO HEAT AND MAINTAIN TEMPERATURE IN STEAM TURBINE CONDENSER. |  | Carbon Monoxide | P | GOOD COMBUSTION CONTROL PRACTICES. | 0.039 | LB/MMBTU | [5 empty] | 0.039 | LB/MMBTU
AR-0070 | GENOVA ARKANSAS I, LLC | GENOVA ARKANSAS I, LLC | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-08-23 | 2002 | COMBINED CYCLE POWER PLANT | DUCT BURNERS | 12.31 | NATURAL GAS | 200 | MMBTU/H | 2 DUCT BURNERS UNDER ANY SCENARIO. INFORMATION PROVIDED IS FOR EACH UNIT. |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.25 | LB/MMBTU | [5 empty] | 0.25 | LB/MMBTU
GA-0096 | SOUTHERN LNG, INC. ELBA ISLAND FACILITY | SOUTHERN LNG, INC. | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2003-02-17 | 2003 | LIQUIFIED NATURAL GAS TERMINAL | LNG VAPORIZER (3) | 12.31 | NATURAL GAS | 121.4 | MMBTU/H |  |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.164 | LB/MMBTU | [5 empty] | 0.164 | LB/MMBTU
GA-0103 | ELBA ISLAND, LNG TERMINAL | SOUTHERN LNG INC | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2003-02-17 | 2003 | LIQUEFIED NATURAL GAS (LNG) TERMINAL | LNG VAPORIZER, (3) | 12.31 | NATURAL GAS | 121.4 | MMBTU/H |  |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 0.164 | LB/MMBTU | [5 empty] | 0.164 | LB/MMBTU
VA-0270 | VCU EAST PLANT | VIRGINIA COMMONWEALTH UNIVERSITY | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-31 | 2003 |  | BOILER NATUAL GAS | 12.31 | NATURAL GAS | 150 | MMBTU/H | This is one of 3 boilers |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES. | 14.9 | LB/H | each unit |  |  |  |  | 0.1 | LB/MMBTU
VA-0278 | VCU EAST PLANT | Virginia Commonwealth University | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-31 | 2003 | STEAM GENERATING PLANT AT UNIVERSITY | BOILER, NATURAL GAS, (3) | 12.31 | NATURAL GAS | 150.6 | MMBTU/H | Throughput for each. The 3 boilers shall consume no more than 3,500 million cf of natural gas per year |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 14.9 | LB/H | [5 empty] | 0.1 | LB/MMBTU | calculated
WI-0204 | UWGP - FUEL GRADE ETHANOL PLANT | UNITED WISCONSIN GRAIN PRODUCERS | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2003-08-14 | 2003 | FERMENTATION BASED PROCESS WITH DISTILLATION, MOLECULAR SIEVES FOR FINAL WATER REMOVAL. ETHANOL DENATURED USING GASOLINE. | BOILER /OXIDIZER ( DRYER / DISTILLATION), P10 | 12.31 | NATURAL GAS | 140 | MMBTU/H | Boiler works as control device. RECEIVES VOC'S FROM DISTILLATION AND RELATED PROCESSES AND FROM Distillers dried grain with solubles (DDGS) DRYER (85 MMBTU/HR.). SUBJECT TO DB |  | Carbon Monoxide | N |  | 18.4 | LB/H | [5 empty] | 0.13 | LB/MMBTU | calculated | SYNTHETIC MINOR SOURCE. BOILER / OXIDIZER CONSUMES CO PRODUCED BY DDGS DRYER
PA-0231 | UNITED REFINERY CO. | UNITED REFINERY CO | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2003-10-09 | 2003 | THE MODIFICATIONS INCLUDE THE INSTALLATION OF THREE NEW SOURCES AND MODS TO EXISTING SOURCES, THIS PERMIT ACTION IS SUBJECT TO SUBPARTS J,GGG QQQ OF THE NSPS, MACT SUBPARTS CC AND UUU AND NESHAPS SUBPARTS FF AND IS PSD FOR CO. | NORTH CRUDE HEATER | 12.39 | REFINERY GAS | 147 | MMBTU/H | The north crude heater was modified by installing low NOx burners. The reduction of NOx emissions reduces the overall increase below significant levels allowing the project to net out" of NSR and PSD for NOx." |  | Carbon Monoxide | P | BACT AND BAT REMAIN AS GOOD COMBUSTION PRACTICES | 9.27 | LB/H |  |  | 40.6 | T/YR |  | 0.063 | LB/MMBTU | Calculated based on heat input | This modification is subject to PSD for CO emissions and BACT is required for this pollutant.
PA-0231 | UNITED REFINERY CO. | UNITED REFINERY CO | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2003-10-09 | 2003 | THE MODIFICATIONS INCLUDE THE INSTALLATION OF THREE NEW SOURCES AND MODS TO EXISTING SOURCES, THIS PERMIT ACTION IS SUBJECT TO SUBPARTS J,GGG QQQ OF THE NSPS, MACT SUBPARTS CC AND UUU AND NESHAPS SUBPARTS FF AND IS PSD FOR CO. | DELAYED COKER UNIT, HEATER | 12.39 | REFINERY GAS | 116 | MMBTU/H | The unit is subject to the NSPS 40 CFR Subpart J, Subpart GGG, Subpart QQQ. The unit is also subject to MACT standards in 40 CFR 63 Subpart CC, and NESHAP requirements in 40 CFR 61 Subpart FF. |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 8.28 | LB/H |  |  | 36.3 | T/YR |  | 0.07 | LB/MMBTU | Calculated using heat input | This modification is subject to PSD for CO emissions and BACT is required for this pollutant.
WV-0023 | MAIDSVILLE | LONGVIEW POWER, LLC | WV | WEST VIRGINIA AIR POLLUTION CONTROL COMM | 2004-03-02 | 2004 | PULVERIZED COAL-FIRED STEAM GENERATOR CAPABLE OF GENERATING 600MW OF ELECTRIC POWER. THIS FACILITY IS A GREEN FIELD SITE, WHICH INCLUDES A 6,114 MMBTU COAL-FIRED BOILER, 225 MMBTU NATURAL GAS-FIRED AUX BOILER, EMERGENCY GENERATOR, FIRE WATER PUMP ENGINE, COOLING TOWERS, AND MATERIAL HANDLING SYSTEMS. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 225 | mmbtu/h | LIMITED TO NATURAL GAS USE AND 3,000 HOURS OF OPERATION PER YEAR |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES, USE OF NATURAL GAS | 0.04 | LB/MMBTU | 3 HOUR ROLLING AVERAGE | N/A |  |  |  | 0.04 | LB/MMBTU | 3 HOUR ROLLING AVERAGE | LIMITED TO USE OF NATURAL GAS AND 3,000 HOURS OF OPERATION PER YEAR
OH-0241 | MILLER BREWING COMPANY - TRENTON | MILLER BREWING COMPANY | OH | HAMILTON CO-SOUTHWESTERN OH APCA | 2004-05-27 | 2004 | BEER BREWING AND PACKAGING. | BOILER (2), NATURAL GAS | 12.31 | NATURAL GAS | 238 | MMBTU/H | TWO BOILERS, CAPABLE OF BURNING AND WITH LIMITS FOR COAL, NATURAL GAS, NUMBERS 2 AND 6 FUEL OILS. POUND PER HOUR LIMITS ARE FOR EACH BOILER; AND EXCEPT FOR VOC AND CO, ALL T/YR LIMITS ARE FOR BOTH BOILERS COMBINED. THESE LIMITS FOR THE NATURAL GAS. |  | Carbon Monoxide | N |  | 20 | LB/H | EACH BOILER | SIP | 87.6 | T/YR | EACH BOILER, ON A ROLLING 12-MO. | 0.084 | LB/MMBTU
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | AUXILLIARY NAT. GAS FIRED BOILER (B25, S25) | 12.31 | NATURAL GAS | 229.8 | MMBTU/H | THE AUXILIARY BOILER WILL BE USED TO PREHEAT STEAM TURBINE, PROVIDE PLANT HEATING AND PROVIDE SUPPLEMENTAL STEAM TO AUXILIARY EQUIPMENT WHEN THE MAIN SCPC BOILER IS OFFLINE. THE AUXILIARY BOILER WILL BE PACKAGED BOILER THAT WILL COMBUST ONLY NATURAL GAS. THE HOURS OF THE OPERATION OF THE AUXILIARY BOILER WILL BE LIMITED TO 2,000 HOURS IN ANY 12 CONSECUTIVE MONTHS. |  | Carbon Monoxide | P | NATURAL GAS, GOOD COMBUSTION PRACTICES, LOW NOX BURNER | 0.08 | LB/MMBTU | 2000 H / 12 MO. ROLLING |  | 18.4 | LB/H |  | 0.08 | LB/MMBTU
LA-0194 | SABINE PASS LNG IMPORT TERMINAL | SABINE PASS LNG, LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2004-11-24 | 2004 | LNG TO BE TRANSFERRED FROM MARINE VESSELS INTO PRESSURIZED TANKS FOR STORAGE, THEN REGASIFIED USING VAPORIZERS. THE VAPORIZED NATURAL GAS WILL BE MEASURED AND SENT TO TRANSMISSION PIPELINES. | SUBMERGED COMBUSTION VAPORIZERS (24) | 12.31 |  | 108 | MMBTU/H |  |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 9.47 | LB/H | HOURLY MAXIMUM | OPERATING PERMIT | 31.22 | T/YR | ANNUAL MAXIMUM | 80 | PPMV @ 5% O2* |  | *0.066 LB/MMBTU = ANNUAL AVERAGE 9.47 LB/H REPRESENTS STARTUP OPERATING SCENARIO
OR-0046 | TURNER ENERGY CENTER, LLC | CALPINE | OR | OREGON DEPT OF ENVIRONMENTAL QUALITY | 2005-01-06 | 2005 | 620 MW TOTAL COMBINED CYCLE GAS TURBINES (2 TURBINES WITH HRSGS) | AUXILIARY BOILER | 12.31 | NATURAL GAS | 417904 | MMBTU/YR | BOILER USED TO PROVIDE AUXILIARY STEAM FOR STANDBY AND STARTUP CONDITIONS WILL BE OPERATED A MAXIMUM OF 3000 HOURS/YR. |  | Carbon Monoxide | A | OXIDATION CATALYST | 0.038 | LB/MMBTU | 3-H BLOCK |  |  |  |  | 0.038 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | VACUUM CRUDE CHARGE HEATER | 12.39 | REFINERY FUEL GAS OR NG | 101 | MMBTU/H | THIS UNIT IS IDENTIFIED BY EQUIPMENT ID # B-02100 |  | Carbon Monoxide | N |  | 0.04 | LB/MMBTU | THREE-HOUR ROLLING AVG |  |  |  |  | 0.04 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | HYDROCRACKER UNIT MAIN FRACTIONATOR HEATER | 12.39 | REFINERY FUEL GAS OR NG | 211 | MMBTU/H | THIS UNIT IS IDENTIFIED BY EQUIPMENT ID # B-10500 |  | Carbon Monoxide | N |  | 0.04 | LB/MMBTU | THREE-HOUR ROLLING AVG |  |  |  |  | 0.04 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT CHARGE HEATER | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 122 | MMBTU/H | THIS UNIT IS IDENTIFIED BY EQUIPMENT ID # B-05110 |  | Carbon Monoxide | N |  | 0.04 | LB/MMBTU | 3-HR AVERAGE | MACT
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT INTERHEATER NO. 1 | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 192 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY EQUIPMENT ID # B-05120 |  | Carbon Monoxide | N |  | 0.04 | LB/MMBTU | 3-HR AVERAGE | MACT |  |  |  | 0.04 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT INTERHEATER NO. 2 | 12.39 | REFINERY FUEL GAS OR NATURAL GAS | 129 | MMBTU/H | THIS EQUIPMENT IS IDENTIFIED BY ID # B-05130 |  | Carbon Monoxide | N |  | 0.04 | LB/MMBTU | 3-HR AVERAGE | NESHAP |  |  |  | 0.04 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | DISTILLATE HYDROTREATER SPLITTER REBOILER | 12.39 | REFINERY FUEL GAS OR NATURAL GAS | 117 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY ID # B-08509 |  | Carbon Monoxide | N |  | 0.04 | LB/MMBTU | 3-HR AVERAGE | NESHAP |  |  |  | 0.04 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | BUTANE CONVERSION UNIT ISOSTRIPPER REBOILER | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 222 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY ID # B-15110 |  | Carbon Monoxide | N |  | 0.04 | LB/MMBTU | 3-HR AVERAGE | NESHAP | [5 empty] | NOT AVAILABLE
TX-0478 | CITGO CORPUS CHRISTI REFINERY - WEST PLANT | CITGO REFINING AND CHEMICALS COMAPNY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-04-20 | 2005 |  | MIXED DISTILLATE HYDROHEATER REBOILER HEATER | 12.39 | REFINERY FUEL GAS | 82 | MMBTU/H | THE MDH UNIT REMOVES ORGANIC NITROGEN AND SULFUR FROM THE FEED STREAMS. FEEDSTOCK IS MIXED WITH HYDROGEN , HEATED, AND FED TO A REACTOR. A CATALYTIC REACTION CONVERTS THE ORGANIC SULFUR TO HYDROGEN SULFIDE AND THE NITROGEN COMPOUNDS TO AMMONIA. THE EFFLUENT STREAM IS COOLED AND EXCESS HYDROGEN REMOVED FOR RECYCLE. HYDROGEN SULFIDE IS REMOVED FROM THE HYDROGEN STREAM BY AN AMINE ABSORBER AND ROUTED TO THE SRU. NEW EQUIPMENT UNDER THE AMENDMENT INCLUDES A SECOND REACTOR, ADDITIONAL PREHEAT TRAIN, AN ADDITIONAL REACTOR PRODUCT FLASH DRUM, A HYDROGEN PURIFICATION MEMBRANE AND AN ADDITIONAL HYDROGEN MAKEUP COMPRESSOR. AS PART OF THE AMENDMENT, THE FRACTIONATOR REBOILER WILL BE RETROFIT WITH LOW NOX BURNERS. |  | Carbon Monoxide | N |  | 6.8 | LB/H |  |  | 29.7 | T/YR
TX-0492 | VIRTEX PETROLEUM COMPANY DOERING RANCH GAS PLANT | VIRTEX PETROLEUM INC. | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-05 | 2005 | VIRTEX CURRENTLY OPERATES A GAS PLANT WHICH IS AUTHORIZED UNDER AN OIL AND GAS STANDARD PERMIT. THE MAXIMUM PRODUCTION IS CURRENTLY AUTHORIZED AT 0.3 LONG TONS PER DAY OF SULFUR. THEY ARE REQUESTING AUTHORIZATION TO MODIFY THE EXISTING FACILITY TO PROCESS SOUR GAS FROM NEW FIELD WELLS AND INCREASE MAXIMUM PRODUCTION TO 0.75 LONG TONS PER DAY OF SULFUR (4.0 MMSDFD OF GAS WITH AN H2S CONTENT OF 8.000 PPM). MODIFICATIONS INCLUDE THE INSTALLATION OF NEW COMPRESSORS, AUTHORIZING AN AMINE SWEETENING UNIT, A LARGER CAPACITY GLYCOL DEHYDRATOR, AND ALL ASSOCIATED PIPING. THE INCREASE IN SO2 REQUIRES PSD ANALYSIS. | 1.8 MMBTU AMINE REBOILER | 12.39 | SWEET NATURAL GAS | 1.8 | MMBTU |  |  | Carbon Monoxide | N |  | 0.02 | LB/H |  |  | 0.64 | T/YR
TX-0475 | FORMOSA POINT COMFORT PLANT | FORMOSA PLASTICS CORPORATION TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-09 | 2005 |  | PYROLYSIS FURNACE (1010B) | 12.39 | FUEL GAS | 250 | MMBtu/H |  |  | Carbon Monoxide | N |  | 8.75 | LB/H |  | N/A | 28.47 | T/YR
TX-0475 | FORMOSA POINT COMFORT PLANT | FORMOSA PLASTICS CORPORATION TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-09 | 2005 |  | REBOILER (1 AND 2) | 12.39 | FUEL GAS | 250 | MMBtu |  |  | Carbon Monoxide | N |  | 1.02 | LB/H |  | N/A | 4.47 | T/YR
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-07-27 | 2005 | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | BOILERS A & B (U-1 & U-2) | 12.39 |  | 250 | MMBTU/H |  |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES AND USE OF GASEOUS FUEL | 0.036 | LB/MMBTU |  | OPERATING PERMIT |  |  |  | 0.036 | LB/MMBTU | THREE ONE-HOUR TEST AVERAGE
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-07-27 | 2005 | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | BOILERS C & D (U-3 & U-4) | 12.39 |  | 250 | MMBTU/H |  |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES AND USE OF NATURAL GAS AS FUEL | 0.036 | LB/MMBTU |  | OPERATING PERMIT |  |  |  | 0.036 | LB/MMBTU | THREE ONE-HOUR TEST AVERAGE
NC-0101 | FORSYTH ENERGY PLANT | FORSYTH ENERGY PROJECTS, LLC | NC | FORSYTH COUNTY ENV AFFAIRS DEPT, NC | 2005-09-29 | 2005 | THREE COMBINED-CYCLE COMBUSTION TURBINE GENERATORS, EACH WITH A HEAT RECOVERY STEAM GENERATORS (HRSG) ALONG WITH NATURAL GAS-FIRED DUCT BURNERS TO MEET PEAK DEMAND. THE STEAM GENERATED THROUGH THE THREE HRSGS WILL DRIVE A STEAM TURBINE. THE ENTIRE PLANT WILL BE CAPABLE OF GENERATING A NOMINAL POWER OUTPUT OF 812 MEGAWATTS. | AUXILLIARY BOILER | 12.31 | NATURAL GAS | 110.2 | MMBTU/H |  |  | Carbon Monoxide | P | LOW-NOX BURNERS, GOOD COMBUSTION CONTROL AND CLEAN BURNING, LOW-SULFUR FUEL (NATURAL GAS). | 9.08 | LB/H | based on 3-hour average |  |  |  |  | 0.0824 | LB/MMBTU | calculated
MN-0062 | HEARTLAND CORN PRODUCTS |  | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2005-12-22 | 2005 |  | BOILER | 12.31 | NATURAL GAS | 198 | MMBTU/H | INCLUDES 2 BOILERS |  | Carbon Monoxide | N |  | 0.04 | LB/MMBTU
*TX-0499 | SANDY CREEK ENERGY STATION | SANDY CREEK ENERGY ASSOCIATES | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-07-24 | 2006 | THE PROPOSED SCES IS A GRASSROOTS NEW, 860 MW GROSS (800 MW NET) ELECTRIC OUTPUT, PC BOILER STEAM ELECTRIC GENERATING FACILITY. THE MAXIMUM HEAT INPUT IS 8,185 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTU/HR). ONLY PRELIMINARY ENGINEERING DESIGN HAS BEEN COMPLETED AT THIS TIME AND THE PERMIT APPLICATION NET PLANT EFFICIENCY OF 10,231 BTU/KWHR (HEAT ENERGY INPUT DIVIDED BY NET ELECTRIC ENERGY OUTPUT) WILL NOT BE FINALIZED UNTIL PROJECT FUNDING IS COMPLETE. THE BOILER MAY BE DESIGNED AS A SUBCRITICAL STEAM PRESSURE UNIT, OR A MORE EFFICIENT, HIGHER PRESSURE, SUPERCRITICAL STEAM UNIT. THE ELECTRIC GENERATING PROCESS IS THE STANDARD RANKINE CLOSED CYCLE: BOILER FEEDWATER IS PUMPED, CONVERTED TO STEAM IN THE BOILER, PASSED THROUGH STEAM TURBINES WHICH TURN ELECTRIC GENERATORS, AND CONDENSED IN WATER-COOLED CONDENSERS TO AGAIN BECOME BOILER FEEDWATER. HEAT IS REMOVED FROM THE TURBINE CONDENSERS VIA A WET COOLING TOWER WHICH EVAPORATES TO THE ATMOSPHERE WATER OBTAINED FROM WACO’S MUNICIPAL WASTE WATER TREATMENT FACILITY. | AUXILLARY BOILER | 12.31 | NATURAL GAS | 175 | MMBTU/H |  |  | Carbon Monoxide | N |  | 6.1 | LB/H
*TX-0496 | INEOS CHOCOLATE BAYOU FACILITY | INEOS USA LLC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-08-29 | 2006 | THE NO. 1 AND NO. 2 OLEFINS UNITS USE PYROLYSIS FURNACES TO CRACK FEEDSTOCKS INTO LOW MOLECULAR WEIGHT HYDROCARBONS THAT CONTAIN OLEFINS. PRODUCTS ARE ETHYLENE, PROPYLENE, PYROLYSIS GASOLINE, CRUDE C4, FUEL OIL, AND HYDROGEN. FEED FOR THE OLEFINS CRACKING FURNACES IS EITHER GAS FEED (ETHANE-RICH OR PROPANE-RICH FEED) OR LIQUID FEED (REFINERY RAFFINATE AND DEBUTANIZED NATURAL GASOLINE (DNG). THE LIQUID FEEDSTOCKS ARE STORED PRIOR TO PROCESSING IN LARGE FLOATING-ROOF TANKS EQUIPPED WITH SECONDARY SEALS. ETHYLENE PRODUCT IS TRANSFERRED OFF-SITE BY PIPELINE. PROPYLENE IS SHIPPED VIA RAILCAR, BARGE, OR SENT TO AN EXISTING POLYPROPYLENE UNIT AT THE CHOCOLATE BAYOU PLANT FOR FURTHER PROCESSING. CRUDE C4 STOCK IS SENT TO THE BUTADIENE EXTRACTION UNIT (BEU) TO PRODUCE HIGH PURITY BUTADIENE WHICH IS SOLD. BUTADIENE PRODUCT IS SHIPPED OFF-SITE VIA RAILCAR OR BARGE. THE RAW PYROLYSIS GASOLINE IS FURTHER HYDROTREATED TO PYROLYSIS GASOLINE PRODUCT FOR SHIPMENT OFF SITE | FURNACE EMISSION CAPS | 12.39 |  |  |  | EMISSION CAPS FOR FURNACES ARE NOT CHANGED IN THIS PERMIT ACTION. SPECIAL CONDITION NO. 13 IS CHANGED TO CLARIFY BACT SHALL BE DEMONSTRATED FOR EACH NEW FURNACE (EQUIPPED WITH SCR) AND ALLOW EXCEPTION WHEN THE UNIT IS IN DECOKING. SPECIAL CONDITION NO. 51 IS CHANGED TO ALLOW BACT FOR OLD FURNACES TO BE DEMONSTRATED AT THE LEVELS WHEN THE FLEXIBLE PERMIT WAS ISSUED. COMBUSTION STAFF WAS CONSULTED AND CONCURRED WITH THE CHANGE. |  | Carbon Monoxide | N |  | 200.78 | LB/H |  |  | 879.41 | T/YR
NV-0043 | LASCO BATHWARE | LASCO BATHWARE | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2006-10-25 | 2006 | A BATHWARE MANUFACTURING FACILITY | FUEL BURNING FOR THERMOSETTING | 12.31 | PROPANE | 6.3 | MMBTU/H | THERMOSETTING IS THE HEATING PROCESS TO HARDEN THE BATHROOM FIXTURES AFTER THEY ARE MOLDED INTO SHAPE. THERE ARE TWO HEATERS FOR EACH PRODUCTION LINE. ADDITIONALLY THERE ARE FIVE AIR HEATERS AT THE CURE TUNNEL. THE TOTAL HEAT INPUT CAPACITY FOR THE FUEL BURNING EQUIPMENT IS 27.56 MMBTU/HR. THE ANNUAL CONSUMPTION OF PROPANE FOR OPERATING THE FUEL BURNING EQUIPMENT IS LIMITED TO 662,645 GALLONS PER YEAR. MOST EMISSIONS COME FROM FUEL COMBUSTION, NOT FROM THE BATHROOM FIXTURES BEING HARDENED. THE EXHAUST OF THE HEATER DESIGNATED IN THE PERMIT AS A02 IS CHOSEN AS THE TYPICAL EMISSION UNIT FOR REPORTING THE PROCESS DATA. THIS HEATER IS SUBJECT TO THE LIMIT OF ANNUAL OPERATING TIME OF 2,200 HOURS PER YEAR. |  | Carbon Monoxide | N | N/A | 0.13 | LB/H |  | SIP | 0.14 | T/YR
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | A & B VACUUM TOWER HEATERS (3-08 & 4-08) | 12.39 | REFINERY FUEL GAS | 155.2 | MMBTU/H EA. |  |  | Carbon Monoxide | P | PROPER DESIGN, OPERATION, AND GOOD ENGINEERING PRACTICES |  |  |  | OPERATING PERMIT |  |  |  | 0.04 | LB/MM BTU | 30-DAY ROLLING AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | NAPHTHA HYDROTREATER STRIPPER REBOILER HEATER (6-08) & KHT STRIPPER REBOILER HEATER (10-08) | 12.39 | REFINERY FUEL GAS |  |  | 6-08: 138.4 MMBTU/H 10-08: 121.8 MMBTU/H |  | Carbon Monoxide | P | PROPER DESIGN, OPERATION, AND GOOD ENGINEERING PRACTICES |  |  |  | OPERATING PERMIT |  |  |  | 0.04 | LB/MMBTU | 30-DAY ROLLING AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | SATS GAS PLANT HOT OIL HEATER (14-08) | 12.39 | REFINERY FUEL GAS | 183.3 | MMBTU/H |  |  | Carbon Monoxide | P | PROPER DESIGN, OPERATION, AND GOOD ENGINEERING PRACTICES |  |  |  | OPERATING PERMIT |  |  |  | 0.04 | LB/MMBTU | 30-DAY ROLLING AVERAGE
*LA-0213 | ST. CHARLES REFINERY | VALERO REFINING - NEW ORLEANS, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2007-02-08 | 2007 | PETROLEUM REFINERY. PROJECT INVOLVES INCREASE IN CAPACITY FROM 220,000 TO 380,000 BARRELS PER DAY. | REBOILER 2005-18 & HEATERS F-15-02 (6-81), 2005-14, 2005-17, 2005-29, 2005-32, & 2005-37 | 12.39 | REFINERY FUEL GAS |  |  | 6-81: 135 MM BTU/HR 2005-14: 195 MM BTU/HR 2005-17: 159 MM BTU/HR 2005-18: 231 MM BTU/HR 2005-29: 195 MM BTU/HR 2005-32: 159 MM BTU/HR 2005-37: 173 MM BTU/HR SOURCES ALSO FIRE NATURAL GAS. |  | Carbon Monoxide | P | PROPER EQUIPMENT DESIGN AND OPERATION, GOOD COMBUSTION PRACTICES, AND USE OF GASEOUS FUELS | 0.08 | LB/MMBTU | HOURLY AVERAGE | OPERATING PERMIT
*MS-0086 | CHEVRON PRODUCTS COMPANY, PASCAGOULA REFINERY | CHEVRON PRODUCTS COMPANY | MS | MISSISSIPPI DEPT OF ENV QUALITY | 2007-05-08 | 2007 | PETROLEUM REFINERY AND PETROCHEMICALS | REFORMATE SPLITTER FURNACE | 12.39 | REFINERY FUEL GAS | 160 | MMBTU/H |  |  | Carbon Monoxide | N |  | 24.96 | LB/H | 3-HR ROLLING AVERAGE | MACT | 24.53 | T/YR | 12-MONTH ROLLING AVERAGE | 50 | PPMVD @ 3% O2 | 12-MONTH ROLLING AVERAGE
*IA-0089 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-08-08 | 2007 | 170 MILLION GALLON PER ROLLING 12-MONTH PERIOD DRY MILL ETHANOL PLANT. THE PROCESS WILL USE GASIFICATION TECHNOLOGY TO PRODUCE SYNGAS AS THE SOURCE FOR ENERGY. WILL USE 60,714,286 BUSHELS OF CORN PER ROLLING 12-MONTH PERIOD PRODUCING EITHER 1.411 MILLION TONS OF WDGS OR 552,500 TONS OF DDGS PER ROLLING 12-MONTH PERIOD. THE GASIFICATION PROCESS COULD USE UP TO 298, 213 TONS OF COAL PER ROLLING 12-MONTH PERIOD. PROJECT NUMBER (PN) 06-672, 28 PERMITS ISSUED | THERMAL OXIDIZER FOR HRSG FROM DRYERS AND GASIFICATION - TWO SYSTEMS, S10 AND S11 (07-A-955P AND 07-A-956P) | 12.3 | SYNGAS | 250 | MM BTU / hr | THE THERMAL OXIDIZER IS 150 MM BTU / HR AND EACH DRYER (TWO TOTAL FOR THIS EMISSION POINT) IS 50 MM BTU / HR. |  | Carbon Monoxide | N |  | 0.086 | LB/MMBTU
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Carbon Monoxide | N |  | 0.035 | LB/T |  |  | 14.37 | LB/H |  |  |  |  | THIS COVERS CO FOR THE NATURAL GAS-FIRED REHEAT FURNACE (LA 21).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Carbon Monoxide | N |  | 0.035 | LB/MMBTU |  |  | 0.21 | LB/H |  |  |  |  | THIS COVERS CO FOR THE 3 COIL DRUM FURNACES (LA24-LA26).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Carbon Monoxide | N |  | 0.09 | LB/MMBTU |  |  | 1.49 | LB/H |  |  |  |  | THIS COVERS CO FOR THE PLATE ANNEALING FURNACE (LA27).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS -FIRED ANNEALING FURNACE (LA43) (MULTIPLE EMISSION POINTS) | 12.31 | NATURAL GAS | 196.4 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X016: SULFURIC ACID PICKLING WITH CAUSTIC SCRUBBER (LA46) - RBLC PROCESS CODE - 81.290 PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Carbon Monoxide | N |  | 0.06 | LB/MMBTU |  |  | 11.75 | LB/H |  |  |  |  | THIS COVERS CO FOR THE NATURAL GAS-FIRED ANNEALING FURNACE (LA43).
*NM-0050 | ARTESIA REFINERY | NAVAJO REFINING COMPANY LLC | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2007-12-14 | 2007 | 115,000 - 125,000 BBL/DAY NOMINALLY RATED PETROLEUM REFINERY. | ROSE 2 HOT OIL HEATER | 12.3 | REFINERY FUEL GAS | 120 | mmbtu/hr |  |  | Carbon Monoxide | P | GASEOUS FUEL COMBUSTION ONLY | 0.06 | LB/MMBTU | 3-HOUR ROLLING AVERAGE @ 3% O2 |  | 7.2 | LBS | 3-HOUR ROLLING AVERAGE @ 3%O2
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | AUXILLIARY NAT. GAS FIRED BOILER (B25, S25) | 12.31 | NATURAL GAS | 229.8 | MMBTU/H | THE AUXILIARY BOILER WILL BE USED TO PREHEAT STEAM TURBINE, PROVIDE PLANT HEATING AND PROVIDE SUPPLEMENTAL STEAM TO AUXILIARY EQUIPMENT WHEN THE MAIN SCPC BOILER IS OFFLINE. THE AUXILIARY BOILER WILL BE PACKAGED BOILER THAT WILL COMBUST ONLY NATURAL GAS. THE HOURS OF THE OPERATION OF THE AUXILIARY BOILER WILL BE LIMITED TO 2,000 HOURS IN ANY 12 CONSECUTIVE MONTHS. |  | Fluorine | P | NATURAL GAS | 0.0003 | LB/MMBTU | 2000 H / 12 MO. ROLLING LIMIT
*IA-0089 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-08-08 | 2007 | 170 MILLION GALLON PER ROLLING 12-MONTH PERIOD DRY MILL ETHANOL PLANT. THE PROCESS WILL USE GASIFICATION TECHNOLOGY TO PRODUCE SYNGAS AS THE SOURCE FOR ENERGY. WILL USE 60,714,286 BUSHELS OF CORN PER ROLLING 12-MONTH PERIOD PRODUCING EITHER 1.411 MILLION TONS OF WDGS OR 552,500 TONS OF DDGS PER ROLLING 12-MONTH PERIOD. THE GASIFICATION PROCESS COULD USE UP TO 298, 213 TONS OF COAL PER ROLLING 12-MONTH PERIOD. PROJECT NUMBER (PN) 06-672, 28 PERMITS ISSUED | THERMAL OXIDIZER FOR HRSG FROM DRYERS AND GASIFICATION - TWO SYSTEMS, S10 AND S11 (07-A-955P AND 07-A-956P) | 12.3 | SYNGAS | 250 | MM BTU / hr | THE THERMAL OXIDIZER IS 150 MM BTU / HR AND EACH DRYER (TWO TOTAL FOR THIS EMISSION POINT) IS 50 MM BTU / HR. |  | Formaldehyde | N |  | 0.074 | LB/H |  | MACT | [6 empty] | LIMITING THE POTENTIAL TO EMIT OF THE POLLUTANT SO THE FACILTIY CAN REMAIN A SYNTHETIC MINOR FOR NESHAP / MACT CATEGORY.
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | AUXILLIARY NAT. GAS FIRED BOILER (B25, S25) | 12.31 | NATURAL GAS | 229.8 | MMBTU/H | THE AUXILIARY BOILER WILL BE USED TO PREHEAT STEAM TURBINE, PROVIDE PLANT HEATING AND PROVIDE SUPPLEMENTAL STEAM TO AUXILIARY EQUIPMENT WHEN THE MAIN SCPC BOILER IS OFFLINE. THE AUXILIARY BOILER WILL BE PACKAGED BOILER THAT WILL COMBUST ONLY NATURAL GAS. THE HOURS OF THE OPERATION OF THE AUXILIARY BOILER WILL BE LIMITED TO 2,000 HOURS IN ANY 12 CONSECUTIVE MONTHS. |  | Hazardous Air Pollutants (HAP) | P | GOOD COMBUSTION PRACTICES | 400 | PPM CO @ 3% O2 | [8 empty] | CASE BY CASE MACT
*IA-0089 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-08-08 | 2007 | 170 MILLION GALLON PER ROLLING 12-MONTH PERIOD DRY MILL ETHANOL PLANT. THE PROCESS WILL USE GASIFICATION TECHNOLOGY TO PRODUCE SYNGAS AS THE SOURCE FOR ENERGY. WILL USE 60,714,286 BUSHELS OF CORN PER ROLLING 12-MONTH PERIOD PRODUCING EITHER 1.411 MILLION TONS OF WDGS OR 552,500 TONS OF DDGS PER ROLLING 12-MONTH PERIOD. THE GASIFICATION PROCESS COULD USE UP TO 298, 213 TONS OF COAL PER ROLLING 12-MONTH PERIOD. PROJECT NUMBER (PN) 06-672, 28 PERMITS ISSUED | THERMAL OXIDIZER FOR HRSG FROM DRYERS AND GASIFICATION - TWO SYSTEMS, S10 AND S11 (07-A-955P AND 07-A-956P) | 12.3 | SYNGAS | 250 | MM BTU / hr | THE THERMAL OXIDIZER IS 150 MM BTU / HR AND EACH DRYER (TWO TOTAL FOR THIS EMISSION POINT) IS 50 MM BTU / HR. |  | Hazardous Air Pollutants (HAP) | N |  | 0.185 | LB/H | ACETALDEHYDE | [7 empty] | LIMIT ESTABLISHED FOR FACILITY TO STAY SYNTHETIC MINOR FOR NESHAP / MACT APPLICABLILITY
*IA-0089 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-08-08 | 2007 | 170 MILLION GALLON PER ROLLING 12-MONTH PERIOD DRY MILL ETHANOL PLANT. THE PROCESS WILL USE GASIFICATION TECHNOLOGY TO PRODUCE SYNGAS AS THE SOURCE FOR ENERGY. WILL USE 60,714,286 BUSHELS OF CORN PER ROLLING 12-MONTH PERIOD PRODUCING EITHER 1.411 MILLION TONS OF WDGS OR 552,500 TONS OF DDGS PER ROLLING 12-MONTH PERIOD. THE GASIFICATION PROCESS COULD USE UP TO 298, 213 TONS OF COAL PER ROLLING 12-MONTH PERIOD. PROJECT NUMBER (PN) 06-672, 28 PERMITS ISSUED | THERMAL OXIDIZER FOR HRSG FROM DRYERS AND GASIFICATION - TWO SYSTEMS, S10 AND S11 (07-A-955P AND 07-A-956P) | 12.3 | SYNGAS | 250 | MM BTU / hr | THE THERMAL OXIDIZER IS 150 MM BTU / HR AND EACH DRYER (TWO TOTAL FOR THIS EMISSION POINT) IS 50 MM BTU / HR. |  | Hazardous Air Pollutants (HAP) | N |  | 0.25 | LB/H | ACROLEIN | [7 empty] | LIMIT ESTABLISHED FOR FACILITY TO STAY SYNTHETIC MINOR FOR NESHAP / MACT APPLICABLILITY
*IA-0089 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-08-08 | 2007 | 170 MILLION GALLON PER ROLLING 12-MONTH PERIOD DRY MILL ETHANOL PLANT. THE PROCESS WILL USE GASIFICATION TECHNOLOGY TO PRODUCE SYNGAS AS THE SOURCE FOR ENERGY. WILL USE 60,714,286 BUSHELS OF CORN PER ROLLING 12-MONTH PERIOD PRODUCING EITHER 1.411 MILLION TONS OF WDGS OR 552,500 TONS OF DDGS PER ROLLING 12-MONTH PERIOD. THE GASIFICATION PROCESS COULD USE UP TO 298, 213 TONS OF COAL PER ROLLING 12-MONTH PERIOD. PROJECT NUMBER (PN) 06-672, 28 PERMITS ISSUED | THERMAL OXIDIZER FOR HRSG FROM DRYERS AND GASIFICATION - TWO SYSTEMS, S10 AND S11 (07-A-955P AND 07-A-956P) | 12.3 | SYNGAS | 250 | MM BTU / hr | THE THERMAL OXIDIZER IS 150 MM BTU / HR AND EACH DRYER (TWO TOTAL FOR THIS EMISSION POINT) IS 50 MM BTU / HR. |  | Hazardous Air Pollutants (HAP) | N |  | 1.66 | LB/H | TOTAL HAP | [7 empty] | LIMIT ESTABLISHED FOR FACILITY TO STAY SYNTHETIC MINOR FOR NESHAP / MACT APPLICABLILITY
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | AUXILLIARY NAT. GAS FIRED BOILER (B25, S25) | 12.31 | NATURAL GAS | 229.8 | MMBTU/H | THE AUXILIARY BOILER WILL BE USED TO PREHEAT STEAM TURBINE, PROVIDE PLANT HEATING AND PROVIDE SUPPLEMENTAL STEAM TO AUXILIARY EQUIPMENT WHEN THE MAIN SCPC BOILER IS OFFLINE. THE AUXILIARY BOILER WILL BE PACKAGED BOILER THAT WILL COMBUST ONLY NATURAL GAS. THE HOURS OF THE OPERATION OF THE AUXILIARY BOILER WILL BE LIMITED TO 2,000 HOURS IN ANY 12 CONSECUTIVE MONTHS. |  | Lead (Pb) / Lead Compounds | P | NATURAL GAS FUEL, GOOD COMBUSTION PRACTICES | 0 | LB/MMBTU | 2000 H / 12 MO. ROLLING | [7 empty] | 8.84 E-8 LBS/MMBTU
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | AUXILLIARY NAT. GAS FIRED BOILER (B25, S25) | 12.31 | NATURAL GAS | 229.8 | MMBTU/H | THE AUXILIARY BOILER WILL BE USED TO PREHEAT STEAM TURBINE, PROVIDE PLANT HEATING AND PROVIDE SUPPLEMENTAL STEAM TO AUXILIARY EQUIPMENT WHEN THE MAIN SCPC BOILER IS OFFLINE. THE AUXILIARY BOILER WILL BE PACKAGED BOILER THAT WILL COMBUST ONLY NATURAL GAS. THE HOURS OF THE OPERATION OF THE AUXILIARY BOILER WILL BE LIMITED TO 2,000 HOURS IN ANY 12 CONSECUTIVE MONTHS. |  | Mercury | P | NATURAL GAS | 0.0001 | LB/H | 2000 H / 12 MO. ROLLING
*IA-0089 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-08-08 | 2007 | 170 MILLION GALLON PER ROLLING 12-MONTH PERIOD DRY MILL ETHANOL PLANT. THE PROCESS WILL USE GASIFICATION TECHNOLOGY TO PRODUCE SYNGAS AS THE SOURCE FOR ENERGY. WILL USE 60,714,286 BUSHELS OF CORN PER ROLLING 12-MONTH PERIOD PRODUCING EITHER 1.411 MILLION TONS OF WDGS OR 552,500 TONS OF DDGS PER ROLLING 12-MONTH PERIOD. THE GASIFICATION PROCESS COULD USE UP TO 298, 213 TONS OF COAL PER ROLLING 12-MONTH PERIOD. PROJECT NUMBER (PN) 06-672, 28 PERMITS ISSUED | THERMAL OXIDIZER FOR HRSG FROM DRYERS AND GASIFICATION - TWO SYSTEMS, S10 AND S11 (07-A-955P AND 07-A-956P) | 12.3 | SYNGAS | 250 | MM BTU / hr | THE THERMAL OXIDIZER IS 150 MM BTU / HR AND EACH DRYER (TWO TOTAL FOR THIS EMISSION POINT) IS 50 MM BTU / HR. |  | Mercury | N |  | 0.0094 | LB/H | [8 empty] | LIMIT ESTABLISHED FOR FACILITY TO STAY SYNTHETIC MINOR FOR NESHAP / MACT APPLICABLILITY
*IA-0089 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-08-08 | 2007 | 170 MILLION GALLON PER ROLLING 12-MONTH PERIOD DRY MILL ETHANOL PLANT. THE PROCESS WILL USE GASIFICATION TECHNOLOGY TO PRODUCE SYNGAS AS THE SOURCE FOR ENERGY. WILL USE 60,714,286 BUSHELS OF CORN PER ROLLING 12-MONTH PERIOD PRODUCING EITHER 1.411 MILLION TONS OF WDGS OR 552,500 TONS OF DDGS PER ROLLING 12-MONTH PERIOD. THE GASIFICATION PROCESS COULD USE UP TO 298, 213 TONS OF COAL PER ROLLING 12-MONTH PERIOD. PROJECT NUMBER (PN) 06-672, 28 PERMITS ISSUED | THERMAL OXIDIZER FOR HRSG FROM DRYERS AND GASIFICATION - TWO SYSTEMS, S10 AND S11 (07-A-955P AND 07-A-956P) | 12.3 | SYNGAS | 250 | MM BTU / hr | THE THERMAL OXIDIZER IS 150 MM BTU / HR AND EACH DRYER (TWO TOTAL FOR THIS EMISSION POINT) IS 50 MM BTU / HR. |  | Methanol | N |  | 0.248 | LB/H | [8 empty] | LIMIT ESTABLISHED FOR FACILITY TO STAY SYNTHETIC MINOR FOR NESHAP / MACT APPLICABLILITY
AL-0128 | ALABAMA POWER COMPANY - THEODORE COGENERATION | ALABAMA POWER COMPANY - THEODORE COGENERATION | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1999-03-16 | 1999 |  | BOILER | 12.31 | NATURAL GAS | 220 | MMBTU/H |  |  | Nitrogen Dioxide (NO2) | P | LNB AND FLUE GAS RECIRCULATION | 0.053 | LB/MMBTU |  |  | 11.7 | LB/H |  | 0.053 | LB/MMBTU
*PA-0170 | SUNOCO INC. (R&M) | SUNOCO INC. (R&M) | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2001-08-02 | 2001 |  | BOILER #7 | 12.31 | NATURAL GAS | 245 | MMBTU/H | limit for nox only |  | Nitrogen Dioxide (NO2) | P | FOUR SPUD BURNERS. SINCE THE BOILER IS COVERED UNDER RACT ONLY NOX LIMIT IS LISTED | 0.25 | LB/MMBTU | [5 empty] | 0.25 | LB/MMBTU
*PA-0170 | SUNOCO INC. (R&M) | SUNOCO INC. (R&M) | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2001-08-02 | 2001 |  | BOILER #6 | 12.31 | NATURAL GAS | 245 | MMBTU/H | limit for nox only |  | Nitrogen Dioxide (NO2) | P | FOUR SPUD BURNERS. THE BOILER IS COVERED UNDER RACT SO ONLY NOX LIMIT IS LISTED | 0.25 | LB/MMBTU | [5 empty] | 0.25 | LB/MMBTU
OR-0040 | KLAMATH GENERATION, LLC | KLAMATH GENERATION, LLC | OR | OREGON DEPT OF ENVIRONMENTAL QUALITY | 2003-03-12 | 2003 | POWER GENERATION FACILITY | DUCT BURNERS | 12.31 | NATURAL GAS | 250 | MMBTU/H | Throughput for each. Used to boost steam during peak generating periods. |  | Nitrogen Dioxide (NO2) | B | DLN COMBUSTION AND SCR | 0.2 | LB/MMBTU | [5 empty] | 0.2 | LB/MMBTU |  | Limit applies at all times, including startup and shut down.
VA-0270 | VCU EAST PLANT | VIRGINIA COMMONWEALTH UNIVERSITY | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-31 | 2003 |  | BOILER NATUAL GAS | 12.31 | NATURAL GAS | 150 | MMBTU/H | This is one of 3 boilers |  | Nitrogen Dioxide (NO2) | B | GOOD COMBUSTION PRACTICES. LOW NOX COMBUSTION AND FGR. CEM SYSTEM. | 0.1 | LB/MMBTU | each unit |  | 15.6 | LB/H | each unit | 0.1 | LB/MMBTU
IN-0100 | ROCKPORT WORKS | AK STEEL CORPORATION | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1997-02-13 | 1997 | STEEL COIL FINISHING PLANT; ALL POLLUTANTS IN PERMIT ARE LISTED | FURNACE, INDUCTION AND HEATING GALVANNEALING | 12.31 | NATURAL GAS | 205.7 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | A | SELECTIVE CATALYTIC REDUCTION (SCR) | 12.3 | LB/H | [5 empty] | 0.06 | LB/MMBTU
IA-0057 | CARGILL, INC | CARGILL, INC | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-02-24 | 1997 | CORN PROCESSING PLANT | BOILER #4 | 12.31 | NATURAL GAS | 230 | MMBTU/H | PERMIT NUMBER: 89-A-210-S2. NO LIMITS FOR CO, SO2, OR VOC IN PERMIT. |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNER. STANDARD EMISSION LIMIT ESTIMATED FROM PERMIT PROCESS DATA. | 46 | LB/H | [5 empty] | 0.2 | LB/MMBTU
IA-0057 | CARGILL, INC | CARGILL, INC | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-02-24 | 1997 | CORN PROCESSING PLANT | BOILER #5 | 12.31 | NATURAL GAS | 182 | MMBTU/H | PERMIT NUMBER: 92-A-227-S3. NO LIMITS FOR CO, SO2, OR VOC IN PERMIT. |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNER. STANDARD EMISSION LIMIT ESTIMATED FROM PERMIT PROCESS DATA. | 18.2 | LB/H |  | NSPS |  |  |  | 0.1 | LB/MMBTU
IA-0057 | CARGILL, INC | CARGILL, INC | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-02-24 | 1997 | CORN PROCESSING PLANT | BOILER #6 | 12.31 | NATURAL GAS | 182 | MMBTU/H | PERMIT NUMBER: 92-A-228-S3. LIMITS FOR CO, SO2, OR VOC ARE NOT INCLUDED IN THE PERMIT. |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNER. BASIS OF LIMIT IS NSPS SUBPART DB, SYNTHETIC MINOR. | 18.2 | LB/H |  | NSPS |  |  |  | 0.1 | LB/MMBTU
AR-0019 | QUINCY SOYBEAN COMPANY OF ARKANSAS | QUINCY SOYBEAN COMPANY OF ARKANSAS | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-03-04 | 1997 |  | BOILER, #3 | 12.31 | NATURAL GAS | 123 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | P | LOW NOX COMBUSTORS | 0.05 | LB/MMBTU |  |  | 0 |  |  | 0.05 | LB/MMBTU
AL-0096 | MEAD COATED BOARD, INC. | MEAD COATED BOARD, INC. | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-03-12 | 1997 |  | DUCT BURNER, NAT GAS | 12.31 | NATURAL GAS | 170 | MMBTU/H | A SEPARATELY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING FUEL OIL. |  | Nitrogen Oxides (NOx) | P | DRY LOW NOX COMBUSTOR. | 0.1 | LB/MMBTU |  |  | 20 | LB/H |  | 0.1 | LB/MMBTU
IN-0075 | GRAIN PROCESSING CORP. | GRAIN PROCESSING CORP. | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1997-06-10 | 1997 |  | BOILERS NO. 1 & 2 | 12.39 | NATURAL GAS/ALCOHOL | 244 | MMBTU/H (EACH) | STACK TEST REQUIRED BY PERMIT, NOT YET CONSTRUCTED. BOILER NO.1 (UP51A), BOILER NO.2 (UP51B). |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION (FGR) | 0.05 | LB/MMBTU |  |  | 0 |  |  | 0.05 | LB/MMBTU
NJ-0031 | UNIVERSITY OF MEDICINE & DENTISTRY OF NEW JERSEY | UNIVERSITY OF MEDICINE & DENTISTRY OF NEW JERSEY | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-06-26 | 1997 |  | BOILER, NATURAL GAS FIRED, 3 | 12.31 | NATURAL GAS | 112 | MMBTU/H | SEPARATELY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING NO.6 FUEL OIL (SECONDARY FUEL). |  | Nitrogen Oxides (NOx) | N |  | 0.55 | LB/MMBTU | [5 empty] | 0.55 | LB/MMBTU
NJ-0041 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-10-08 | 1997 |  | DUCT BURNER ONLY | 12.31 | NATURAL GAS | 234 | MMBTU/H | TOTAL NATURAL GAS BURNED IN THE HEAT RECOVERY BOILER SHALL NOT EXCEED 1153.2 MILLION CUBIC FEET PER CALENDAR YEAR |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNER | 35.1 | LB/H |  |  | 39 | PPMVD @ 15% O2 |  | 0.15 | LB/MMBTU
LA-0114 | ST. JAMES STYRENE PLANT | CHEVRON CHEMICAL COMPANY | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1997-12-10 | 1997 | MODIFICATION TO THE EXISTING STYRENE PRODUCTION FACILITY | SUPERHEATER | 12.31 | NATURAL GAS | 165 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 0.07 | LB/MMBTU | [5 empty] | 0.07 | LB/MMBTU
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, NAT GAS | 12.31 | NATURAL GAS | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Nitrogen Oxides (NOx) | A | LOW NOX BURNER | 0.05 | LB/MMBTU |  |  | 9.5 | LB/H |  | 0.05 | LB/MMBTU
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, HYDROGEN | 12.39 | HYDROGEN | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Nitrogen Oxides (NOx) | A |  | 0.07 | LB/MMBTU |  |  | 13.3 | LB/H |  | 0.07 | LB/MMBTU
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, COMBINED FUEL (NAT GAS/HYDROGEN) | 12.39 | NAT GAS/HYDRO COMBO | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Nitrogen Oxides (NOx) | A |  | 0.07 | LB/MMBTU |  |  | 13.3 | LB/H |  | 0.07 | LB/MMBTU
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | DUCT BURNER | 12.39 | NAT GAS/HYDROGEN | 260 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | P |  | 0.2 | LB/MMBTU |  |  | 34 | LB/H |  |  |  | NOT AVAILABLE
MO-0051 | PROCTOR & GAMBLE PAPER PRODUCTS | Proctor & Gamble Paper Products | MO | MISSOURI DNR, AIR POLL CONTROL PROGRAM | 1998-01-01 | 1998 | SANITARY TISSUE & TOWEL BUSINESS, EXPANSION TO EXISTING DIAPER MANUFACTURING PLANT | BOILERS, NATURAL GAS, (3) | 12.31 | NATURAL GAS | 1095 | MMCF/YR | ADDITIONAL THROUGHPUT INFORMATION: 125 MMBTU/H, EACH. |  | Nitrogen Oxides (NOx) | P | LOW NOX FUEL, W/O FLUE GAS RECIRCULATION, GOOD COMBUSTION. LIMIT IS 1 HR AVG. | 0.08 | LB/MMBTU | [5 empty] | 0.08 | LB/MMBTU
SC-0075 | NUCOR STEEL- DARLINGTON COUNTY | NUCOR STEEL CORPORATION | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 1998-01-08 | 1998 | STEEL MILL | REHEAT FURNACE #1 | 12.31 | NATURAL GAS | 140 | MMBTU/H | MAIN FUEL IS NATURAL GAS, PROPANE AS A BACK-UP. UTILIZES LOW NOX BURNERS. NATURAL GAS AND PROPANE USAGE IS RESTRICTED TO AN EQUIVALENT OF 1150 X MMSCF PER YEAR AT ESTABLISHED BTU CONTENTS OF 1000 BTU/CF AND 90500 BTU/GALLON RESPECTIVELY. SUBJECT TO PSD. |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND RECUPERATORS, FUEL RESTRICTIONS. | 13.7 | LB/H |  |  | 60 | T/YR |  | 0.098 | LB/MMBTU
SC-0075 | NUCOR STEEL- DARLINGTON COUNTY | NUCOR STEEL CORPORATION | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 1998-01-08 | 1998 | STEEL MILL | REHEAT FURNACE #2 | 12.31 | NATURAL GAS | 125 | MMBTU/H | NATURAL GAS IS MAIN FUEL, PROPANE AS BACK UP. UTILIZES LOW NOX BURNERS AND EXTERNAL FLUE GAS RECIRCULATION. NATURAL GAS AND PROPANE USAGE IS RESTRICTED TO AN EQUIVALENT OF 1095 MMSCF PER YEAR AS ESTABLISHED BTU CONTENTS OF 1000 BTU/CF AND 90500 BTU/GAL RESPECTIVELY. SUBJECT TO PSD. |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND EXTERNAL FLUE GAS RECIRCULATION, FUEL RESTRICTIONS. | 17.5 | LB/H |  |  | 76.6 | T/YR |  | 0.125 | LB/MMBTU
PA-0150 | NATIONAL GYPSUM COMPANY | NATIONAL GYPSUM COMPANY | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 1998-02-24 | 1998 | WALLBOARD MANUFACTURING FACILITY | BOARD DRYER | 12.31 | NATURAL GAS | 150 | MMBTU/H | ANY FUEL OIL USE LIMITED TO 3.8 MILLION GALLONS PER YEAR TO AVOID NSR REQUIREMENTS |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS (ULNB) | 9.9 | PPM |  |  | 1.9 | LB/H |  | 0.013 | LB/MMBTU
PA-0152 | PEI POWER | PEI POWER | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 1998-05-22 | 1998 |  | BOILER, CFB, MODIFIED | 12.39 | LANDFILL GAS | 249 | MMBTU/H | MFG. BY DB RILEY AND FOSTER WHEELER |  | Nitrogen Oxides (NOx) | P | LNB WITH FGR | 0.06 | LB/MMBTU |  |  | 15 | LB/H |  | 0.06 | LB/MMBTU
TX-0259 | FREEPORT COGENERATION FACILITY | BASF CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-06-26 | 1998 | CONSTRUCTION OF A COGENERATION UNIT | BOILER, B-20A | 12.39 | H2 WASTE & NAT GAS | 213 | MMBTU/H | HYDROGEN WASTE GAS AND PIPELINE QUALITY, SWEET NAT GAS CONTAINING NO >0.25 GR H2S AND 5 GR TOTAL S/100 DSCF. SCC CODE FOR NATURAL GAS CHOSEN FOR THE PURPOSE OF THIS DATABASE. |  | Nitrogen Oxides (NOx) | N | NONE INDICATED. | 122.1 | LB/H |  | NSPS | 535 | T/YR |  | 0.57 | LB/MMBTU | CALCULATED | EMISSION LIMIT IN STANDARDIZED UNITS CALCULATED FROM THE HOURLY EMISSION LIMIT AND THE THROUGHPUT.
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | 1998 | VEGETABLE OIL PLANT | BOILER, TRANE MURRAY, NAT GAS | 12.31 | NATURAL GAS | 189 | MMBTU/H | No add-on controls. See separate process for backup fuel (No. 2 oil) requirements. |  | Nitrogen Oxides (NOx) | N |  | 0.053 | LB/MMBTU | [5 empty] | 0.053 | LB/MMBTU
IN-0104 | CON AGRA SOYBEAN PROCESSING CO. | CON AGRA SOYBEAN PROCESSING CO. | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1998-08-14 | 1998 | SOYBEAN PROCESSING | BOILER, (2) | 12.31 | NATURAL GAS | 200 | MMBTU/H | 2 main boilers, throughput for each, low sulfur fuel oil is auxilary fuel. |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 0.035 | LB/MMBTU | gas |  | 0.087 | LB/MMBTU | distillate fuel oil | 0.035 | LB/MMBTU
TX-0237 | PORT ARTHUR REFINERY | FINA OIL AND CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-09-08 | 1998 | CHEMICAL AND OIL COMPANY, 2.2 BILLION LB/YR ETHYLENE CRACKING UNIT & ASSOCIATED FACILITIES. LOCATED AT INTERSECTION OF HWY 366 & 32ND ST. | DUCT BURNERS (2) | 12.31 | NATURAL GAS | 310.4 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.09 | LB/MMBTU | [5 empty] | 0.09 | LB/MMBTU
TX-0237 | PORT ARTHUR REFINERY | FINA OIL AND CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-09-08 | 1998 | CHEMICAL AND OIL COMPANY, 2.2 BILLION LB/YR ETHYLENE CRACKING UNIT & ASSOCIATED FACILITIES. LOCATED AT INTERSECTION OF HWY 366 & 32ND ST. | BOILER, SUPPLEMENTAL, STEAM | 12.31 | NATURAL GAS | 227 | mmbtu/h | THIS SUPPLEMENTAL STEAM BOILER IS PART OF THE COGENERATION PACKAGE INCLUDING 2 COMBINED CYCLE TURBINES AND 2 DUCT BURNERS. |  | Nitrogen Oxides (NOx) | P | FLUE GAS RECIRCULATION, LOW NOX BURNERS | 0.06 | LB/MMBTU | [5 empty] | 0.06 | LB/MMBTU
AL-0123 | U S ALLIANCE | U S ALLIANCE | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1998-09-25 | 1998 |  | BOILER, AUX. POWER, NO.1 | 12.31 | NATURAL GAS | 0 |  |  |  | Nitrogen Oxides (NOx) | N |  | 0.2 | LB/MBTU |  |  | 91.4 | LB/H
TX-0305 | PARIS GENERATING STATION | PANDA PARIS LLC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-10-28 | 1998 | PANDA PARIS, LLC, PROPOSES TO CONSTRUCT A NATURAL GAS-FIRED COMBINED- CYCLE POWER GENERATION FACILITY TO BE KNOWN AS THE PARIS GENERATING STATION, LOCATED IN LAMAR COUNTY. THE PROPOSED FACILITY WILL CONSIST OF FOUR 170 MW GENERAL ELECTRIC 7241FA COMBUSTION TURBINES AND ASSOCIATED HEAT RECOVERY STEAM GENERATORS WITH 200 MMBTU/H DUCT BURNERS EACH. THE TURBINES AND DUCT BURNERS WILL BE FIRED WITH PIPELINE NAT GAS. PROCESS STEAM FROM THE HRSGS WILL BE USED TO GENERATE ADDITIONAL ELECTRICITY FROM TWO 160 MW STEAM TURBINES. THE COMBINED UNITS WILL HAVE A NOMINAL CAPACITY OF 1000 MW. THERE WILL BE TWO 2000 DIESEL FUEL- FIRED BLACK START EMERGENCY GENERATORS, ONE 400 KW DIESEL FUEL- FIRED EMERGENCY ELECTRICAL GENERATOR TO PROVIDE GENERAL SITE POWER, ONE 260- HP DIESEL FUEL-FIRED EMERGENCY FIRE WATER PUMP AND ANCILLARY EQUIPMENT INCLUDING RAW AND DEMINERALIZED WATER STORAGE TANKS. A LETTER DATED AUGUST 20, 1998 FROM THE COMPANY'S CONSULTANT (ECT) ALSO REQUESTED THESE DIESEL- FIRED ENGINES BE EXEMPT UNDER 30 TAC SECTION 106.511 AND 106.512 AND NOT HAVE THEM INCLUDED IN THIS PERMIT. | (4) DUCT BURNERS | 12.31 | NAT GAS | 200 | MMBTU/H, EA | THE TOTAL ANNUAL HEAT INPUT TO ALL DUCT BURNERS SHALL NOT EXCEED 3,200,000 MMBTU FOR THE FACILITY SITE. |  | Nitrogen Oxides (NOx) | P | DRY LOW-NOX COMBUSTORS | 0.08 | LB/MMBTU | EACH UNIT |  |  |  |  | 0.08 | LB/MMBTU | EACH UNIT
MN-0035 | LSP - COTTAGE GROVE, L.P. | LSP - COTTAGE GROVE, L.P. | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 1998-11-10 | 1998 |  | BOILERS, AUXILIARY, 2, NAT GAS | 12.31 | NATURAL GAS | 114 | MMBTU/H (NAT GAS) | A SEPARETLY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING FUEL OIL. |  | Nitrogen Oxides (NOx) | P | NATURAL GAS LIMIT. BOILERS HAVE A NOX PEMS TO DETERMINE NOX EMISSIONS. DISTILLATE FUEL OIL BURN WITH A LIMIT OF 1700 H/YR. | 0.06 | LB/MMBTU | [5 empty] | 0.06 | LB/MMBTU
CA-0861 | SAN BENITO FOODS TOMATO PROCESSING | SAN BENITO FOODS TOMATO PROCESSING | CA | MONTEREY BAY UNIFIED APCD, CA | 1998-12-14 | 1998 |  | BOILER, CLEAVER BROOKS W/ TODD COMBUSTION VARIFLAM | 12.31 | NATURAL GAS | 210 | MMBTU/H | ARB RECORD #: A370-872-99 CONTINUE PROCESS: LOW NOX BURNER |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNER ADN FLUE GAS RECIRCULATION | 30 | PPMVD @ 3% O2 |  |  | 0 |  |  | 0
OH-0245 | REPUBLIC TECHNOLOGIES INTERNATIONAL | REPUBLIC TECHNOLOGIES INTERNATIONAL/CANTON | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 1999-01-27 | 1999 | STEEL MILL. THIS PLANT IS PSD FOR PM, SO2, NOX, CO, AND VOC. THIS MODIFICATION IS A SIGNIFICANT INCREASE FOR NOX. | BLOOM REHEAT FURNACE | 12.31 | NATURAL GAS | 196.2 | MMBTU/H | STACK TEST 0.0489 LB NOX/HR |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS, LOOKED AT SCR AND SNCR, NOT FEASIBLE. | 22 | LB/H |  |  | 96.2 | T/YR |  | 0.112 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 4 (NAT GAS) | 12.31 | NATURAL GAS | 118 | MMBTU/H | MFR. IS BABCOCK & WILCOX. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Nitrogen Oxides (NOx) | N | NONE LISTED | 33 | LB/H |  |  | 0.28 | LB/MMBTU |  | 0.28 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 2 (NAT GAS) | 12.31 | NATURAL GAS | 134 | MMBTU/H | MFR. IS COMBUSTION ENGINEERING. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Nitrogen Oxides (NOx) | N | NONE LISTED | 37.6 | LB/H |  |  | 0.28 | LB/MMBTU |  | 0.28 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 3 (NAT GAS) | 12.31 | NATURAL GAS | 152 | MMBTU/H | MFR. IS BABCOCK & WILCOX. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Nitrogen Oxides (NOx) | N | NONE LISTED | 42.6 | LB/H |  |  | 0.28 | LB/MMBTU |  | 0.28 | LB/MMBTU
IA-0050 | CARGILL-EDDYVILLE | CARGILL-EDDYVILLE | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1999-04-22 | 1999 |  | BOILER 7 | 12.31 | NATURAL GAS | 182.1 | MMBTU/H | NATURAL GAS ONLY |  | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS WITH FGR | 0.05 | LB/MMBTU |  |  | 9.11 | LB/H |  | 0.05 | LB/MMBTU
TX-0414 | ATOFINA PETROCHEMICALS PORT ARTHUR COMPLEX | FINA OIL & CHEMICAL COPMANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1999-04-22 | 1999 | FACILITY WANTS TO INSTALL A COGENERATION FACILITY CONSISTING OF 2 TURBINES AND SUPPLEMENTAL BOILER TO SUBSTITUTE FOR 2 AUXILIARY STEAM BOILERS | SUPPLEMENTAL BOILER | 12.31 | NATURAL GAS | 227 | MMBTU/H | BOILER PRODUCES AS MUCH AS 150,000 LB/H OF STEAM. |  | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICE | 13.65 | LB/H |  |  | 16.2 | T/YR |  | 0.06 | LB/MMBTU
AR-0026 | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1999-05-05 | 1999 | COMBUSTION TURBINE COMBINED CYCLE COGENERATION FACILITY | DUCT BURNER | 12.31 | NATURAL GAS | 315 | MMBTU/H | TURBINE AND DUCT BURNER EMISSIONS COMBINED IN ONE STACK. DUCT BURNER ALWAYS FIRES NATURAL GAS. |  | Nitrogen Oxides (NOx) | P | DLN COMBUSTORS | 0.08 | LB/MMBTU | [5 empty] | 0.08 | LB/MMBTU
AR-0026 | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1999-05-05 | 1999 | COMBUSTION TURBINE COMBINED CYCLE COGENERATION FACILITY | BOILER, NATURAL GAS | 12.31 | NATURAL GAS | 362 | MMBTU/H | BOILER FIRES NATURAL GAS AND FUEL OIL. BOILER WILL PROVIDE STEAM FOR STEAM TURBINE AND INTERNATIONAL PAPER MILL. |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS, FLUE GAS RECIRCULATION, AND GOOD COMBUSTION PRACTICES. | 0.037 | LB/MMBTU | [5 empty] | 0.037 | LB/MMBTU
LA-0119 | LAKE CHARLES REFINERY | CONOCO INC. | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1999-08-12 | 1999 | PERMIT TO IMPLEMENT THE PETROZUATA SYNCRUDE PROJECT, ALLOWING REFINERY TO PROCESS A MIXTURE OF VIRGIN CRUDE AND CUTTER STOCK. SECURES A GUARANTEED CRUDE SUPPLY AND INCREASE PRODUCTION OF HEAVY PRODUCTS. MODIFICATION TO VARIOUS PROCESS UNITS WILL BE REQUIRED TO ENABLE THE FACILITY TO PROCESS THE INCREASED SULFUR LOAD ASSOCIATED WITH REFINING THE SYNCRUDE. CONOCO WILL REMOVE AN EXISTING HEATER, CONSTRUCT A NEW HEATER, AND MODIFY EQUIPMENT AND/OR INCREASE CAPACITIES OF THE FOLLOWING PROCESS UNITS: NOS. 3 AND 4 CRUDE TOPPING UNITS; NOS. 2 AND 3 CRUDE VACUUM UNITS; NOS. 4 AND 7 HYDRODESULFURIZATION UNITS; FRACTIONATOR; NOS. 4 AND 5 HYDROGEN SYSTEMS; HYDROGEN PURIFICATION AND DISTRIBUTION; NOS. 1, 2, 3, AND 5 SOUR WATER STRIPPERS; NO. 4 SULFUR RECOVERY UNIT; MARINE TANK FARM; MARINE DOCK; TANK FARM; AND Y-5 COOLING TOWER. | HEATER, CRUDE VACUUM UNIT FEED (H-20002) | 12.39 | NATURAL GAS | 150 | MMBTU/H | HEATER BURNS NATURAL GAS AND REFINERY OFF GAS. |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 6.8 | LB/H* | HOURLY MAXIMUM | OPERATING PERMIT | 25 | T/YR* | ANNUAL MAXIMUM | 0.038 | LB/MMBTU* |  | *AS SET BY PSD-LA-584(M-3), DATED SEPTEMBER 20, 2002. PSD-LA-584(M-2) ORIGINALLY ESTABLISHED LIMITS AT 0.03 LB/MMBTU, 4.5 LB/H (HOURLY MAXIMUM), AND 19.7 T/YR (ANNUAL MAXIMUM).
LA-0119 | LAKE CHARLES REFINERY | CONOCO INC. | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1999-08-12 | 1999 | PERMIT TO IMPLEMENT THE PETROZUATA SYNCRUDE PROJECT, ALLOWING REFINERY TO PROCESS A MIXTURE OF VIRGIN CRUDE AND CUTTER STOCK. SECURES A GUARANTEED CRUDE SUPPLY AND INCREASE PRODUCTION OF HEAVY PRODUCTS. MODIFICATION TO VARIOUS PROCESS UNITS WILL BE REQUIRED TO ENABLE THE FACILITY TO PROCESS THE INCREASED SULFUR LOAD ASSOCIATED WITH REFINING THE SYNCRUDE. CONOCO WILL REMOVE AN EXISTING HEATER, CONSTRUCT A NEW HEATER, AND MODIFY EQUIPMENT AND/OR INCREASE CAPACITIES OF THE FOLLOWING PROCESS UNITS: NOS. 3 AND 4 CRUDE TOPPING UNITS; NOS. 2 AND 3 CRUDE VACUUM UNITS; NOS. 4 AND 7 HYDRODESULFURIZATION UNITS; FRACTIONATOR; NOS. 4 AND 5 HYDROGEN SYSTEMS; HYDROGEN PURIFICATION AND DISTRIBUTION; NOS. 1, 2, 3, AND 5 SOUR WATER STRIPPERS; NO. 4 SULFUR RECOVERY UNIT; MARINE TANK FARM; MARINE DOCK; TANK FARM; AND Y-5 COOLING TOWER. | HEATER, NO. 4 CTU (H-4050) | 12.39 | NATURAL GAS | 237 | MMBTU/H | UNIT BURNS NATURAL GAS AND REFINERY OFF GAS. FORMERLY IDENTIFIED AS H-40001 |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 9.1 | LB/H* | HOURLY MAXIMUM | OPERATING PERMIT | 33.2 | T/YR* | ANNUAL MAXIMUM | 0.032 | LB/MMBTU |  | *AS SET BY PSD-LA-584(M-3), DATED SEPTEMBER 20, 2002. PSD-LA-584(M-2) ORIGINALLY ESTABLISHED LIMITS AT 7.1 LB/H (HOURLY MAXIMUM) AND 33.1 T/YR (ANNUAL MAXIMUM).
*PA-0193 | MERCK AND COMPANY - WEST POINT PLANT | MERCK AND COMPANY, INC | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 1999-08-26 | 1999 | COGEN PLANT | BOILER, NATURAL GAS, (2) | 12.31 | NATURAL GAS | 249 | MMBTU/H | LO-NOX BURNERS, FLUE GAS RECIRCULATION AND SCR SYSTEM |  | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS, FLUE GAS RECIRCULATION, AND SELECTIVE CATALYTIC REDUCTION | 0.012 | LB/MMBTU | [5 empty] | 0.012 | LB/MMBTU
SC-0049 | SKYGEN | BROAD RIVER ENERGY, LLC | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 1999-12-02 | 1999 |  | THREE NATURAL GAS FIRED BOILERS (UTILITY) | 12.31 | NATURAL GAS | 230 | MMBTU/H | 1700 H/YR MAX OPERATION PER BOILER. |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS WITH FLUE GAS RECIRCULATION AND GOOD COMBUSTIONPRACTICES | 0.04 | LB/MMBTU | [5 empty] | 0.04 | LB/MMBTU
TX-0429 | VALERO REFINING CO. - TEXAS CITY | VALERO REFINING CO. - TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-02-23 | 2000 | SITE IS A PETROLEUM REFINERY DESIGNED TO PROCESS CRUDE OIL INTO A VARIETY OF GASOLINES, DIESELS (INCLUDING LOW-S), AND DISTILLATE OILS | BOILERS AND HEATERS | 12.39 | NATURAL GAS |  |  | FUELS ARE NATURAL GAS AND REFINERY FUEL GAS. H2S CONCENTRATION < 162 PPMV OR 0.1 GR/DSCF |  | Nitrogen Oxides (NOx) | P | ULTRA LOW-NOX BURNERS | 0.06 | LB/MMBTU | [5 empty] | 0.06 | LB/MMBTU
TX-0294 | GATEWAY POWER PROJECT | GATEWAY POWER PROJECT LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-03-20 | 2000 | THIS IS A GRASS-ROOTS ELECTRICAL GENERATION FACILITY. THE PRIMARY EQUIPMENT CONSISTS OF THREE COMBUSTION TURBINES DRIVING ELECTRICAL GENERATORS, WHERE EACH GENERATOR IS RATED NOMINALLY AT 170 MW. THE TURBINES OPERATE IN COMBINED CYCLE MODE IN WHICH A SUPPLEMENTARY FIRED HEAT RECOVERY STEAM GENERATOR (HRSG) WILL BE UTILIZED. THE ASSOCIATED DUCT BURNERS WILL EACH HAVE A MAXIMUM RATING OF 290 MMBTU/H HEAT INPUT. THE TURBINES AND DUCT BURNERS WILL BE FIRED WITH PIPELINE-QUALITY NAT GAS ONLY. PROCESS STEAM FROM THE HRSGS WILL BE USED BY THREE STEAM TURBINES TO GENERATE UP TO 90 MW ADDITIONAL ELECTRICITY EACH. THE THREE COMBINED CTG-HRSG UNITS WILL HAVE A NOMINAL CAPACITY OF 800 MW. | (3) DUCT BURNERS | 12.31 | NAT GAS | 160 | MMBTU/H, EA | PERMIT INDICATES STANDARD EMISSION LIMITS FOR NOX, CO, AND VOC SEPARATELY FOR THIS PROCESS, HOWEVER THEY ARE CONSIDERED AS A COMBINED PROCESS WITH THE TURBINES. |  | Nitrogen Oxides (NOx) | P | DRY LOW-NOX BURNERS | 0.08 | LB/MMBTU | EACH UNIT |  |  |  |  | 0.08 | LB/MMBTU | EACH UNIT
AK-0037 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFIDE CONTENT TO 0.01% FROM 0.001%, AN INCREASE IN OPERATING HOURS OF P708C FROM 200 TO 600 HOURS PER YEAR, THE REMOVAL OF PERCENT EFFICIENCY REQUIREMENTS FOR AS1310 AND 1320, AND USE OF THERMAL OXIDATION TO CONTROL EMISSIONS FROM AS1320. | CRUDE HEATER, H101A | 12.39 | NATURAL GAS* | 140 | MMBTU/H | INSTALLED PRIOR TO 1975, THEREFORE NOT REQUIRED TO COMPLY WITH THE PSD PROGRAM. DESIGN CAPACITY OF 140.0 MMBTU/H AUTHORIZED RATED CAPACITY IS 1 MMBTU/H. *FUELS ARE NATURAL GAS, REFINERY GAS AND LPG. NO INDICATION IS PROVIDED AS TO WHICH IS THE PRIMARY FUEL. |  | Nitrogen Oxides (NOx) | N | NONE INDICATED | 0.25 | LB/MMBTU |  | NSPS |  |  |  | 0.25 | LB/MMBTU |  | ESTIMATED EMISSIONS ARE 153.3 T/YR, BUT THIS IS NOT AN EMISSION LIMIT.
AK-0037 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFIDE CONTENT TO 0.01% FROM 0.001%, AN INCREASE IN OPERATING HOURS OF P708C FROM 200 TO 600 HOURS PER YEAR, THE REMOVAL OF PERCENT EFFICIENCY REQUIREMENTS FOR AS1310 AND 1320, AND USE OF THERMAL OXIDATION TO CONTROL EMISSIONS FROM AS1320. | CRUDE HEATER, H101B | 12.39 | NATURAL GAS* | 165 | MMBTU/H | DESIGN CAPACITY IS 165.0 MMBTU/H BUT AUTHORIZED RATED CAPACITY IS 1 MMBTU/H. *SOURCE BURNS COMBINATION OF REFINERY GAS, NATURAL GAS, AND LIQUID PETROLEUM GAS. IT IS NOT SPECIFIIED WHICH TYPE OF FUEL IS PRIMARY. |  | Nitrogen Oxides (NOx) | N | NONE INDICATED | 0.06 | LB/MMBTU | [5 empty] | 0.06 | LB/MMBTU |  | ESTIMATED EMISSIONS ARE 43.4 T/YR, BUT THIS IS NOT A LIMIT.
TX-0395 | DIAMOND SHAMROCK MCKEE PLANT | DIAMOND SHAMROCK REFINING COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-05-23 | 2000 |  | NO. 1 REFORMER CHARGE HEATER | 12.39 | REFINERY GAS | 248 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | N |  | 12.4 | LB/H |  |  | 54.32 | T/YR |  | 0.05 | LB/MMBTU | CALCULATED
TX-0395 | DIAMOND SHAMROCK MCKEE PLANT | DIAMOND SHAMROCK REFINING COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-05-23 | 2000 |  | NO 1 INTERHEATER | 12.39 | REFINERY GAS | 147.2 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | N |  | 7.36 | LB/H |  |  | 32.24 | T/YR |  | 0.05 | LB/MMBTU | CALCULATED
TX-0333 | MONT BELVIEU COMPLEX | TAME ENVIRO-FUEL PARTNERS - ENTERPRISE PRODUCTS CO | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-12-05 | 2000 | TAME ENVIRO-FUELS PARTNERS (TEF) IS PROPOSING TO CONSTRUCT A NEW TERTIARY- AMYL-METHYL-ETHER (TAME) MANUFACTURING PLANT AT THE MONT BELVIEU COMPLEX, WHICH IS OWNED BY ENTERPRISE PRODUCTS COMPANY. LIKE METHYL-TERTIARY-BUTYL- ETHER (MTBE), TAME IS AN OXYGENATED ADDITIVE THAT INCREASES THE OCTANE RATING OF AUTO GASOLINE WHILE DECREASING AUTO EMISSIONS (NOX & VOC). THE EMISSIONS FROM THIS PROJECT WILL CONSIST MAINLY OF PRODUCTS OF COMBUSTION & VOC. THE PLANT''S FIREWATER ENGINE, WHICH POWERS THE WATER SPRAY SYSTEM WILL BE USED TO FIGHT FIRES. THE REVIEW OF THIS PROJECT WAS LENGTHENED CONSIDERABLY DUE TO A NUMBER OF THINGS. FIRST, IT HAS BEEN ASSIGNED (FOR VARIOUS REASONS) TO THREE ENGINEERS. SECOND, THERE WERE TWO TECHNICAL ISSUES THAT REQUIRED EXPERTISE OUTSIDE OF THE AIR PERMITS DIVISION. THIS ISSUE TOOK OVER A YEAR & THE EFFORTS OF STAFF FROM SEVERAL AGENCY DIVISIONS TO RESOLVE. THE BOTTOM LINE IS THAT WE WILL ALLOW ENTERPRISE & ALL ITS JOINT VENTURES TO BE VIEWED SEPARATELY FOR NSR, BUT AS A SINGLE ENTITY FOR TITLE V PURPOSES, HOWEVER, THIS IS THE EXCEPTION TO THE RULE. THE TNRCC POLICY IS THAT AS OF SEPTEMBER 1, 1999, ALL SOURCES AT A SITE THAT ARE OPERATED UNDER ONE OR MORE COMPANIES THAT SHARE COMMON OWNERSHIP &/OR CONTROL WILL BE REVIEWED THE SAME UNDER NSR & TITLE V. THIS MEANS ONE NSR & ONE TITLE V PERMIT FOR THE ENTIRE SITE, OR MULTIPLE NSR & MULTIPLE TITLE V PERMITS (TO EACH JOINT VENTURE). THIS FACILITY IS AUTHORIZED TO CONTAIN A MAX OF 2 TONS OF CL2 AT ANY ONE TIME. | DUCT BURNERS | 12.31 | TURBINE EXHAUST | 128 | MMBTU/H | PERMIT DOES NOT INDICATE THE USE OF SUPPLEMENTAL FUEL. THE TURBINE'S EXHAUST FEEDS INTO THE DUCT BURNER. |  | Nitrogen Oxides (NOx) | A | SELECTIVE CATALYTIC REDUCTION | 0.092 | LB/MMBTU |  | NSPS |  |  |  | 0.092 | LB/MMBTU
TN-0146 | FLORIM, USA, INC. | FLORIM, USA, INC. | TN | TENNESSEE DIV OF AIR POLLUTION CONTROL | 2000-12-20 | 2000 | CERAMIC TILE MANUFACTURING PROCESS CONSISTING OF RAW MATERIAL HANDLING, SPRAY DRYING, TILE PREPARATION, AND TILE FIRING OPERATIONS. THE COMPANY APPLIED FOR A PSD PERMIT TO INCREASE THE MATERIAL INPUT RATE THROUGH THE FACILITY'S TILE KILNS. | GAS-FIRED KILNS | 12.31 | NATURAL GAS | 125 | MMBTU/H | Seven (7) gas-fired tile kilns and one (1) gas-fired trim kiln with lime injection/coated baghouse controls. |  | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICES | 0.241 | LB/MMBTU |  |  | 30.1 | LB/H |  | 0.241 | LB/MMBTU |  | The facility must meet compliance with production limits and recordkeeeping requirements to demonstrate compliance with emission limits.
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | 2001 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORIZED FIRING RATE WILL BE 481 MMBTU/H ON A ROLLING 12 MONTH AVERAGE, AND 502 MMBTU/H MAXIMUM HOURLY FIRING RATE. THE ADDITION OF THE NEW FURNACE TRIGGERED PSD REVIEW. | FURNACE HF-01 | 12.39 | ETHANE | 238 | MMBTU/H | 200 MMBTU/H AVE. FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% THEANE/PROPANE MIXTURE. |  | Nitrogen Oxides (NOx) | N | NONE INDICATED | 42.1 | LB/H |  |  | 52.6 | T/YR |  | 0.177 | LB/MMBTU | HOURLY AV | ADDITIONAL LIMITS: 0.060 LB/MMBTU ROLLING 12-MO AV. NOX LIMITS ARE NOT APPLICABLE WHEN THE CRACKING FURNACE IS IN ITS DECOKING CYCLE; HOWEVER THE NOX MASS EMISSIONS RATES SPECIFIED SHALL NOT BE EXCEEDED WHEN THE FURNACE IS IN ITS DECOKING CYCLE.
IN-0085 | PSEG LAWRENCEBURG ENERGY FACILITY | PSEG LAWRENCEBURG ENERGY FACILITY | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-06-07 | 2001 |  | AUXILIARY BOILER, NATURAL GAS | 12.31 | NATURAL GAS | 124.6 | MMBTU/H | AUXILIARY BOILER IS LIMITED TO 1000 H/YR OF OPERATION |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS. NATURAL GAS ONLY | 0.036 | LB/MMBTU |  |  | 4.49 | LB/H |  | 0.036 | LB/MMBTU
OK-0045 | REDBUD POWER PLT | REDBUD ENERGY LP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-15 | 2001 | ELECTRICAL GENERATION FACILITY | BOILER, AUXILIARY | 12.31 | NATURAL GAS | 20 | MMBTU/H | boiler operates < 3000 hours per year |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.049 | LB/MMBTU | [5 empty] | 0.049 | LB/MMBTU
AR-0057 | TENASKA ARKANSAS PARTNERS, LP | TENASKA ARKANSAS PARTNERS, LP | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-10-09 | 2001 | ELECTRIC POWER GENERATING STATION. FACILITY WAS NEVER CONSTRUCTED AND THE PERMIT WAS VOIDED 1/07/03. ADDITIONAL PLANTWIDE EMISSIONS: PM10 858 T/YR, AMMONIA 844 T/YR. | BOILER, NATURAL GAS, (2) | 12.31 | NATURAL GAS | 122 | MMBTU/H | Throughput for each boiler. |  | Nitrogen Oxides (NOx) | P | FLUE GAS RECIRCULATION (FGR). | 0.04 | LB/MMBTU | [5 empty] | 0.04 | LB/MMBTU
AR-0055 | NUCOR YAMATO STEEL (ARMOREL) | NUCOR YAMATO STEEL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-10-10 | 2001 | STEEL MILL. | REHEAT FURNACE | 12.31 | NATURAL GAS | 225 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS WITH EGR | 0.094 | LB/MMBTU | [5 empty] | 0.094 | LB/MMBTU
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | 2001 | ELECTRICITY GENERATION | AUXILIARY BOILER | 12.31 | NATURAL GAS | 120 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | P | LIMITED OPERATION OF 3600 H/YR | 0.036 | LB/MMBTU |  |  | 4.32 | LB/H |  | 0.036 | LB/MMBTU
FL-0251 | OKEELANTA CORPORATION SUGAR MILL | NEW HOPE POWER PARTNERSHIP | FL | FLORIDA DEPT. OF ENVIRONMENTLA PROTECTION | 2001-10-29 | 2001 | SUGAR MILL | BOILER, NATURAL GAS | 12.31 | NATURAL GAS | 211 | MMBTU/H | State SIP rule requires a BACT for SO2 and PM emissions regardless of increase. The efficient combustion of clean fuels will minimize emissions of CO, PM/PM10, SO2, and VOC. The installation of low NOx burners with flue gas recirculation will reduce NOx emissions. |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS W/FLUE GAS RECIRCULATION AND GOOD COMBUSTION. | 0.06 | LB/MMBTU | [5 empty] | 0.06 | LB/MMBTU
WV-0015 | E.I. DUPONT - WASHINGTON WORKS | E. I. DUPONT DE NEMOURS AND COMPANY | WV | WEST VIRGINIA AIR POLLUTION CONTROL COMM | 2002-01-02 | 2002 | FACILITY IS INVOLVED IN A WIDE RANGE OF PLASTICS PRODUCTION. THE AFFECTED BOILER IS PART OF THE POWER PLANT OF THE FACILITY. | BOILER, NATURAL GAS, 181 MMBTU/H | 12.31 | NATURAL GAS | 181 | MMBTU/H | 181.00 MMBTU/HR N/G FIRED BOILER. UTILIZES LOW-NOX BURNERS, FLUE-GAS RECIRCULATION AND COMBUSTION CONTROLS TO CONTROL NOX. ALSO UTILIZES NOX CEMS TO ENSURE COMPLIANCE. ONLY NOX IS SUBJECT TO PSD. |  | Nitrogen Oxides (NOx) | P | BOILER USES LOW-NOX BURNERS, FLUE GAS RECIRCULATION AND COMBUSTION CONTROLS TO CONTROL NOX. | 18.1 | LB/H |  |  | 79.28 | T/YR |  | 0.1 | LB/MMBTU
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BTU-NO. 1 REACTOR FEED HEATER | 12.39 |  | 121.74 | MMBTU/H | EMISSION POINT NO. BTU-HF103. |  | Nitrogen Oxides (NOx) | A | SCR | 4.4 | LB/H | SEE NOTES |  | 19.2 | T/YR | SEE NOTES | 0.036 | LB/MMBTU | CALCULATED | ADDITIONAL EMISSION LIMITS: PRE-INSTALLATION OF SCR: 8.50 LB/H AND 37.30 T/YR.
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ISOM II WEST REACTOR FEED HEATER | 12.39 |  | 104.25 | MMBTU/H | EMISSION POINT NO. BTU-HF106. |  | Nitrogen Oxides (NOx) | A | SCR | 3.8 | LB/H | SEE NOTES |  | 16.4 | T/YR | SEE NOTES | 0.036 | LB/MMBTU | CALCULATED | ADDITIONAL EMISSION LIMITS APPLICABLE PRIOR TO INSTALLATION OF SCR: 7.30 LB/H AND 32.00 T/YR.
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ORTHOXYLENE II HEATER | 12.39 |  | 226.42 | MMBTU/H | EMISSION POINT NO.: ORTHOII-H2. |  | Nitrogen Oxides (NOx) | A | SCR | 8.2 | LB/H | SEE NOTES |  | 35.7 | T/YR | SEE NOTES | 0.036 | LB/MMBTU | CALCULATED | ADDITIONAL EMISSION LIMITS APPLICABLE PRIOR TO INSTALLATION OF SCR: 15.80 LB/H AND 69.40 T/YR.
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BOILER NO. 12 | 12.39 |  | 245 | MMBTU/H | EMISSION PT NO: BOILER-12. SHALL BE SHUTDOWN. |  | Nitrogen Oxides (NOx) | N |  | 19.6 | LB/H |  |  | 85.8 | T/YR |  | 0.08 | LB/MMBTU | CALCULATED
CA-1113 | PRAXAIR | PRAXAIR | CA | SOUTH COAST AQMD, CA | 2002-03-15 | 2002 |  | HEATER-OTHER PROCESS | 12.39 | WASTE GAS | 117.6 | MMBTU/H | EQUIP: , MFR: SELAS FLUID PROCESING CORPORATION, TYPE: HYDROGEN REFORMER, MODEL: LH 1207 B001, FUNC EQUIP: PROVIDES HEAT TO CATYST FILLED TUBES TO PRODUCE HYDROGEN-*, FUEL_TYPE: NATURAL GAS (WARM UP AND SUPPLEMENT), SCHEDULE: CONTINUOUS, H/D: 24, D/W: 7, W/Y: 52, NOTES: AMMONIA IS MIXED INTO FLUE GAS, AND THE MIXTURE IS PASSED THROUGH A CATALYST BED, IN WHICH THE AMMONIA REACTS WITH NOX REDUCING IT TO N2. SCR DESIGN OPERATING TEMPERATURE IS 760F, AND DESIGN REMOVAL EFFICIENCY IS 90%. A SOURCE TEST IS REQUIRED WITHIN 90 DAYS AFTER STARTUP FOR NOX, CO, ROG, NH3, PM, SOX. THE FACILITY IS IN RECLAIM, AND WILL HAVE CEMS FOR NOX AND O2. THE PERMIT REQUIRES CEMS FOR NH3 ALSO; HOWEVER, THE APPLICANT IS REQUESTING TO SUBSTITUTE A PARAMETRIC MONITORING METHOD. |  | Nitrogen Oxides (NOx) | A | SCR SYSTEM | 50 | PPMVD @ 3% O2 | 1H | N/A |  |  |  | 0.061 | LB/MMBTU
TX-0386 | AMELLA ENERGY CENTER | CALPINE CONSTRUCTION FINANCE CO. LP | TX | CITY OF HOUSTON BUREAU AIR QUAL CTRL, TX | 2002-03-26 | 2002 |  | AUXILIARY BOILER | 12.31 | NATURAL GAS | 155 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | N |  | 6.2 | LB/H | [5 empty] | 0.04 | LB/MMBTU
TX-0411 | AMELIA ENERGY CENTER | CALPINE CONSTRUCTION FINANCE COMPANY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-26 | 2002 | NEW 1030 MW COMBINED CYCLE COGENERATION FACILITY CONSISTING OF THREE 180 MW WESTINGHOUSE 501F COMBUSTION TURBINES EACH EQUIPPED WITH A HEAT RECOVERY STEAM GENERATOR AND 400 MMBTU/H DUCT BURNER. | BOILER, AUXILIARY, NATURAL GAS | 12.31 | NATURAL GAS | 155 | mmbtu/h | BACT FOR NOX ONLY. |  | Nitrogen Oxides (NOx) | N |  | 0.04 | LB/MMBTU | [5 empty] | 0.04 | LB/MMBTU
NJ-0043 | LIBERTY GENERATING STATION | LIBERTY GENERATING STATION | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2002-03-28 | 2002 | ELECTRICITY GENERATION | AUXILIARY BOILER | 12.31 | NATURAL GAS | 200 | MMBTU/H | NATURAL GAS USAGE RESTRICTED TO 181.0 MILLION SCF/YR (EQUIVALENT TO A 10% ANNUAL CAPACITY FACTOR) |  | Nitrogen Oxides (NOx) | A | SCR | 0.2 | LB/MMBTU |  |  | 7.2 | LB/H |  | 0.036 | LB/MMBTU |  | BASIS OF LIMIT IS STATE.
TN-0153 | WILLIAMS REFINING & MARKETING, L.L.C. | WILLIAMS REFINING & MARKETING, L.L.C. | TN | MEMPHIS AND SHELBY CO HEALTH DEPT, TN | 2002-04-03 | 2002 | PETROLEUM REFINERY | BOILER, NO. 10 | 12.31 | NATURAL GAS | 180 | MMBTU/H | annual capacity factor (ACF) for natural gas, coal or oil shall not exceed 10% |  | Nitrogen Oxides (NOx) | N |  | 0.06 | LB/MMBTU | [5 empty] | 0.06 | LB/MMBTU
LA-0121 | CONVENT REFINERY | MOTIVA ENTERPRISES LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-05-17 | 2002 | PERMIT IS TO MODIFY AN EXISTING FACILITY TO MANUFACTURE LOW SULFUR GASOLINE, BY INSTALLING A HYDRO- DESULFURIZATION UNIT (HDS-1) AND MODIFYING ITS SULFUR BLOCK AND H-OIL UNIT (VACUUM RESIDUUM UPGRADE UNIT). | HDS-1 HEATER | 12.39 | FUEL GAS | 140 | MMBTU/H | EMISSION POINT 96H-201 |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 5.6 | LB/H |  |  | 17.52 | T/YR |  | 0.04 | LB/MMBTU | CALCULATED | EMISSION LIMIT IN STANDARDIZED UNITS CALCULATED BY DIVIDING THE HOURLY EMISSION LIMIT BY THE HOURLY THROUGHPUT: 5.6 LB/H / 140 MMBTU/H.
CA-1024 | AES HUNTINGTON BEACH | AES HUNTINGTON BEACH | CA | SOUTH COAST AQMD, CA | 2002-08-01 | 2002 |  | BOILER: >= 50 MMBTU/HR | 12.31 | NATURAL GAS | 225 | MW | EQUIP: ELECTRIC UTILITY BOILER, MFR: BABCOCK & WILCOX, TYPE: MULTI-WALL FIRED, MODEL: , FUNC EQUIP: USE IS CURRENTLY FOR PEAK POWER DEMAND PERIODS, FUEL_TYPE: , SCHEDULE: VARIABLE, H/D: 24, D/W: 5, W/Y: 20, NOTES: FACILITY APPLIED TO BRING THIS RETIRED BOILER BACK INTO SERVICE. FACILITY IS EXPERIENCING DIFFICULTY MEETING NOX AND AMMONIA LIMITS ON ONE- HOUR AVERAGING BASIS, AND DISTRICT IS CONSIDERING REQUEST FOR LONGER AVERAGING TIME. SOURCE TEST RESULTS: PPM@3%O2, GR/DSCF: 225 MW: NOX-3.5, CO-0.0, VOC- 4.2, NH3-3.1, PM-.001. 169 MW: NOX-4.2, NH3-1.6, PM-.002. 115MW: NOX-3.8, NH3-0.5. 90 MW: NOX-4.5, NH3-0.7, PM-.004 |  | Nitrogen Oxides (NOx) | A | LOW-NOX BURNERS, FLUE GAS RECIRC., SELECTIVE CAT. RED. | 5 | PPMVD @3% O2 | 1-H AV | N/A | [5 empty] | NOT AVAILABLE
CO-0052 | ROCKY MOUNTAIN ENERGY CENTER, LLC. | ROCKY MOUNTAIN ENERGY CENTER, LLC. | CO | COLORADO DEPT OF HEALTH - AIR POLL CTRL | 2002-08-11 | 2002 | ELECTRIC POWER | NATURAL GAS FIRED BOILER (AUXILIARY BOILER) | 12.31 | NATURAL GAS | 129 | MMBTU/H | THIS BOILER IS USED TO HEAT AND MAINTAIN TEMPERATURE IN STEAM TURBINE CONDENSER. |  | Nitrogen Oxides (NOx) | P | OPERATION IS LIMITED TO 1900 H/YR. LOW NOX COMBUSTION SYSTEM. | 0.038 | LB/MMBTU | [5 empty] | 0.038 | LB/MMBTU
AR-0070 | GENOVA ARKANSAS I, LLC | GENOVA ARKANSAS I, LLC | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-08-23 | 2002 | COMBINED CYCLE POWER PLANT | DUCT BURNERS | 12.31 | NATURAL GAS | 200 | MMBTU/H | 2 DUCT BURNERS UNDER ANY SCENARIO. INFORMATION PROVIDED IS FOR EACH UNIT. |  | Nitrogen Oxides (NOx) | B | LOW NOX BURNER/SCR | 0.08 | LB/MMBTU | [5 empty] | 0.08 | LB/MMBTU
GA-0096 | SOUTHERN LNG, INC. ELBA ISLAND FACILITY | SOUTHERN LNG, INC. | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2003-02-17 | 2003 | LIQUIFIED NATURAL GAS TERMINAL | LNG VAPORIZER (3) | 12.31 | NATURAL GAS | 121.4 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | P | WATER INJECTION AND GOOD COMBUSTION PRACTICES | 0.08 | LB/MMBTU | [5 empty] | 0.08 | LB/MMBTU
GA-0103 | ELBA ISLAND, LNG TERMINAL | SOUTHERN LNG INC | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2003-02-17 | 2003 | LIQUEFIED NATURAL GAS (LNG) TERMINAL | LNG VAPORIZER, (3) | 12.31 | NATURAL GAS | 121.4 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | P | WATER INJECTION | 0.08 | LB/MMBTU | [5 empty] | 0.08 | LB/MMBTU
VA-0278 | VCU EAST PLANT | Virginia Commonwealth University | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-31 | 2003 | STEAM GENERATING PLANT AT UNIVERSITY | BOILER, NATURAL GAS, (3) | 12.31 | NATURAL GAS | 150.6 | MMBTU/H | Throughput for each. The 3 boilers shall consume no more than 3,500 million cf of natural gas per year |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS, FLUE GAS RECIRCULATION, AND GOOD OPERATING PROCEDURES | 15.6 | LB/H |  |  | 0.1 | LB/MMBTU | 30-day rolling avg | 0.08 | LB/MMBTU | annual avg
OK-0089 | TPI PETROLEUM INC., VALERO ARDMORE REFINERY | TPI PETROLEUM INC. | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2003-06-09 | 2003 | FACILITY PROCESSES MEDIUM AND SOUR CRUDE OILS FROM BOTH THE DOMESTIC AND FOREIGN MARKETS | CRUDE UNIT HEATER, H-102A | 12.39 |  | 145 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 0.045 | LB/MMBTU |  |  | 28.6 | T/YR |  | 0.045 | LB/MMBTU
OK-0089 | TPI PETROLEUM INC., VALERO ARDMORE REFINERY | TPI PETROLEUM INC. | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2003-06-09 | 2003 | FACILITY PROCESSES MEDIUM AND SOUR CRUDE OILS FROM BOTH THE DOMESTIC AND FOREIGN MARKETS | CRUDE UNIT HEATER, H-102B | 12.39 |  | 135 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 0.059 | LB/MMBTU |  |  | 34.9 | T/YR |  | 0.059 | LB/MMBTU
WI-0204 | UWGP - FUEL GRADE ETHANOL PLANT | UNITED WISCONSIN GRAIN PRODUCERS | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2003-08-14 | 2003 | FERMENTATION BASED PROCESS WITH DISTILLATION, MOLECULAR SIEVES FOR FINAL WATER REMOVAL. ETHANOL DENATURED USING GASOLINE. | BOILER /OXIDIZER ( DRYER / DISTILLATION), P10 | 12.31 | NATURAL GAS | 140 | MMBTU/H | Boiler works as control device. RECEIVES VOC'S FROM DISTILLATION AND RELATED PROCESSES AND FROM Distillers dried grain with solubles (DDGS) DRYER (85 MMBTU/HR.). SUBJECT TO DB |  | Nitrogen Oxides (NOx) | P | BOILER / BURNER DESIGN | 0.095 | LB/MMBTU | [5 empty] | 0.095 | LB/MMBTU |  | SYNTHETIC MINOR SOURCE: LIMIT (SLIGHTLY) MORE STRINGENT THAN NSPS
LA-0197 | ALLIANCE REFINERY | CONOCOPHILLIPS CO | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2003-10-03 | 2003 | CLEAN FUELS PROJECT TO COMPLY WITH TIER 2 SULFUR STANDARDS. PROJECT INVOLVES CONSTRUCTION OF A CHARGE HEATER, A REBOILER, 3 INTERMEDIATE GASOLINE STORAGE TANKS, AND PIPING AND FUGITIVE COMPONENTS. ALSO, STEAM PRODUCTION FROM THE EXISTING BOILERS, COOLING TOWER RECIRCULATION RATE, SULFUR PRODUCTION AT THE SULFUR RECOVERY UNITS, AND WASTEWATER THROUGHPUT WILL ALSO INCREASE. | LOW SULFUR GASOLINE FEED HEATER NO. 1 | 12.39 | FUEL GAS | 138.12 | MMBTU/H | AVERAGE HEAT INPUT = 115.10 MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS WITH INTERNAL FLUE GAS RECIRCULATION | 4.6 | LB/H | HOURLY MAXIMUM | OPERATING PERMIT | 20.17 | T/YR | ANNUAL MAXIMUM | 0.04 | LB/MMBTU | ANNUAL AVERAGE
PA-0231 | UNITED REFINERY CO. | UNITED REFINERY CO | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2003-10-09 | 2003 | THE MODIFICATIONS INCLUDE THE INSTALLATION OF THREE NEW SOURCES AND MODS TO EXISTING SOURCES, THIS PERMIT ACTION IS SUBJECT TO SUBPARTS J,GGG QQQ OF THE NSPS, MACT SUBPARTS CC AND UUU AND NESHAPS SUBPARTS FF AND IS PSD FOR CO. | NORTH CRUDE HEATER | 12.39 | REFINERY GAS | 147 | MMBTU/H | The north crude heater was modified by installing low NOx burners. The reduction of NOx emissions reduces the overall increase below significant levels allowing the project to net out" of NSR and PSD for NOx." |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 6.68 | LB/H |  |  | 29.5 | T/YR |  | 0.045 | LB/MMBTU | Calculated using heat input | Best available technology (BAT) review done.
PA-0231 | UNITED REFINERY CO. | UNITED REFINERY CO | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2003-10-09 | 2003 | THE MODIFICATIONS INCLUDE THE INSTALLATION OF THREE NEW SOURCES AND MODS TO EXISTING SOURCES, THIS PERMIT ACTION IS SUBJECT TO SUBPARTS J,GGG QQQ OF THE NSPS, MACT SUBPARTS CC AND UUU AND NESHAPS SUBPARTS FF AND IS PSD FOR CO. | DELAYED COKER UNIT, HEATER | 12.39 | REFINERY GAS | 116 | MMBTU/H | The unit is subject to the NSPS 40 CFR Subpart J, Subpart GGG, Subpart QQQ. The unit is also subject to MACT standards in 40 CFR 63 Subpart CC, and NESHAP requirements in 40 CFR 61 Subpart FF. |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 4.04 | LB/H |  |  | 17.7 | T/YR |  | 0.035 | LB/MMBTU | Calculated using heat input | Best available technology (BAT) review done.
LA-0183 | TITANIUM DIOXIDE FACILITY | LOUISIANA PIGMENT COMPANY, LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2003-11-14 | 2003 | TITANIUM DIOXIDE (TIO2) PRODUCTION FACILITY | BOILERS, UTILITY, D841-1X & D841-2X | 12.31 | NATURAL GAS | 135 | MMBTU/H | 135 MM BTU/H EA. |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS INCORPORATING OPTIMAL EXCESS AIR FIRING | 10 | LB/H | HOURLY MAXIMUM | OPERATING PERMIT | 37.7 | T/YR | ANNUAL MAXIMUM | 0.074 | LB/MMBTU | ANNUAL AVERAGE | PSD PERMIT GIVES LB/MM BTU RATE AT 0.10 LB/MM BTU; HOWEVER, THIS MUST BE IN ERROR, AS THIS RATE, COUPLED WITH THE BOILERS'' RATED HEAT INPUT OF 135 MM BTU/HR, RESULTS IN MAXIMUM HOURLY EMISSIONS OF 13.5 POUNDS. THE PSD CLEARLY ESTABLISHES THE MAXIMUM HOURLY RATE AT 10.00 LB/HR PER BOILER.
NC-0106 | UNIVERSITY OF NORTH CAROLINA - CHAPEL HILL | UNIVERSITY OF NORTH CAROLINA - CHAPEL HILL | NC | NORTH CAROLINA DIV OF ENV MGMT | 2004-02-10 | 2004 | NONPROFIT EDUCATIONAL INSTITUTION | MANNING STEAM PLANT (TWO BOILERS) | 12.31 | NATURAL GAS | 249 | MMBTU/H EACH |  |  | Nitrogen Oxides (NOx) | P | THE BOILERS ARE EQUIPPED WITH LOW NOX BURNERS AND FGR |  |  | SEE NOTE | NSPS | [6 empty] | BACT DOES NOT APPLY TO NONPROFIT EDUCATIONAL INSTALLATIONS.
WV-0023 | MAIDSVILLE | LONGVIEW POWER, LLC | WV | WEST VIRGINIA AIR POLLUTION CONTROL COMM | 2004-03-02 | 2004 | PULVERIZED COAL-FIRED STEAM GENERATOR CAPABLE OF GENERATING 600MW OF ELECTRIC POWER. THIS FACILITY IS A GREEN FIELD SITE, WHICH INCLUDES A 6,114 MMBTU COAL-FIRED BOILER, 225 MMBTU NATURAL GAS-FIRED AUX BOILER, EMERGENCY GENERATOR, FIRE WATER PUMP ENGINE, COOLING TOWERS, AND MATERIAL HANDLING SYSTEMS. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 225 | mmbtu/h | LIMITED TO NATURAL GAS USE AND 3,000 HOURS OF OPERATION PER YEAR |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND GOOD COMBUSTION PRACTICES | 0.098 | LB/MMBTU | 3 HOUR ROLLING AVERAGE | NSPS |  |  |  | 0.098 | LB/MMBTU | 3 HOUR ROLLING | LIMITED TO USE OF NATURAL GAS AND 3,000 HOURS OF OPERATION PER YEAR
OK-0098 | PONCA CITY REF | CONOCOPHILLIPS PONCA CITY REFINERY | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2004-03-31 | 2004 | CRUDE OIL REFINERY | CRUDE CHARGE UNIT, HEATER H-0001 | 12.39 | REFINERY FUEL GAS |  |  | Compliance to be verified by stack testing, then monitored with CEM |  | Nitrogen Oxides (NOx) | B | ULTRA LOW NOX BURNERS | 8.75 | LB/H | 365 day average |  | 38.33 | T/YR |  | 0.05 | LB/MMBTU |  | Because of operational mode, heater is not able to reach 0.035 lb/mmbtu
OK-0098 | PONCA CITY REF | CONOCOPHILLIPS PONCA CITY REFINERY | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2004-03-31 | 2004 | CRUDE OIL REFINERY | CRUDE VACUUM UNIT, HEATER H-0016 | 12.39 | REFINERY FUEL GAS |  |  | Compliance to be verified by stack testing |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 3.73 | LB/H | 365 day rolling average |  | 16.36 | T/YR |  | 0.035 | LB/MMBTU
ID-0015 | J R SIMPLOT COMPANY - DON SIDING PLANT | J R SIMPLOT COMPANY | ID | IDAHO DEPT OF ENVIRONMENTAL QUALITY | 2004-04-05 | 2004 | THE DON SIDING PLANT IS A PHOSPHATE FERTILIZER MANUFACTURING FACILITY. EMISSION UNITS REVIEWED FOR RACT INCLUDE: 300 SULFURIC ACID PLANT, 400 SULFURIC ACID PLANT, PHOSPHORIC ACID PLANT, RECLAIM COOLING TOWERS, GRANULATION I, GRANULATION II, GRANULATION III, AMMONIUM SULFATE PLANT, BABCOCK & WILCOX BOILER, HPB&W BOILER. | BOILER, 175 MMBTU/H | 12.31 | NATURAL GAS | 175 | MMBTU/H | HPB&W BOILER |  | Nitrogen Oxides (NOx) | P | LOW-NOX BURNER | 7 | LB/H |  | SIP | 30.7 | T/YR |  | 0.04 | LB/MMBTU | 30-DAY ROLLING AVG
OH-0241 | MILLER BREWING COMPANY - TRENTON | MILLER BREWING COMPANY | OH | HAMILTON CO-SOUTHWESTERN OH APCA | 2004-05-27 | 2004 | BEER BREWING AND PACKAGING. | BOILER (2), NATURAL GAS | 12.31 | NATURAL GAS | 238 | MMBTU/H | TWO BOILERS, CAPABLE OF BURNING AND WITH LIMITS FOR COAL, NATURAL GAS, NUMBERS 2 AND 6 FUEL OILS. POUND PER HOUR LIMITS ARE FOR EACH BOILER; AND EXCEPT FOR VOC AND CO, ALL T/YR LIMITS ARE FOR BOTH BOILERS COMBINED. THESE LIMITS FOR THE NATURAL GAS. |  | Nitrogen Oxides (NOx) | P | OVERFIRE AND SIDE FIRE AIR TO REDUCE FLAME TEMERATURE | 0.7 | LB/MMBTU |  | SIP | 1375.9 | T/YR | BOTH BOILERS TOGETHER, PER ROLLING 12-MO | 0.7 | LB/MMBTU
MS-0069 | DUPONT DELISLE FACILITY | E. I. DUPONT DE NEMOURS | MS | MISSISSIPPI DEPT OF ENV QUALITY | 2004-06-08 | 2004 | TITANIUM DIOXIDE PRODUCTION. | BOILER #3 | 12.31 | NATURAL GAS | 231 | MMBTU/H | AF-103. RETROFITTED TO BURN LANDFILL GAS IN ADDITION TO NATURAL GAS. |  | Nitrogen Oxides (NOx) | B | LOW-NOX BURNER WITH FGR. | 0.09 | LB/MMBTU |  |  | 20.79 | LB/H |  | 0.09 | LB/MMBTU
MS-0069 | DUPONT DELISLE FACILITY | E. I. DUPONT DE NEMOURS | MS | MISSISSIPPI DEPT OF ENV QUALITY | 2004-06-08 | 2004 | TITANIUM DIOXIDE PRODUCTION. | BOILER #4 | 12.31 | NATURAL GAS | 231 | MMBTU/H | MAY BURN LANDFILL GAS IN ADDITION TO NATURAL GAS. |  | Nitrogen Oxides (NOx) | B | LOW-NOX BURNER AND FGR. | 0.058 | LB/MMBTU |  |  | 13.4 | LB/H |  | 0.058 | LB/MMBTU
MS-0069 | DUPONT DELISLE FACILITY | E. I. DUPONT DE NEMOURS | MS | MISSISSIPPI DEPT OF ENV QUALITY | 2004-06-08 | 2004 | TITANIUM DIOXIDE PRODUCTION. | BOILER (RENTAL/TEMPORARY) | 12.31 | NATURAL GAS | 231 | MMBTU/H | AF-202. RENTAL BOILER MAY ONLY OPERATE 2,085 H/YR. |  | Nitrogen Oxides (NOx) | B | LOW-NOX BURNER WITH FGR. | 0.09 | LB/MMBTU |  |  | 20.79 | LB/H |  | 0.09 | LB/MMBTU
NE-0024 | CARGILL - BLAIR PLANT | CARGILL, INC. | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2004-06-22 | 2004 | WET CORN MILLING, ETHANOL, FRUCTOSE, CORN OIL, CLUTEN MEAL AND OTHER CORN BY- PRODUCTS. | BOILERS A, B & C | 12.31 | NATURAL GAS | 198 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS AND INDUCED DRAFT FLUE GAS RECIRCULATION | 0.07 | LB/MMBTU | [5 empty] | 0.07 | LB/MMBTU
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | AUXILLIARY NAT. GAS FIRED BOILER (B25, S25) | 12.31 | NATURAL GAS | 229.8 | MMBTU/H | THE AUXILIARY BOILER WILL BE USED TO PREHEAT STEAM TURBINE, PROVIDE PLANT HEATING AND PROVIDE SUPPLEMENTAL STEAM TO AUXILIARY EQUIPMENT WHEN THE MAIN SCPC BOILER IS OFFLINE. THE AUXILIARY BOILER WILL BE PACKAGED BOILER THAT WILL COMBUST ONLY NATURAL GAS. THE HOURS OF THE OPERATION OF THE AUXILIARY BOILER WILL BE LIMITED TO 2,000 HOURS IN ANY 12 CONSECUTIVE MONTHS. |  | Nitrogen Oxides (NOx) | P | NATURAL GAS, GOOD COMBUSTION PRACTICES, LOW NOX BURNERS | 0.1 | LB/MMBTU | 2000 H / 12 MO. ROLLING | NSPS | 22.9 | LB/H |  | 0.1 | LB/MMBTU | NOT AVAILABLE | HIGH HEAT RELEASE RATE BOILER (NSPS LIMIT OF 0.2 LBS/MMBTU)
LA-0194 | SABINE PASS LNG IMPORT TERMINAL | SABINE PASS LNG, LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2004-11-24 | 2004 | LNG TO BE TRANSFERRED FROM MARINE VESSELS INTO PRESSURIZED TANKS FOR STORAGE, THEN REGASIFIED USING VAPORIZERS. THE VAPORIZED NATURAL GAS WILL BE MEASURED AND SENT TO TRANSMISSION PIPELINES. | SUBMERGED COMBUSTION VAPORIZERS (24) | 12.31 |  | 108 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | B | WATER INJECTION AND GOOD COMBUSTION PRACTICES | 4.5 | LB/H | HOURLY MAXIMUM | OPERATING PERMIT | 17.5 | T/YR | ANNUAL MAXIMUM | 0.037 | LB/MMBTU |  | 30 | PPMV @ 3% O2* | *0.037 LB/MM BTU = ANNUAL AVERAGE 4.5 LB/H REPRESENTS STARTUP OPERATING SCENARIO.
OR-0046 | TURNER ENERGY CENTER, LLC | CALPINE | OR | OREGON DEPT OF ENVIRONMENTAL QUALITY | 2005-01-06 | 2005 | 620 MW TOTAL COMBINED CYCLE GAS TURBINES (2 TURBINES WITH HRSGS) | AUXILIARY BOILER | 12.31 | NATURAL GAS | 417904 | MMBTU/YR | BOILER USED TO PROVIDE AUXILIARY STEAM FOR STANDBY AND STARTUP CONDITIONS WILL BE OPERATED A MAXIMUM OF 3000 HOURS/YR. |  | Nitrogen Oxides (NOx) | A | SELECTIVE CATALYTIC REDUCTION | 0.011 | LB/MMBTU | 3-H BLOCK | NSPS |  |  |  | 0.011 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | VACUUM CRUDE CHARGE HEATER | 12.39 | REFINERY FUEL GAS OR NG | 101 | MMBTU/H | THIS UNIT IS IDENTIFIED BY EQUIPMENT ID # B-02100 |  | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS AND SELECTIVE CATALYTIC REDUCTION | 0.0125 | LB/MMBTU | THREE-HOUR ROLLING AVG |  |  |  |  | 0.125 | LB/MMBTU |  | THE INITIAL LIMIT FOR NOX IS 0.0125 LB PER MMBTU HEAT INPUT (HHV). AFTER THE FIRST 24 MONTHS, A NEW LIMIT IS TO BE ESTABLISHED BASED ON THE PERFORMANCE OF THE UNIT. A LIMIT OF 0.006 LB PER MMBTU MAY BE TAKEN WITHOUT REGARD TO THE UNIT PERFORMANCE.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | HYDROCRACKER UNIT MAIN FRACTIONATOR HEATER | 12.39 | REFINERY FUEL GAS OR NG | 211 | MMBTU/H | THIS UNIT IS IDENTIFIED BY EQUIPMENT ID # B-10500 |  | Nitrogen Oxides (NOx) | A | LOW-NOX BURNERS | 0.025 | LB/MMBTU | THREE HOUR ROLLING AVG |  |  |  |  | 0.025 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT CHARGE HEATER | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 122 | MMBTU/H | THIS UNIT IS IDENTIFIED BY EQUIPMENT ID # B-05110 |  | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS AND SELECTIVE CATALYTIC REDUCTION | 0.0125 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.0125 | LB/MMBTU |  | THE INITIAL LIMIT FOR NOX IS 0.0125 LB PER MMBTU HEAT INPUT (HHV). AFTER THE FIRST 24 MONTHS, A NEW LIMIT IS TO BE ESTABLISHED BASED ON THE PERFORMANCE OF THE UNIT. A LIMIT OF 0.006 LB PER MMBTU MAY BE TAKEN WITHOUT REGARD TO THE UNIT PERFORMANCE.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT INTERHEATER NO. 1 | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 192 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY EQUIPMENT ID # B-05120 |  | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS AND SELECTIVE CATALYTIC REDUCTION | 0.0125 | LB/MMBTU | 3-HOUR AVERAGE |  |  |  |  | 0.0125 | LB/MMBTU |  | THE INITIAL LIMIT FOR NOX IS 0.0125 LB PER MMBTU HEAT INPUT (HHV). AFTER THE FIRST 24 MONTHS, A NEW LIMIT IS TO BE ESTABLISHED BASED ON THE PERFORMANCE OF THE UNIT. A LIMIT OF 0.006 LB PER MMBTU MAY BE TAKEN WITHOUT REGARD TO THE UNIT PERFORMANCE.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT INTERHEATER NO. 2 | 12.39 | REFINERY FUEL GAS OR NATURAL GAS | 129 | MMBTU/H | THIS EQUIPMENT IS IDENTIFIED BY ID # B-05130 |  | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS AND SELECTIVE CATALYTIC REDUCTION | 0.0125 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.0125 | LB/MMBTU |  | THE INITIAL LIMIT FOR NOX IS 0.0125 LB PER MMBTU HEAT INPUT (HHV). AFTER THE FIRST 24 MONTHS, A NEW LIMIT IS TO BE ESTABLISHED BASED ON THE PERFORMANCE OF THE UNIT. A LIMIT OF 0.006 LB PER MMBTU MAY BE TAKEN WITHOUT REGARD TO THE UNIT PERFORMANCE.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | BUTANE CONVERSION UNIT ISOSTRIPPER REBOILER | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 222 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY ID # B-15110 |  | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS AND SELECTIVE CATALYTIC REDUCTION | 0.0125 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.0125 | LB/MMBTU |  | THE INITIAL LIMIT FOR NOX IS 0.0125 LB PER MMBTU HEAT INPUT (HHV). AFTER THE FIRST 24 MONTHS, A NEW LIMIT IS TO BE ESTABLISHED BASED ON THE PERFORMANCE OF THE UNIT. A LIMIT OF 0.006 LB PER MMBTU MAY BE TAKEN WITHOUT REGARD TO THE UNIT PERFORMANCE.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | DISTILLATE HYDROTREATER SPLITTER REBOILER | 12.39 | REFINERY FUEL GAS OR NATURAL GAS | 117 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY ID # B-08509 |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.032 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.032 | LB/MMBTU
TX-0478 | CITGO CORPUS CHRISTI REFINERY - WEST PLANT | CITGO REFINING AND CHEMICALS COMAPNY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-04-20 | 2005 |  | MIXED DISTILLATE HYDROHEATER REBOILER HEATER | 12.39 | REFINERY FUEL GAS | 82 | MMBTU/H | THE MDH UNIT REMOVES ORGANIC NITROGEN AND SULFUR FROM THE FEED STREAMS. FEEDSTOCK IS MIXED WITH HYDROGEN , HEATED, AND FED TO A REACTOR. A CATALYTIC REACTION CONVERTS THE ORGANIC SULFUR TO HYDROGEN SULFIDE AND THE NITROGEN COMPOUNDS TO AMMONIA. THE EFFLUENT STREAM IS COOLED AND EXCESS HYDROGEN REMOVED FOR RECYCLE. HYDROGEN SULFIDE IS REMOVED FROM THE HYDROGEN STREAM BY AN AMINE ABSORBER AND ROUTED TO THE SRU. NEW EQUIPMENT UNDER THE AMENDMENT INCLUDES A SECOND REACTOR, ADDITIONAL PREHEAT TRAIN, AN ADDITIONAL REACTOR PRODUCT FLASH DRUM, A HYDROGEN PURIFICATION MEMBRANE AND AN ADDITIONAL HYDROGEN MAKEUP COMPRESSOR. AS PART OF THE AMENDMENT, THE FRACTIONATOR REBOILER WILL BE RETROFIT WITH LOW NOX BURNERS. |  | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS | 9.9 | LB/H |  |  | 43.3 | T/YR |  | 0.12073 | LB/MMBTU
TX-0492 | VIRTEX PETROLEUM COMPANY DOERING RANCH GAS PLANT | VIRTEX PETROLEUM INC. | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-05 | 2005 | VIRTEX CURRENTLY OPERATES A GAS PLANT WHICH IS AUTHORIZED UNDER AN OIL AND GAS STANDARD PERMIT. THE MAXIMUM PRODUCTION IS CURRENTLY AUTHORIZED AT 0.3 LONG TONS PER DAY OF SULFUR. THEY ARE REQUESTING AUTHORIZATION TO MODIFY THE EXISTING FACILITY TO PROCESS SOUR GAS FROM NEW FIELD WELLS AND INCREASE MAXIMUM PRODUCTION TO 0.75 LONG TONS PER DAY OF SULFUR (4.0 MMSDFD OF GAS WITH AN H2S CONTENT OF 8.000 PPM). MODIFICATIONS INCLUDE THE INSTALLATION OF NEW COMPRESSORS, AUTHORIZING AN AMINE SWEETENING UNIT, A LARGER CAPACITY GLYCOL DEHYDRATOR, AND ALL ASSOCIATED PIPING. THE INCREASE IN SO2 REQUIRES PSD ANALYSIS. | 1.8 MMBTU AMINE REBOILER | 12.39 | SWEET NATURAL GAS | 1.8 | MMBTU |  |  | Nitrogen Oxides (NOx) | N |  | 0.17 | LB/H |  |  | 0.76 | T/YR |  | 0.094444 | LB/MMBTU
TX-0475 | FORMOSA POINT COMFORT PLANT | FORMOSA PLASTICS CORPORATION TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-09 | 2005 |  | PYROLYSIS FURNACE (1010B) | 12.39 | FUEL GAS | 250 | MMBtu/H |  |  | Nitrogen Oxides (NOx) | B | THE PYROLYSIS FURNACES WILL USE INTERNAL FLUE GAS RECIRCULATION (IFGR) AND STAGED FUEL GAS ULTRA LOW-NOX BURNERS TO CONTROL NOX EMISSIONS. THE BURNER TECHNOLOGY INSTALLED WILL USE THE FUEL GAS MOMENTUM TO INSPIRATE HOT FLUE | 18.75 | LB/H |  |  | 65.7 | T/YR |  | 0.075 | LB/MMBTU
TX-0475 | FORMOSA POINT COMFORT PLANT | FORMOSA PLASTICS CORPORATION TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-09 | 2005 |  | REBOILER (1 AND 2) | 12.39 | FUEL GAS | 250 | MMBtu |  |  | Nitrogen Oxides (NOx) | B | THE PYROLYSIS FURNACES WILL USE INTERNAL FLUE GAS RECIRCULATION (IFGR) AND STAGED FUEL GAS ULTRA LOW-NOX BURNERS TO CONTROL NOX EMISSIONS. THE BURNER TECHNOLOGY INSTALLED WILL USE THE FUEL GAS MOMENTUM TO INSPIRATE HOT FLUE | 1.82 | LB/H |  |  | 7.97 | T/YR |  | 0.00728 | LB/MMBTU
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-07-27 | 2005 | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | BOILERS C & D (U-3 & U-4) | 12.39 |  | 250 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 0.012 | LB/MMBTU |  | OPERATING PERMIT |  |  |  | 0.012 | LB/MMBTU | 24-HR ROLLING AVG BASED ON A 1-HR AVG
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-07-27 | 2005 | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | BOILERS A & B (U-1 & U-2) | 12.39 |  | 250 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 0.04 | LB/MMBTU | 24-HR ROLLING AVG BASED ON A 1-HR AVG | OPERATING PERMIT |  |  |  | 0.04 | LB/MMBTU
IA-0079 | KOCH NITROGEN COMPANY | KOCH NITROGEN COMPANY | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2005-09-08 | 2005 | AMMONIA AND UREA PRODUCTION FACILITY | NATURAL GAS FIRED BOILER | 12.3 | NATURAL GAS | 240 | MMBTU/H | BOILER SUPPLIES HEAT FOR AMMONIA REFORING PROCESS |  | Nitrogen Oxides (NOx) | P | LOW-NOX BURNERS AND FLUE GAS RECIRCULATION | 0.06 | LB/MMBTU | ONE HOUR | SIP |  |  |  | 0.6 | LB/MMBTU
NC-0101 | FORSYTH ENERGY PLANT | FORSYTH ENERGY PROJECTS, LLC | NC | FORSYTH COUNTY ENV AFFAIRS DEPT, NC | 2005-09-29 | 2005 | THREE COMBINED-CYCLE COMBUSTION TURBINE GENERATORS, EACH WITH A HEAT RECOVERY STEAM GENERATORS (HRSG) ALONG WITH NATURAL GAS-FIRED DUCT BURNERS TO MEET PEAK DEMAND. THE STEAM GENERATED THROUGH THE THREE HRSGS WILL DRIVE A STEAM TURBINE. THE ENTIRE PLANT WILL BE CAPABLE OF GENERATING A NOMINAL POWER OUTPUT OF 812 MEGAWATTS. | AUXILLIARY BOILER | 12.31 | NATURAL GAS | 110.2 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | P | LOW-NOX BURNERS, GOOD COMBUSTION CONTROL AND CLEAN BURNING, LOW-SULFUR FUEL (NATURAL GAS). | 15.13 | LB/H | based on 3-hour average |  |  |  |  | 0.137 | LB/MMBTU | calculated
MN-0062 | HEARTLAND CORN PRODUCTS |  | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2005-12-22 | 2005 |  | BOILER | 12.31 | NATURAL GAS | 198 | MMBTU/H | INCLUDES 2 BOILERS |  | Nitrogen Oxides (NOx) | N |  | 0.04 | LB/MMBTU | [5 empty] | 0.04 | LB/MMBTU
*TX-0499 | SANDY CREEK ENERGY STATION | SANDY CREEK ENERGY ASSOCIATES | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-07-24 | 2006 | THE PROPOSED SCES IS A GRASSROOTS NEW, 860 MW GROSS (800 MW NET) ELECTRIC OUTPUT, PC BOILER STEAM ELECTRIC GENERATING FACILITY. THE MAXIMUM HEAT INPUT IS 8,185 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTU/HR). ONLY PRELIMINARY ENGINEERING DESIGN HAS BEEN COMPLETED AT THIS TIME AND THE PERMIT APPLICATION NET PLANT EFFICIENCY OF 10,231 BTU/KWHR (HEAT ENERGY INPUT DIVIDED BY NET ELECTRIC ENERGY OUTPUT) WILL NOT BE FINALIZED UNTIL PROJECT FUNDING IS COMPLETE. THE BOILER MAY BE DESIGNED AS A SUBCRITICAL STEAM PRESSURE UNIT, OR A MORE EFFICIENT, HIGHER PRESSURE, SUPERCRITICAL STEAM UNIT. THE ELECTRIC GENERATING PROCESS IS THE STANDARD RANKINE CLOSED CYCLE: BOILER FEEDWATER IS PUMPED, CONVERTED TO STEAM IN THE BOILER, PASSED THROUGH STEAM TURBINES WHICH TURN ELECTRIC GENERATORS, AND CONDENSED IN WATER-COOLED CONDENSERS TO AGAIN BECOME BOILER FEEDWATER. HEAT IS REMOVED FROM THE TURBINE CONDENSERS VIA A WET COOLING TOWER WHICH EVAPORATES TO THE ATMOSPHERE WATER OBTAINED FROM WACO’S MUNICIPAL WASTE WATER TREATMENT FACILITY. | AUXILLARY BOILER | 12.31 | NATURAL GAS | 175 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | N |  | 1.8 | LB/H | [5 empty] | 0.010286 | LB/MMBTU
*TX-0496 | INEOS CHOCOLATE BAYOU FACILITY | INEOS USA LLC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-08-29 | 2006 | THE NO. 1 AND NO. 2 OLEFINS UNITS USE PYROLYSIS FURNACES TO CRACK FEEDSTOCKS INTO LOW MOLECULAR WEIGHT HYDROCARBONS THAT CONTAIN OLEFINS. PRODUCTS ARE ETHYLENE, PROPYLENE, PYROLYSIS GASOLINE, CRUDE C4, FUEL OIL, AND HYDROGEN. FEED FOR THE OLEFINS CRACKING FURNACES IS EITHER GAS FEED (ETHANE-RICH OR PROPANE-RICH FEED) OR LIQUID FEED (REFINERY RAFFINATE AND DEBUTANIZED NATURAL GASOLINE (DNG). THE LIQUID FEEDSTOCKS ARE STORED PRIOR TO PROCESSING IN LARGE FLOATING-ROOF TANKS EQUIPPED WITH SECONDARY SEALS. ETHYLENE PRODUCT IS TRANSFERRED OFF-SITE BY PIPELINE. PROPYLENE IS SHIPPED VIA RAILCAR, BARGE, OR SENT TO AN EXISTING POLYPROPYLENE UNIT AT THE CHOCOLATE BAYOU PLANT FOR FURTHER PROCESSING. CRUDE C4 STOCK IS SENT TO THE BUTADIENE EXTRACTION UNIT (BEU) TO PRODUCE HIGH PURITY BUTADIENE WHICH IS SOLD. BUTADIENE PRODUCT IS SHIPPED OFF-SITE VIA RAILCAR OR BARGE. THE RAW PYROLYSIS GASOLINE IS FURTHER HYDROTREATED TO PYROLYSIS GASOLINE PRODUCT FOR SHIPMENT OFF SITE | FURNACE EMISSION CAPS | 12.39 |  |  |  | EMISSION CAPS FOR FURNACES ARE NOT CHANGED IN THIS PERMIT ACTION. SPECIAL CONDITION NO. 13 IS CHANGED TO CLARIFY BACT SHALL BE DEMONSTRATED FOR EACH NEW FURNACE (EQUIPPED WITH SCR) AND ALLOW EXCEPTION WHEN THE UNIT IS IN DECOKING. SPECIAL CONDITION NO. 51 IS CHANGED TO ALLOW BACT FOR OLD FURNACES TO BE DEMONSTRATED AT THE LEVELS WHEN THE FLEXIBLE PERMIT WAS ISSUED. COMBUSTION STAFF WAS CONSULTED AND CONCURRED WITH THE CHANGE. |  | Nitrogen Oxides (NOx) | N |  | 401.91 | LB/H |  |  | 1760.37 | T/YR
NV-0043 | LASCO BATHWARE | LASCO BATHWARE | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2006-10-25 | 2006 | A BATHWARE MANUFACTURING FACILITY | FUEL BURNING FOR THERMOSETTING | 12.31 | PROPANE | 6.3 | MMBTU/H | THERMOSETTING IS THE HEATING PROCESS TO HARDEN THE BATHROOM FIXTURES AFTER THEY ARE MOLDED INTO SHAPE. THERE ARE TWO HEATERS FOR EACH PRODUCTION LINE. ADDITIONALLY THERE ARE FIVE AIR HEATERS AT THE CURE TUNNEL. THE TOTAL HEAT INPUT CAPACITY FOR THE FUEL BURNING EQUIPMENT IS 27.56 MMBTU/HR. THE ANNUAL CONSUMPTION OF PROPANE FOR OPERATING THE FUEL BURNING EQUIPMENT IS LIMITED TO 662,645 GALLONS PER YEAR. MOST EMISSIONS COME FROM FUEL COMBUSTION, NOT FROM THE BATHROOM FIXTURES BEING HARDENED. THE EXHAUST OF THE HEATER DESIGNATED IN THE PERMIT AS A02 IS CHOSEN AS THE TYPICAL EMISSION UNIT FOR REPORTING THE PROCESS DATA. THIS HEATER IS SUBJECT TO THE LIMIT OF ANNUAL OPERATING TIME OF 2,200 HOURS PER YEAR. |  | Nitrogen Oxides (NOx) | N | N/A | 0.96 | LB/H |  | SIP | 1.06 | T/YR |  | 0.15238 | LB/MMBTU
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | A & B VACUUM TOWER HEATERS (3-08 & 4-08) | 12.39 | REFINERY FUEL GAS | 155.2 | MMBTU/H EA. |  |  | Nitrogen Oxides (NOx) | B | ULTRA LOW NOX BURNERS (ULNB) AND SELECTIVE CATALYTIC REDUCTION (SCR VOLUNTARY) |  |  |  | OPERATING PERMIT |  |  |  | 0.0125 | LB/MMBTU | ANNUAL AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | NAPHTHA HYDROTREATER STRIPPER REBOILER HEATER (6-08) & KHT STRIPPER REBOILER HEATER (10-08) | 12.39 | REFINERY FUEL GAS |  |  | 6-08: 138.4 MMBTU/H 10-08: 121.8 MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS (ULNB) WITHOUT AIR PREHEAT |  |  |  | OPERATING PERMIT |  |  |  | 0.03 | LB/MMBTU | ANNUAL AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | SATS GAS PLANT HOT OIL HEATER (14-08) | 12.39 | REFINERY FUEL GAS | 183.3 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS (ULNB) WITHOUT AIR PREHEAT |  |  |  | OPERATING PERMIT |  |  |  | 0.03 | LB/MMBTU | ANNUAL AVERAGE
*LA-0213 | ST. CHARLES REFINERY | VALERO REFINING - NEW ORLEANS, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2007-02-08 | 2007 | PETROLEUM REFINERY. PROJECT INVOLVES INCREASE IN CAPACITY FROM 220,000 TO 380,000 BARRELS PER DAY. | REBOILER 2005-18 & HEATERS F-15-02 (6-81), 2005-14, 2005-17, 2005-29, 2005-32, & 2005-37 | 12.39 | REFINERY FUEL GAS |  |  | 6-81: 135 MM BTU/HR 2005-14: 195 MM BTU/HR 2005-17: 159 MM BTU/HR 2005-18: 231 MM BTU/HR 2005-29: 195 MM BTU/HR 2005-32: 159 MM BTU/HR 2005-37: 173 MM BTU/HR SOURCES ALSO FIRE NATURAL GAS. |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 0.04 | LB/MMBTU | THREE 1-HOUR TEST AVERAGE | OPERATING PERMIT |  |  |  | 0.04 | LB/MMBTU
*MS-0086 | CHEVRON PRODUCTS COMPANY, PASCAGOULA REFINERY | CHEVRON PRODUCTS COMPANY | MS | MISSISSIPPI DEPT OF ENV QUALITY | 2007-05-08 | 2007 | PETROLEUM REFINERY AND PETROCHEMICALS | REFORMATE SPLITTER FURNACE | 12.39 | REFINERY FUEL GAS | 160 | MMBTU/H |  |  | Nitrogen Oxides (NOx) | P | ULTRA LOW-NOX BURNERS | 7.2 | LB/H | 3-HR ROLLING AVERAGE |  | 21.02 | T/YR | 12-MONTH ROLLING AVERAGE | 0.03 | LB/MMBTU | 12-MONTH ROLLING AVERAGE
*IA-0089 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-08-08 | 2007 | 170 MILLION GALLON PER ROLLING 12-MONTH PERIOD DRY MILL ETHANOL PLANT. THE PROCESS WILL USE GASIFICATION TECHNOLOGY TO PRODUCE SYNGAS AS THE SOURCE FOR ENERGY. WILL USE 60,714,286 BUSHELS OF CORN PER ROLLING 12-MONTH PERIOD PRODUCING EITHER 1.411 MILLION TONS OF WDGS OR 552,500 TONS OF DDGS PER ROLLING 12-MONTH PERIOD. THE GASIFICATION PROCESS COULD USE UP TO 298, 213 TONS OF COAL PER ROLLING 12-MONTH PERIOD. PROJECT NUMBER (PN) 06-672, 28 PERMITS ISSUED | THERMAL OXIDIZER FOR HRSG FROM DRYERS AND GASIFICATION - TWO SYSTEMS, S10 AND S11 (07-A-955P AND 07-A-956P) | 12.3 | SYNGAS | 250 | MM BTU / hr | THE THERMAL OXIDIZER IS 150 MM BTU / HR AND EACH DRYER (TWO TOTAL FOR THIS EMISSION POINT) IS 50 MM BTU / HR. |  | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS | 0.04 | LB/MMBTU | 30 DAY ROLLING AVERAGE, BACT | NSPS | 0.2 | LB/MMBTU | 30-DAY ROLLING AVERAGE, NSPS | 0.04 | LB/MMBTU
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Nitrogen Oxides (NOx) | A | SCR | 100 | PPMUD |  |  | 3.43 | LB/H |  |  |  |  | THIS COVERS NOX FOR THE NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Nitrogen Oxides (NOx) | N |  | 0.085 | LB/MMBTU |  |  | 0.51 | LB/H |  | 0.085 | LB/MMBTU |  | THIS COVERS NOX FOR THE 3 COIL DRUM FURNACES (LA24-LA26).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX AND LOW NOX BURNERS | 0.085 | LB/MMBTU |  |  | 14.37 | LB/H |  | 0.085 | LB/MMBTU |  | THIS COVERS NOX FOR THE NATURAL GAS-FIRED REHEAT FURNACE (LA 21).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Nitrogen Oxides (NOx) | P | UNLB WITH EGR | 0.11 | LB/MMBTU |  |  | 1.82 | LB/H |  | 0.11 | LB/MMBTU |  | THIS COVERS NOX FOR THE PLATE ANNEALING FURNACE (LA27).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS -FIRED ANNEALING FURNACE (LA43) (MULTIPLE EMISSION POINTS) | 12.31 | NATURAL GAS | 196.4 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X016: SULFURIC ACID PICKLING WITH CAUSTIC SCRUBBER (LA46) - RBLC PROCESS CODE - 81.290 PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Nitrogen Oxides (NOx) | P | UNLB WITH EGR | 0.06 | LB/MMBTU |  |  | 11.75 | LB/H |  | 0.06 | LB/MMBTU |  | THIS COVERS NOX FOR THE NATURAL GAS-FIRED ANNEALING FURNACE (LA43).
*NM-0050 | ARTESIA REFINERY | NAVAJO REFINING COMPANY LLC | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2007-12-14 | 2007 | 115,000 - 125,000 BBL/DAY NOMINALLY RATED PETROLEUM REFINERY. | ROSE 2 HOT OIL HEATER | 12.3 | REFINERY FUEL GAS | 120 | mmbtu/hr |  |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 0.03 | LB/MMBTU | 3-HOUR ROLLING AVERAGE @ 3% O2 |  |  |  |  | 0.03 | LB/MMBTU
AL-0096 | MEAD COATED BOARD, INC. | MEAD COATED BOARD, INC. | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-03-12 | 1997 |  | DUCT BURNER, NAT GAS | 12.31 | NATURAL GAS | 170 | MMBTU/H | A SEPARATELY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING FUEL OIL. |  | Particulate Matter (PM) | P | EFFICIENT OPERATION OF THE COMBUSTION TURBINE. | 0.01 | LB/MMBTU |  |  | 2.1 | LB/H |  | 0.01 | LB/MMBTU | NOT AVAILABLE
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, NAT GAS | 12.31 | NATURAL GAS | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Particulate Matter (PM) | A |  | 0.01 | LB/MMBTU |  |  | 1.9 | LB/H |  | 0.01 | LB/MMBTU
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, HYDROGEN | 12.39 | HYDROGEN | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Particulate Matter (PM) | A |  | 0.01 | LB/MMBTU |  |  | 1.9 | LB/H |  | 0.01 | LB/MMBTU
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, COMBINED FUEL (NAT GAS/HYDROGEN) | 12.39 | NAT GAS/HYDRO COMBO | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Particulate Matter (PM) | A |  | 0.01 | LB/MMBTU |  |  | 1.9 | LB/H |  | 0.01 | LB/MMBTU
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | DUCT BURNER | 12.39 | NAT GAS/HYDROGEN | 260 | MMBTU/H |  |  | Particulate Matter (PM) | P | GOOD COMBUSTION PRACTICES | 0.02 | LB/MMBTU |  |  | 2.9 | LB/H |  | 0.02 | LB/MMBTU
SC-0075 | NUCOR STEEL- DARLINGTON COUNTY | NUCOR STEEL CORPORATION | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 1998-01-08 | 1998 | STEEL MILL | REHEAT FURNACE #1 | 12.31 | NATURAL GAS | 140 | MMBTU/H | MAIN FUEL IS NATURAL GAS, PROPANE AS A BACK-UP. UTILIZES LOW NOX BURNERS. NATURAL GAS AND PROPANE USAGE IS RESTRICTED TO AN EQUIVALENT OF 1150 X MMSCF PER YEAR AT ESTABLISHED BTU CONTENTS OF 1000 BTU/CF AND 90500 BTU/GALLON RESPECTIVELY. SUBJECT TO PSD. |  | Particulate Matter (PM) | N |  | 2 | LB/H |  |  | 8.8 | T/YR |  | 0.01 | LB/MMBTU
SC-0075 | NUCOR STEEL- DARLINGTON COUNTY | NUCOR STEEL CORPORATION | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 1998-01-08 | 1998 | STEEL MILL | REHEAT FURNACE #2 | 12.31 | NATURAL GAS | 125 | MMBTU/H | NATURAL GAS IS MAIN FUEL, PROPANE AS BACK UP. UTILIZES LOW NOX BURNERS AND EXTERNAL FLUE GAS RECIRCULATION. NATURAL GAS AND PROPANE USAGE IS RESTRICTED TO AN EQUIVALENT OF 1095 MMSCF PER YEAR AS ESTABLISHED BTU CONTENTS OF 1000 BTU/CF AND 90500 BTU/GAL RESPECTIVELY. SUBJECT TO PSD. |  | Particulate Matter (PM) | N | NONE INDICATED | 1.9 | LB/H |  |  | 8.3 | T/YR |  | 0.01 | LB/MMBTU
TX-0259 | FREEPORT COGENERATION FACILITY | BASF CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-06-26 | 1998 | CONSTRUCTION OF A COGENERATION UNIT | BOILER, B-20A | 12.39 | H2 WASTE & NAT GAS | 213 | MMBTU/H | HYDROGEN WASTE GAS AND PIPELINE QUALITY, SWEET NAT GAS CONTAINING NO >0.25 GR H2S AND 5 GR TOTAL S/100 DSCF. SCC CODE FOR NATURAL GAS CHOSEN FOR THE PURPOSE OF THIS DATABASE. |  | Particulate Matter (PM) | P | USE OF GOOD COMBUSTION. | 0.11 | LB/H |  | NSPS | 0.48 | T/YR |  | 0.0005 | LB/MMBTU | CALCULATED | EMISSION LIMIT IN STANDARDIZED UNITS CALCULATED FROM THE HOURLY EMISSION LIMIT AND THE THROUGHPUT.
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | 1998 | VEGETABLE OIL PLANT | BOILER, TRANE MURRAY, NAT GAS | 12.31 | NATURAL GAS | 189 | MMBTU/H | No add-on controls. See separate process for backup fuel (No. 2 oil) requirements. |  | Particulate Matter (PM) | N |  | 0.014 | LB/MMBTU | [5 empty] | 0.014 | LB/MMBTU
MN-0035 | LSP - COTTAGE GROVE, L.P. | LSP - COTTAGE GROVE, L.P. | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 1998-11-10 | 1998 |  | BOILERS, AUXILIARY, 2, NAT GAS | 12.31 | NATURAL GAS | 114 | MMBTU/H (NAT GAS) | A SEPARETLY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING FUEL OIL. |  | Particulate Matter (PM) | P | LOW NOX BURNER. EACH BURNER HAS A NOX PREDICTIVE EMISSION MONITORING SYSTEM. | 0.005 | LB/MMBTU | [5 empty] | 0.005 | LB/MMBTU
AL-0128 | ALABAMA POWER COMPANY - THEODORE COGENERATION | ALABAMA POWER COMPANY - THEODORE COGENERATION | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1999-03-16 | 1999 |  | BOILER | 12.31 | NATURAL GAS | 220 | MMBTU/H |  |  | Particulate Matter (PM) | P | COMBUSTION OF NATURAL GAS ONLY | 0.008 | LB/MMBTU |  |  | 1.7 | LB/H |  | 0.008 | LB/MMBTU
LA-0119 | LAKE CHARLES REFINERY | CONOCO INC. | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1999-08-12 | 1999 | PERMIT TO IMPLEMENT THE PETROZUATA SYNCRUDE PROJECT, ALLOWING REFINERY TO PROCESS A MIXTURE OF VIRGIN CRUDE AND CUTTER STOCK. SECURES A GUARANTEED CRUDE SUPPLY AND INCREASE PRODUCTION OF HEAVY PRODUCTS. MODIFICATION TO VARIOUS PROCESS UNITS WILL BE REQUIRED TO ENABLE THE FACILITY TO PROCESS THE INCREASED SULFUR LOAD ASSOCIATED WITH REFINING THE SYNCRUDE. CONOCO WILL REMOVE AN EXISTING HEATER, CONSTRUCT A NEW HEATER, AND MODIFY EQUIPMENT AND/OR INCREASE CAPACITIES OF THE FOLLOWING PROCESS UNITS: NOS. 3 AND 4 CRUDE TOPPING UNITS; NOS. 2 AND 3 CRUDE VACUUM UNITS; NOS. 4 AND 7 HYDRODESULFURIZATION UNITS; FRACTIONATOR; NOS. 4 AND 5 HYDROGEN SYSTEMS; HYDROGEN PURIFICATION AND DISTRIBUTION; NOS. 1, 2, 3, AND 5 SOUR WATER STRIPPERS; NO. 4 SULFUR RECOVERY UNIT; MARINE TANK FARM; MARINE DOCK; TANK FARM; AND Y-5 COOLING TOWER. | HEATER, CRUDE VACUUM UNIT FEED (H-20002) | 12.39 | NATURAL GAS | 150 | MMBTU/H | HEATER BURNS NATURAL GAS AND REFINERY OFF GAS. |  | Particulate Matter (PM) | P | GOOD COMBUSTION PRACTICES, USE CLEAN GASEOUS FUEL | 1.1 | LB/H | HOURLY MAXIMUM | OPERATING PERMIT | 5 | T/YR | ANNUAL MAXIMUM | 0.0073333 | LB/MMBTU
LA-0119 | LAKE CHARLES REFINERY | CONOCO INC. | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1999-08-12 | 1999 | PERMIT TO IMPLEMENT THE PETROZUATA SYNCRUDE PROJECT, ALLOWING REFINERY TO PROCESS A MIXTURE OF VIRGIN CRUDE AND CUTTER STOCK. SECURES A GUARANTEED CRUDE SUPPLY AND INCREASE PRODUCTION OF HEAVY PRODUCTS. MODIFICATION TO VARIOUS PROCESS UNITS WILL BE REQUIRED TO ENABLE THE FACILITY TO PROCESS THE INCREASED SULFUR LOAD ASSOCIATED WITH REFINING THE SYNCRUDE. CONOCO WILL REMOVE AN EXISTING HEATER, CONSTRUCT A NEW HEATER, AND MODIFY EQUIPMENT AND/OR INCREASE CAPACITIES OF THE FOLLOWING PROCESS UNITS: NOS. 3 AND 4 CRUDE TOPPING UNITS; NOS. 2 AND 3 CRUDE VACUUM UNITS; NOS. 4 AND 7 HYDRODESULFURIZATION UNITS; FRACTIONATOR; NOS. 4 AND 5 HYDROGEN SYSTEMS; HYDROGEN PURIFICATION AND DISTRIBUTION; NOS. 1, 2, 3, AND 5 SOUR WATER STRIPPERS; NO. 4 SULFUR RECOVERY UNIT; MARINE TANK FARM; MARINE DOCK; TANK FARM; AND Y-5 COOLING TOWER. | HEATER, NO. 4 CTU (H-4050) | 12.39 | NATURAL GAS | 237 | MMBTU/H | UNIT BURNS NATURAL GAS AND REFINERY OFF GAS. FORMERLY IDENTIFIED AS H-40001 |  | Particulate Matter (PM) | P | GOOD COMBUSTION PRACTICES, USE CLEAN GASEOUS FUELS | 1.8 | LB/H | HOURLY MAXIMUM | OPERATING PERMIT | 7.9 | T/YR | ANNUAL MAXIMUM | 0.008 | LB/MMBTU | CALCULATED BY CATC
AK-0037 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFIDE CONTENT TO 0.01% FROM 0.001%, AN INCREASE IN OPERATING HOURS OF P708C FROM 200 TO 600 HOURS PER YEAR, THE REMOVAL OF PERCENT EFFICIENCY REQUIREMENTS FOR AS1310 AND 1320, AND USE OF THERMAL OXIDATION TO CONTROL EMISSIONS FROM AS1320. | CRUDE HEATER, H101A | 12.39 | NATURAL GAS* | 140 | MMBTU/H | INSTALLED PRIOR TO 1975, THEREFORE NOT REQUIRED TO COMPLY WITH THE PSD PROGRAM. DESIGN CAPACITY OF 140.0 MMBTU/H AUTHORIZED RATED CAPACITY IS 1 MMBTU/H. *FUELS ARE NATURAL GAS, REFINERY GAS AND LPG. NO INDICATION IS PROVIDED AS TO WHICH IS THE PRIMARY FUEL. |  | Particulate Matter (PM) | N | NONE INDICATED | 0.005 | LB/MMBTU |  | SIP |  |  |  | 0.005 | LB/MMBTU |  | SOURCE IS SUBJECT TO STATE EMISSION LIMITS FOR PM. ESTIMATED EMISSIONS ARE 3.07 T/YR, BUT THIS IS NOT AN EMISSION LIMIT.
AK-0037 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFIDE CONTENT TO 0.01% FROM 0.001%, AN INCREASE IN OPERATING HOURS OF P708C FROM 200 TO 600 HOURS PER YEAR, THE REMOVAL OF PERCENT EFFICIENCY REQUIREMENTS FOR AS1310 AND 1320, AND USE OF THERMAL OXIDATION TO CONTROL EMISSIONS FROM AS1320. | CRUDE HEATER, H101B | 12.39 | NATURAL GAS* | 165 | MMBTU/H | DESIGN CAPACITY IS 165.0 MMBTU/H BUT AUTHORIZED RATED CAPACITY IS 1 MMBTU/H. *SOURCE BURNS COMBINATION OF REFINERY GAS, NATURAL GAS, AND LIQUID PETROLEUM GAS. IT IS NOT SPECIFIIED WHICH TYPE OF FUEL IS PRIMARY. |  | Particulate Matter (PM) | N | NONE INDICATED. | 0.005 | LB/MMBTU |  | SIP |  |  |  | 0.005 | LB/MMBTU |  | ESTIMATED EMISSIONS ARE 3.61 T/YR BUT THIS IS NOT A LIMIT. SUBJECT TO PM LIMITS BY THE STATE OF ALASKA.
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | 2001 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORIZED FIRING RATE WILL BE 481 MMBTU/H ON A ROLLING 12 MONTH AVERAGE, AND 502 MMBTU/H MAXIMUM HOURLY FIRING RATE. THE ADDITION OF THE NEW FURNACE TRIGGERED PSD REVIEW. | FURNACE HF-01 | 12.39 | ETHANE | 238 | MMBTU/H | 200 MMBTU/H AVE. FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% THEANE/PROPANE MIXTURE. |  | Particulate Matter (PM) | N | NONE INDICATED | 0.73 | LB/H |  |  | 2.8 | T/YR |  | 0.003 | LB/MMBTU | CALCULATED USING MAX THROUGHPUT
IN-0085 | PSEG LAWRENCEBURG ENERGY FACILITY | PSEG LAWRENCEBURG ENERGY FACILITY | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-06-07 | 2001 |  | AUXILIARY BOILER, NATURAL GAS | 12.31 | NATURAL GAS | 124.6 | MMBTU/H | AUXILIARY BOILER IS LIMITED TO 1000 H/YR OF OPERATION |  | Particulate Matter (PM) | P | GOOD COMBUSTION | 0.928 | LB/H | [5 empty] | 0.007 | LB/MMBTU
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | 2001 | ELECTRICITY GENERATION | AUXILIARY BOILER | 12.31 | NATURAL GAS | 120 | MMBTU/H |  |  | Particulate Matter (PM) | P | GOOD COMBUSTION PRACTICES | 0.792 | LB/H |  |  | 1.426 | T/YR |  | 0.0066 | LB/MMBTU
FL-0251 | OKEELANTA CORPORATION SUGAR MILL | NEW HOPE POWER PARTNERSHIP | FL | FLORIDA DEPT. OF ENVIRONMENTLA PROTECTION | 2001-10-29 | 2001 | SUGAR MILL | BOILER, NATURAL GAS | 12.31 | NATURAL GAS | 211 | MMBTU/H | State SIP rule requires a BACT for SO2 and PM emissions regardless of increase. The efficient combustion of clean fuels will minimize emissions of CO, PM/PM10, SO2, and VOC. The installation of low NOx burners with flue gas recirculation will reduce NOx emissions. |  | Particulate Matter (PM) | P | FUEL SPECIFICATIONS | [9 empty] | see note | BACT is use of pipeline natural gas. Emissions factor, lb/MMBtu: 0.002
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BOILER NO. 12 | 12.39 |  | 245 | MMBTU/H | EMISSION PT NO: BOILER-12. SHALL BE SHUTDOWN. |  | Particulate Matter (PM) | P | LOW S FUEL: FUEL GAS WITH H2S CONTENT NO MORE THAN 0.1 GR/DSCF OVER A 3 H ROLLING BASIS, OR NATURAL GAS WITH H2S CONTENT NO MORE THAN 0.25 GR/100 DSCF AND TOTAL S CONTENT NO MORE THAN 5.0 GR/ 100 DSCF. | 1.83 | LB/H |  |  | 8 | T/YR |  | 0.007 | LB/MMBTU | CALCULATED
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BTU-NO. 1 REACTOR FEED HEATER | 12.39 |  | 121.74 | MMBTU/H | EMISSION POINT NO. BTU-HF103. |  | Particulate Matter (PM) | P | LOW S FUEL: FUEL GAS WITH H2S CONTENT NO MORE THAN 0.1 GR/DSCF OVER A 3 H ROLLING BASIS, OR NATURAL GAS WITH H2S CONTENT NO MORE THAN 0.25 GR/100 DSCF AND TOTAL S CONTENT NO MORE THAN 5.0 GR/ 100 DSCF. | 1.56 | LB/H | SEE NOTES |  | 6.8 | T/YR | SEE NOTES | 0.013 | LB/MMBTU | CALCULATED FROM FINAL HOURLY EMISS LIMIT | ADDITONAL EMISSION LIMITS PRIOR TO INSTALLATION OF SCR: 0.91 LB/H AND 3.97 T/YR.
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ISOM II WEST REACTOR FEED HEATER | 12.39 |  | 104.25 | MMBTU/H | EMISSION POINT NO. BTU-HF106. |  | Particulate Matter (PM) | P | LOW S FUEL: FUEL GAS WITH H2S CONTENT NO MORE THAN 0.1 GR/DSCF OVER A 3 H ROLLING BASIS, OR NATURAL GAS WITH H2S CONTENT NO MORE THAN 0.25 GR/100 DSCF AND TOTAL S CONTENT NO MORE THAN 5.0 GR/ 100 DSCF. | 1.33 | LB/H | SEE NOTES |  | 5.82 | T/YR | SEE NOTES | 0.013 | LB/MMBTU | CALCULATED | ADDITIONAL EMISSION LIMITS APPLICABLE PRIOR TO INSTALLATION OF SCR: 0.78 LB/H AND 3.40 T/YR.
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ORTHOXYLENE II HEATER | 12.39 |  | 226.42 | MMBTU/H | EMISSION POINT NO.: ORTHOII-H2. |  | Particulate Matter (PM) | P | LOW SULFUR CONTENT FUEL: USE REFINERY FUEL GAS WITH NO MORE THAN 0.1 GR/DSCF H2S OR USE NATURAL GAS WITH NO MORE THAN 0.25 GR/100 DSCF H2S AND NO MORE THAN 5.0 GR/100 DSCF TOTAL S. | 2.89 | LB/H | SEE NOTES |  | 12.65 | T/YR | SEE NOTES | 0.013 | LB/MMBTU | CALCULATED | ADDITIONAL EMISSION LIMITS APPLICABLE PRIOR TO THE INSTALLATION OF SCR: 1.69 LB/H AND 7.39 T/YR.
CA-1024 | AES HUNTINGTON BEACH | AES HUNTINGTON BEACH | CA | SOUTH COAST AQMD, CA | 2002-08-01 | 2002 |  | BOILER: >= 50 MMBTU/HR | 12.31 | NATURAL GAS | 225 | MW | EQUIP: ELECTRIC UTILITY BOILER, MFR: BABCOCK & WILCOX, TYPE: MULTI-WALL FIRED, MODEL: , FUNC EQUIP: USE IS CURRENTLY FOR PEAK POWER DEMAND PERIODS, FUEL_TYPE: , SCHEDULE: VARIABLE, H/D: 24, D/W: 5, W/Y: 20, NOTES: FACILITY APPLIED TO BRING THIS RETIRED BOILER BACK INTO SERVICE. FACILITY IS EXPERIENCING DIFFICULTY MEETING NOX AND AMMONIA LIMITS ON ONE- HOUR AVERAGING BASIS, AND DISTRICT IS CONSIDERING REQUEST FOR LONGER AVERAGING TIME. SOURCE TEST RESULTS: PPM@3%O2, GR/DSCF: 225 MW: NOX-3.5, CO-0.0, VOC- 4.2, NH3-3.1, PM-.001. 169 MW: NOX-4.2, NH3-1.6, PM-.002. 115MW: NOX-3.8, NH3-0.5. 90 MW: NOX-4.5, NH3-0.7, PM-.004 |  | Particulate Matter (PM) | N |  | 0.01 | GR/DSCF |  | N/A | [5 empty] | NOT AVAILABLE
GA-0103 | ELBA ISLAND, LNG TERMINAL | SOUTHERN LNG INC | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2003-02-17 | 2003 | LIQUEFIED NATURAL GAS (LNG) TERMINAL | LNG VAPORIZER, (3) | 12.31 | NATURAL GAS | 121.4 | MMBTU/H |  |  | Particulate Matter (PM) | N |  | 0.14 | LB/MMBTU | [5 empty] | 0.14 | LB/MMBTU |  | EMISSION LIMIT BASED ON STATE RULE 391-3-0-.02(2) (D)2
VA-0270 | VCU EAST PLANT | VIRGINIA COMMONWEALTH UNIVERSITY | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-31 | 2003 |  | BOILER NATUAL GAS | 12.31 | NATURAL GAS | 150 | MMBTU/H | This is one of 3 boilers |  | Particulate Matter (PM) | P | GOOD COMBUSTION PRACTICES. | 1.2 | LB/H | each unit |  |  |  |  | 0.01 | LB/MMBTU
WI-0204 | UWGP - FUEL GRADE ETHANOL PLANT | UNITED WISCONSIN GRAIN PRODUCERS | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2003-08-14 | 2003 | FERMENTATION BASED PROCESS WITH DISTILLATION, MOLECULAR SIEVES FOR FINAL WATER REMOVAL. ETHANOL DENATURED USING GASOLINE. | BOILER /OXIDIZER ( DRYER / DISTILLATION), P10 | 12.31 | NATURAL GAS | 140 | MMBTU/H | Boiler works as control device. RECEIVES VOC'S FROM DISTILLATION AND RELATED PROCESSES AND FROM Distillers dried grain with solubles (DDGS) DRYER (85 MMBTU/HR.). SUBJECT TO DB |  | Particulate Matter (PM) | N |  | 5.5 | LB/H |  |  | 0.3 | LB/T | TON DDGS AT 11% MOISTURE | 0.04 | LB/MMBTU | calculated | SYNTHETIC MINOR SOURCE. BOILER / OXIDIZER CONSUMES COMBUSTABLE PARTICULATE MATTER WHICH ESCAPES DDGS DRYER.
WV-0023 | MAIDSVILLE | LONGVIEW POWER, LLC | WV | WEST VIRGINIA AIR POLLUTION CONTROL COMM | 2004-03-02 | 2004 | PULVERIZED COAL-FIRED STEAM GENERATOR CAPABLE OF GENERATING 600MW OF ELECTRIC POWER. THIS FACILITY IS A GREEN FIELD SITE, WHICH INCLUDES A 6,114 MMBTU COAL-FIRED BOILER, 225 MMBTU NATURAL GAS-FIRED AUX BOILER, EMERGENCY GENERATOR, FIRE WATER PUMP ENGINE, COOLING TOWERS, AND MATERIAL HANDLING SYSTEMS. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 225 | mmbtu/h | LIMITED TO NATURAL GAS USE AND 3,000 HOURS OF OPERATION PER YEAR |  | Particulate Matter (PM) | P | GOOD COMBUSTION PRACTICES AND THE USE OF CLEAN FUELS | 0.0022 | LB/MMBTU | 6 HOUR ROLLING AVERAGE | SIP |  |  |  | 0.0022 | LB/MMBTU | 6 HOUR ROLLING AVERAGE | LIMITED TO NATURAL GAS USE AND 3000 HOURS OF OPERATION
*TX-0499 | SANDY CREEK ENERGY STATION | SANDY CREEK ENERGY ASSOCIATES | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-07-24 | 2006 | THE PROPOSED SCES IS A GRASSROOTS NEW, 860 MW GROSS (800 MW NET) ELECTRIC OUTPUT, PC BOILER STEAM ELECTRIC GENERATING FACILITY. THE MAXIMUM HEAT INPUT IS 8,185 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTU/HR). ONLY PRELIMINARY ENGINEERING DESIGN HAS BEEN COMPLETED AT THIS TIME AND THE PERMIT APPLICATION NET PLANT EFFICIENCY OF 10,231 BTU/KWHR (HEAT ENERGY INPUT DIVIDED BY NET ELECTRIC ENERGY OUTPUT) WILL NOT BE FINALIZED UNTIL PROJECT FUNDING IS COMPLETE. THE BOILER MAY BE DESIGNED AS A SUBCRITICAL STEAM PRESSURE UNIT, OR A MORE EFFICIENT, HIGHER PRESSURE, SUPERCRITICAL STEAM UNIT. THE ELECTRIC GENERATING PROCESS IS THE STANDARD RANKINE CLOSED CYCLE: BOILER FEEDWATER IS PUMPED, CONVERTED TO STEAM IN THE BOILER, PASSED THROUGH STEAM TURBINES WHICH TURN ELECTRIC GENERATORS, AND CONDENSED IN WATER-COOLED CONDENSERS TO AGAIN BECOME BOILER FEEDWATER. HEAT IS REMOVED FROM THE TURBINE CONDENSERS VIA A WET COOLING TOWER WHICH EVAPORATES TO THE ATMOSPHERE WATER OBTAINED FROM WACO’S MUNICIPAL WASTE WATER TREATMENT FACILITY. | AUXILLARY BOILER | 12.31 | NATURAL GAS | 175 | MMBTU/H |  |  | Particulate Matter (PM) | N |  | 0.88 | LB/H
*IA-0089 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-08-08 | 2007 | 170 MILLION GALLON PER ROLLING 12-MONTH PERIOD DRY MILL ETHANOL PLANT. THE PROCESS WILL USE GASIFICATION TECHNOLOGY TO PRODUCE SYNGAS AS THE SOURCE FOR ENERGY. WILL USE 60,714,286 BUSHELS OF CORN PER ROLLING 12-MONTH PERIOD PRODUCING EITHER 1.411 MILLION TONS OF WDGS OR 552,500 TONS OF DDGS PER ROLLING 12-MONTH PERIOD. THE GASIFICATION PROCESS COULD USE UP TO 298, 213 TONS OF COAL PER ROLLING 12-MONTH PERIOD. PROJECT NUMBER (PN) 06-672, 28 PERMITS ISSUED | THERMAL OXIDIZER FOR HRSG FROM DRYERS AND GASIFICATION - TWO SYSTEMS, S10 AND S11 (07-A-955P AND 07-A-956P) | 12.3 | SYNGAS | 250 | MM BTU / hr | THE THERMAL OXIDIZER IS 150 MM BTU / HR AND EACH DRYER (TWO TOTAL FOR THIS EMISSION POINT) IS 50 MM BTU / HR. |  | Particulate Matter (PM) | N |  | 0.01 | LB/MMBTU | BACT | OTHER | 0.03 | LB/MMBTU | SUBPART DB | 0.1 | GR/DSCF | 23.3(2)
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS -FIRED ANNEALING FURNACE (LA43) (MULTIPLE EMISSION POINTS) | 12.31 | NATURAL GAS | 196.4 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X016: SULFURIC ACID PICKLING WITH CAUSTIC SCRUBBER (LA46) - RBLC PROCESS CODE - 81.290 PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Particulate Matter (PM) | A | SCRUBBER | 0.005 | GR/DSCF |  |  | 0.18 | LB/H |  |  |  |  | THIS COVERS PM FOR THE SULFURIC ACID PICKLING WITH CAUSTIC SCRUBBER (LA46).
IA-0057 | CARGILL, INC | CARGILL, INC | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-02-24 | 1997 | CORN PROCESSING PLANT | BOILER #5 | 12.31 | NATURAL GAS | 182 | MMBTU/H | PERMIT NUMBER: 92-A-227-S3. NO LIMITS FOR CO, SO2, OR VOC IN PERMIT. |  | Particulate Matter < 10 μ (PM10) | A | BASIS OF LIMIT, OTHER NAAQS. STANDARD EMISSION LIMIT ESTIMATED FROM PERMIT PROCESS DATA. | 1.82 | LB/H | [5 empty] | 0.01 | LB/MMBTU
IA-0057 | CARGILL, INC | CARGILL, INC | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-02-24 | 1997 | CORN PROCESSING PLANT | BOILER #6 | 12.31 | NATURAL GAS | 182 | MMBTU/H | PERMIT NUMBER: 92-A-228-S3. LIMITS FOR CO, SO2, OR VOC ARE NOT INCLUDED IN THE PERMIT. |  | Particulate Matter < 10 μ (PM10) | A | BASIS OF LIMIT - OTHER NAAQS | 1.82 | LB/H | [5 empty] | 0.01 | LB/MMBTU
IA-0057 | CARGILL, INC | CARGILL, INC | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-02-24 | 1997 | CORN PROCESSING PLANT | BOILER #4 | 12.31 | NATURAL GAS | 230 | MMBTU/H | PERMIT NUMBER: 89-A-210-S2. NO LIMITS FOR CO, SO2, OR VOC IN PERMIT. |  | Particulate Matter < 10 μ (PM10) | P | BASIS FOR LIMIT : OTHER - NAAQS. STANDARD EMISSION LIMIT ESTIMATED FROM PERMIT PROCESS DATA. | 2.3 | LB/H | [5 empty] | 0.01 | LB/MMBTU
IN-0075 | GRAIN PROCESSING CORP. | GRAIN PROCESSING CORP. | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1997-06-10 | 1997 |  | BOILERS NO. 1 & 2 | 12.39 | NATURAL GAS/ALCOHOL | 244 | MMBTU/H (EACH) | STACK TEST REQUIRED BY PERMIT, NOT YET CONSTRUCTED. BOILER NO.1 (UP51A), BOILER NO.2 (UP51B). |  | Particulate Matter < 10 μ (PM10) | N |  | 5 | LB/MMCF NG |  |  | 2.44 | LB/H EACH |  |  |  | NOT AVAILABLE
NJ-0041 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-10-08 | 1997 |  | DUCT BURNER ONLY | 12.31 | NATURAL GAS | 234 | MMBTU/H | TOTAL NATURAL GAS BURNED IN THE HEAT RECOVERY BOILER SHALL NOT EXCEED 1153.2 MILLION CUBIC FEET PER CALENDAR YEAR |  | Particulate Matter < 10 μ (PM10) | P | LOW NOX BURNER | 5.2 | LB/H |  |  | 0.022 | LB/MMBTU |  | 0.022 | LB/MMBTU
LA-0114 | ST. JAMES STYRENE PLANT | CHEVRON CHEMICAL COMPANY | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1997-12-10 | 1997 | MODIFICATION TO THE EXISTING STYRENE PRODUCTION FACILITY | SUPERHEATER | 12.31 | NATURAL GAS | 165 | MMBTU/H |  |  | Particulate Matter < 10 μ (PM10) | P | GOOD DESIGN AND OPERATION | 0.005 | LB/MMBTU | [5 empty] | 0.005 | LB/MMBTU
MO-0051 | PROCTOR & GAMBLE PAPER PRODUCTS | Proctor & Gamble Paper Products | MO | MISSOURI DNR, AIR POLL CONTROL PROGRAM | 1998-01-01 | 1998 | SANITARY TISSUE & TOWEL BUSINESS, EXPANSION TO EXISTING DIAPER MANUFACTURING PLANT | BOILERS, NATURAL GAS, (3) | 12.31 | NATURAL GAS | 1095 | MMCF/YR | ADDITIONAL THROUGHPUT INFORMATION: 125 MMBTU/H, EACH. |  | Particulate Matter < 10 μ (PM10) | P | LOW NOX NATURAL GAS-FIRED W/O FLUE GAS RECIRC., GOOD COMBUSTION | 0.007 | LB/MMBTU | [5 empty] | 0.007 | LB/MMBTU
MN-0035 | LSP - COTTAGE GROVE, L.P. | LSP - COTTAGE GROVE, L.P. | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 1998-11-10 | 1998 |  | BOILERS, AUXILIARY, 2, NAT GAS | 12.31 | NATURAL GAS | 114 | MMBTU/H (NAT GAS) | A SEPARETLY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING FUEL OIL. |  | Particulate Matter < 10 μ (PM10) | P | BOILERS BURN NATURAL GAS MOST OF THE TIME. BOILERS ARE LIMITED TO BURN DISTILLATE FUEL OIL UP TO 1700 H/YR. | 0.005 | LB/MMBTU | [5 empty] | 0.005 | LB/MMBTU
OH-0245 | REPUBLIC TECHNOLOGIES INTERNATIONAL | REPUBLIC TECHNOLOGIES INTERNATIONAL/CANTON | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 1999-01-27 | 1999 | STEEL MILL. THIS PLANT IS PSD FOR PM, SO2, NOX, CO, AND VOC. THIS MODIFICATION IS A SIGNIFICANT INCREASE FOR NOX. | BLOOM REHEAT FURNACE | 12.31 | NATURAL GAS | 196.2 | MMBTU/H | STACK TEST 0.0489 LB NOX/HR |  | Particulate Matter < 10 μ (PM10) | N |  | 1 | LB/H |  | SIP | 4.4 | T/YR |  | 0.005 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 4 (NAT GAS) | 12.31 | NATURAL GAS | 118 | MMBTU/H | MFR. IS BABCOCK & WILCOX. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Particulate Matter < 10 μ (PM10) | N | NONE LISTED | 10.2 | LB/H | [5 empty] | 0.0864 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 2 (NAT GAS) | 12.31 | NATURAL GAS | 134 | MMBTU/H | MFR. IS COMBUSTION ENGINEERING. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Particulate Matter < 10 μ (PM10) | N | NONE LISTED | 0.7 | LB/H |  |  | 0.005 | LB/MMBTU |  | 0.005 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 3 (NAT GAS) | 12.31 | NATURAL GAS | 152 | MMBTU/H | MFR. IS BABCOCK & WILCOX. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Particulate Matter < 10 μ (PM10) | N | NONE LISTED | 0.8 | LB/H | [5 empty] | 0.005 | LB/MMBTU
TX-0414 | ATOFINA PETROCHEMICALS PORT ARTHUR COMPLEX | FINA OIL & CHEMICAL COPMANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1999-04-22 | 1999 | FACILITY WANTS TO INSTALL A COGENERATION FACILITY CONSISTING OF 2 TURBINES AND SUPPLEMENTAL BOILER TO SUBSTITUTE FOR 2 AUXILIARY STEAM BOILERS | SUPPLEMENTAL BOILER | 12.31 | NATURAL GAS | 227 | MMBTU/H | BOILER PRODUCES AS MUCH AS 150,000 LB/H OF STEAM. |  | Particulate Matter < 10 μ (PM10) | P | LOW ASH FUEL | 1.59 | LB/H |  |  | 1.89 | T/YR |  | 0.007 | LB/MMBTU | CALCULATED
AR-0026 | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1999-05-05 | 1999 | COMBUSTION TURBINE COMBINED CYCLE COGENERATION FACILITY | DUCT BURNER | 12.31 | NATURAL GAS | 315 | MMBTU/H | TURBINE AND DUCT BURNER EMISSIONS COMBINED IN ONE STACK. DUCT BURNER ALWAYS FIRES NATURAL GAS. |  | Particulate Matter < 10 μ (PM10) | P | CLEAN FUEL | 0.008 | LB/MMBTU | [5 empty] | 0.008 | LB/MMBTU
AR-0026 | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1999-05-05 | 1999 | COMBUSTION TURBINE COMBINED CYCLE COGENERATION FACILITY | BOILER, NATURAL GAS | 12.31 | NATURAL GAS | 362 | MMBTU/H | BOILER FIRES NATURAL GAS AND FUEL OIL. BOILER WILL PROVIDE STEAM FOR STEAM TURBINE AND INTERNATIONAL PAPER MILL. |  | Particulate Matter < 10 μ (PM10) | P | CLEN FUELS AND GOOD COMBUSTION | 0.005 | LB/MMBTU | [5 empty] | 0.005 | LB/MMBTU
SC-0049 | SKYGEN | BROAD RIVER ENERGY, LLC | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 1999-12-02 | 1999 |  | THREE NATURAL GAS FIRED BOILERS (UTILITY) | 12.31 | NATURAL GAS | 230 | MMBTU/H | 1700 H/YR MAX OPERATION PER BOILER. |  | Particulate Matter < 10 μ (PM10) | P | LOW SULFUR FUELS (NG) WITH GOOD COMBUSTION PRACTICES | 0.005 | LB/MMBTU | [5 empty] | 0.005 | LB/MMBTU
TX-0395 | DIAMOND SHAMROCK MCKEE PLANT | DIAMOND SHAMROCK REFINING COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-05-23 | 2000 |  | NO. 1 REFORMER CHARGE HEATER | 12.39 | REFINERY GAS | 248 | MMBTU/H |  |  | Particulate Matter < 10 μ (PM10) | N |  | 2.64 | LB/H |  |  | 11.56 | T/YR
TX-0395 | DIAMOND SHAMROCK MCKEE PLANT | DIAMOND SHAMROCK REFINING COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-05-23 | 2000 |  | NO 1 INTERHEATER | 12.39 | REFINERY GAS | 147.2 | MMBTU/H |  |  | Particulate Matter < 10 μ (PM10) | N |  | 1.57 | LB/H |  |  | 6.86 | T/YR
OK-0045 | REDBUD POWER PLT | REDBUD ENERGY LP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-15 | 2001 | ELECTRICAL GENERATION FACILITY | BOILER, AUXILIARY | 12.31 | NATURAL GAS | 20 | MMBTU/H | boiler operates < 3000 hours per year |  | Particulate Matter < 10 μ (PM10) | P | USE OF LOW ASH FUEL, EFFICIENT COMBUSTION | 0.0074 | LB/MMBTU | [5 empty] | 0.0074 | LB/MMBTU
AR-0057 | TENASKA ARKANSAS PARTNERS, LP | TENASKA ARKANSAS PARTNERS, LP | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-10-09 | 2001 | ELECTRIC POWER GENERATING STATION. FACILITY WAS NEVER CONSTRUCTED AND THE PERMIT WAS VOIDED 1/07/03. ADDITIONAL PLANTWIDE EMISSIONS: PM10 858 T/YR, AMMONIA 844 T/YR. | BOILER, NATURAL GAS, (2) | 12.31 | NATURAL GAS | 122 | MMBTU/H | Throughput for each boiler. |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES. | 0.005 | LB/MMBTU | [5 empty] | 0.005 | LB/MMBTU
AR-0055 | NUCOR YAMATO STEEL (ARMOREL) | NUCOR YAMATO STEEL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-10-10 | 2001 | STEEL MILL. | REHEAT FURNACE | 12.31 | NATURAL GAS | 225 | MMBTU/H |  |  | Particulate Matter < 10 μ (PM10) | P | CLEAN FUEL | 0.0168 | LB/MMBTU | [5 empty] | 0.0168 | LB/MMBTU
TX-0386 | AMELLA ENERGY CENTER | CALPINE CONSTRUCTION FINANCE CO. LP | TX | CITY OF HOUSTON BUREAU AIR QUAL CTRL, TX | 2002-03-26 | 2002 |  | AUXILIARY BOILER | 12.31 | NATURAL GAS | 155 | MMBTU/H |  |  | Particulate Matter < 10 μ (PM10) | N |  | 3.23 | LB/H | [5 empty] | 0.02 | LB/MMBTU
NJ-0043 | LIBERTY GENERATING STATION | LIBERTY GENERATING STATION | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2002-03-28 | 2002 | ELECTRICITY GENERATION | AUXILIARY BOILER | 12.31 | NATURAL GAS | 200 | MMBTU/H | NATURAL GAS USAGE RESTRICTED TO 181.0 MILLION SCF/YR (EQUIVALENT TO A 10% ANNUAL CAPACITY FACTOR) |  | Particulate Matter < 10 μ (PM10) | N |  | 1.6 | LB/H | [5 empty] | 0.008 | LB/MMBTU |  | BASIS OF LIMIT IS STATE.
TN-0153 | WILLIAMS REFINING & MARKETING, L.L.C. | WILLIAMS REFINING & MARKETING, L.L.C. | TN | MEMPHIS AND SHELBY CO HEALTH DEPT, TN | 2002-04-03 | 2002 | PETROLEUM REFINERY | BOILER, NO. 10 | 12.31 | NATURAL GAS | 180 | MMBTU/H | annual capacity factor (ACF) for natural gas, coal or oil shall not exceed 10% |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0075 | LB/MMBTU | [5 empty] | 0.0075 | LB/MMBTU
LA-0121 | CONVENT REFINERY | MOTIVA ENTERPRISES LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-05-17 | 2002 | PERMIT IS TO MODIFY AN EXISTING FACILITY TO MANUFACTURE LOW SULFUR GASOLINE, BY INSTALLING A HYDRO- DESULFURIZATION UNIT (HDS-1) AND MODIFYING ITS SULFUR BLOCK AND H-OIL UNIT (VACUUM RESIDUUM UPGRADE UNIT). | HDS-1 HEATER | 12.39 | FUEL GAS | 140 | MMBTU/H | EMISSION POINT 96H-201 |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES | 1.04 | LB/H |  |  | 3.26 | T/YR |  | 0.02 | LB/MMBTU |  | EMISSION LIMIT IN STANDARDIZED UNITS APPLY WHILE BURNING REFINERY FUEL GAS.
AR-0070 | GENOVA ARKANSAS I, LLC | GENOVA ARKANSAS I, LLC | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-08-23 | 2002 | COMBINED CYCLE POWER PLANT | DUCT BURNERS | 12.31 | NATURAL GAS | 200 | MMBTU/H | 2 DUCT BURNERS UNDER ANY SCENARIO. INFORMATION PROVIDED IS FOR EACH UNIT. |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICE | 0.02 | LB/MMBTU | [5 empty] | 0.02 | LB/MMBTU
VA-0278 | VCU EAST PLANT | Virginia Commonwealth University | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-31 | 2003 | STEAM GENERATING PLANT AT UNIVERSITY | BOILER, NATURAL GAS, (3) | 12.31 | NATURAL GAS | 150.6 | MMBTU/H | Throughput for each. The 3 boilers shall consume no more than 3,500 million cf of natural gas per year |  | Particulate Matter < 10 μ (PM10) | N |  | 1.2 | LB/H | [5 empty] | 0.008 | LB/MMBTU | calculated
VA-0270 | VCU EAST PLANT | VIRGINIA COMMONWEALTH UNIVERSITY | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-31 | 2003 |  | BOILER NATUAL GAS | 12.31 | NATURAL GAS | 150 | MMBTU/H | This is one of 3 boilers |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES. | 1.2 | LB/H | each unit |  |  |  |  | 0.01 | LB/MMBTU
PA-0231 | UNITED REFINERY CO. | UNITED REFINERY CO | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2003-10-09 | 2003 | THE MODIFICATIONS INCLUDE THE INSTALLATION OF THREE NEW SOURCES AND MODS TO EXISTING SOURCES, THIS PERMIT ACTION IS SUBJECT TO SUBPARTS J,GGG QQQ OF THE NSPS, MACT SUBPARTS CC AND UUU AND NESHAPS SUBPARTS FF AND IS PSD FOR CO. | DELAYED COKER UNIT, HEATER | 12.39 | REFINERY GAS | 116 | MMBTU/H | The unit is subject to the NSPS 40 CFR Subpart J, Subpart GGG, Subpart QQQ. The unit is also subject to MACT standards in 40 CFR 63 Subpart CC, and NESHAP requirements in 40 CFR 61 Subpart FF. |  | Particulate Matter < 10 μ (PM10) | P | SPRAY CHAMBER, GOOD COMBUSTION PRACTICE | 0.1 | LB/H |  |  | 0.4 | T/YR |  | 0.0009 | LB/MMBTU | Calculated using heat input | Best available technology (BAT) review done.
WV-0023 | MAIDSVILLE | LONGVIEW POWER, LLC | WV | WEST VIRGINIA AIR POLLUTION CONTROL COMM | 2004-03-02 | 2004 | PULVERIZED COAL-FIRED STEAM GENERATOR CAPABLE OF GENERATING 600MW OF ELECTRIC POWER. THIS FACILITY IS A GREEN FIELD SITE, WHICH INCLUDES A 6,114 MMBTU COAL-FIRED BOILER, 225 MMBTU NATURAL GAS-FIRED AUX BOILER, EMERGENCY GENERATOR, FIRE WATER PUMP ENGINE, COOLING TOWERS, AND MATERIAL HANDLING SYSTEMS. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 225 | mmbtu/h | LIMITED TO NATURAL GAS USE AND 3,000 HOURS OF OPERATION PER YEAR |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES AND THE USE OF CLEAN FUELS | 0.0022 | LB/MMBTU | 6 HOUR ROLLING AVERAGE | SIP |  |  |  | 0.0022 | LB/MMBTU | 6 HOUR ROLLING AVERAGE | LIMITED TO NATURAL GAS USE AND 3000 HOURS OF OPERATION
OK-0098 | PONCA CITY REF | CONOCOPHILLIPS PONCA CITY REFINERY | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2004-03-31 | 2004 | CRUDE OIL REFINERY | CRUDE VACUUM UNIT, HEATER H-0016 | 12.39 | REFINERY FUEL GAS |  |  | Compliance to be verified by stack testing |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES | 0.8 | LB/H | 365 day average |  | 3.48 | T/YR |  | 0.0075 | LB/MMBTU
OK-0098 | PONCA CITY REF | CONOCOPHILLIPS PONCA CITY REFINERY | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2004-03-31 | 2004 | CRUDE OIL REFINERY | CRUDE CHARGE UNIT, HEATER H-0001 | 12.39 | REFINERY FUEL GAS |  |  | Compliance to be verified by stack testing, then monitored with CEM |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES | 1.31 | LB/H | 365 day average |  | 5.75 | T/YR |  | 0.0075 | LB/MMBTU
OH-0241 | MILLER BREWING COMPANY - TRENTON | MILLER BREWING COMPANY | OH | HAMILTON CO-SOUTHWESTERN OH APCA | 2004-05-27 | 2004 | BEER BREWING AND PACKAGING. | BOILER (2), NATURAL GAS | 12.31 | NATURAL GAS | 238 | MMBTU/H | TWO BOILERS, CAPABLE OF BURNING AND WITH LIMITS FOR COAL, NATURAL GAS, NUMBERS 2 AND 6 FUEL OILS. POUND PER HOUR LIMITS ARE FOR EACH BOILER; AND EXCEPT FOR VOC AND CO, ALL T/YR LIMITS ARE FOR BOTH BOILERS COMBINED. THESE LIMITS FOR THE NATURAL GAS. |  | Particulate Matter < 10 μ (PM10) | A | BAGHOUSE | 0.01 | GR/ACF |  | SIP | 122.9 | T/YR | BOTH BOILERS TOGETHER, PER ROLLING 12-MO | 0.02 | LB/MMBTU
MS-0069 | DUPONT DELISLE FACILITY | E. I. DUPONT DE NEMOURS | MS | MISSISSIPPI DEPT OF ENV QUALITY | 2004-06-08 | 2004 | TITANIUM DIOXIDE PRODUCTION. | BOILER #3 | 12.31 | NATURAL GAS | 231 | MMBTU/H | AF-103. RETROFITTED TO BURN LANDFILL GAS IN ADDITION TO NATURAL GAS. |  | Particulate Matter < 10 μ (PM10) | P | USE OF NATURAL GAS CONSIDERED BACT. | 1.76 | LB/H |  |  | 7.69 | T/YR |  | 0.0076 | LB/MMBTU
MS-0069 | DUPONT DELISLE FACILITY | E. I. DUPONT DE NEMOURS | MS | MISSISSIPPI DEPT OF ENV QUALITY | 2004-06-08 | 2004 | TITANIUM DIOXIDE PRODUCTION. | BOILER #4 | 12.31 | NATURAL GAS | 231 | MMBTU/H | MAY BURN LANDFILL GAS IN ADDITION TO NATURAL GAS. |  | Particulate Matter < 10 μ (PM10) | P | USE OF NATURAL GAS CONSIDERED BACT. | 1.76 | LB/H |  |  | 7.69 | T/YR |  | 0.0076 | LB/MMBTU
MS-0069 | DUPONT DELISLE FACILITY | E. I. DUPONT DE NEMOURS | MS | MISSISSIPPI DEPT OF ENV QUALITY | 2004-06-08 | 2004 | TITANIUM DIOXIDE PRODUCTION. | BOILER (RENTAL/TEMPORARY) | 12.31 | NATURAL GAS | 231 | MMBTU/H | AF-202. RENTAL BOILER MAY ONLY OPERATE 2,085 H/YR. |  | Particulate Matter < 10 μ (PM10) | P | USE OF NATURAL GAS CONSIDERED BACT. | 1.76 | LB/H |  |  | 1.83 | T/YR |  | 0.0076 | LB/MMBTU
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | AUXILLIARY NAT. GAS FIRED BOILER (B25, S25) | 12.31 | NATURAL GAS | 229.8 | MMBTU/H | THE AUXILIARY BOILER WILL BE USED TO PREHEAT STEAM TURBINE, PROVIDE PLANT HEATING AND PROVIDE SUPPLEMENTAL STEAM TO AUXILIARY EQUIPMENT WHEN THE MAIN SCPC BOILER IS OFFLINE. THE AUXILIARY BOILER WILL BE PACKAGED BOILER THAT WILL COMBUST ONLY NATURAL GAS. THE HOURS OF THE OPERATION OF THE AUXILIARY BOILER WILL BE LIMITED TO 2,000 HOURS IN ANY 12 CONSECUTIVE MONTHS. |  | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS ONLY, GOOD COMBUSTION PRACTICES | 0.0075 | LB/MMBTU | 2000 H / 12 MO. ROLLING | NSPS | 1.712 | LB/H |  |  |  |  | BOTH PM AND PM10 (INCLUDES BACKHALF M202 CATCH)
LA-0194 | SABINE PASS LNG IMPORT TERMINAL | SABINE PASS LNG, LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2004-11-24 | 2004 | LNG TO BE TRANSFERRED FROM MARINE VESSELS INTO PRESSURIZED TANKS FOR STORAGE, THEN REGASIFIED USING VAPORIZERS. THE VAPORIZED NATURAL GAS WILL BE MEASURED AND SENT TO TRANSMISSION PIPELINES. | SUBMERGED COMBUSTION VAPORIZERS (24) | 12.31 |  | 108 | MMBTU/H |  |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES AND THE USE OF NATURAL GAS AS FUEL | 0.15 | LB/H | HOURLY MAXIMUM | OPERATING PERMIT | 0.66 | T/YR | ANNUAL MAXIMUM | 0.0014 | LB/MM BTU
OR-0046 | TURNER ENERGY CENTER, LLC | CALPINE | OR | OREGON DEPT OF ENVIRONMENTAL QUALITY | 2005-01-06 | 2005 | 620 MW TOTAL COMBINED CYCLE GAS TURBINES (2 TURBINES WITH HRSGS) | AUXILIARY BOILER | 12.31 | NATURAL GAS | 417904 | MMBTU/YR | BOILER USED TO PROVIDE AUXILIARY STEAM FOR STANDBY AND STARTUP CONDITIONS WILL BE OPERATED A MAXIMUM OF 3000 HOURS/YR. |  | Particulate Matter < 10 μ (PM10) | N | USE OF NATURAL GAS |  |  | SEE NOTE | [7 empty] | USE OF NATURAL GAS IS RACT.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | VACUUM CRUDE CHARGE HEATER | 12.39 | REFINERY FUEL GAS OR NG | 101 | MMBTU/H | THIS UNIT IS IDENTIFIED BY EQUIPMENT ID # B-02100 |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0075 | LB/MMBTU | THREE-HOUR AVERAGE |  |  |  |  | 0.0075 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | HYDROCRACKER UNIT MAIN FRACTIONATOR HEATER | 12.39 | REFINERY FUEL GAS OR NG | 211 | MMBTU/H | THIS UNIT IS IDENTIFIED BY EQUIPMENT ID # B-10500 |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0075 | LB/MMBTU | THREE-HOUR AVG |  |  |  |  | 0.0075 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT CHARGE HEATER | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 122 | MMBTU/H | THIS UNIT IS IDENTIFIED BY EQUIPMENT ID # B-05110 |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0075 | LB/MMBTU | 3-HR AVG. | [6 empty] | NOT AVAILABLE
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT INTERHEATER NO. 1 | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 192 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY EQUIPMENT ID # B-05120 |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0075 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.0075 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT INTERHEATER NO. 2 | 12.39 | REFINERY FUEL GAS OR NATURAL GAS | 129 | MMBTU/H | THIS EQUIPMENT IS IDENTIFIED BY ID # B-05130 |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0075 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.0075 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | DISTILLATE HYDROTREATER SPLITTER REBOILER | 12.39 | REFINERY FUEL GAS OR NATURAL GAS | 117 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY ID # B-08509 |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0075 | LB/MMBTU | 3-HR AVERAGE |  |  |  |  | 0.0075 | LB/MMBTU
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | BUTANE CONVERSION UNIT ISOSTRIPPER REBOILER | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 222 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY ID # B-15110 |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0075 | LB/MMBTU | 3-HR AVERAGE | [6 empty] | NOT AVAILABLE
TX-0478 | CITGO CORPUS CHRISTI REFINERY - WEST PLANT | CITGO REFINING AND CHEMICALS COMAPNY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-04-20 | 2005 |  | MIXED DISTILLATE HYDROHEATER REBOILER HEATER | 12.39 | REFINERY FUEL GAS | 82 | MMBTU/H | THE MDH UNIT REMOVES ORGANIC NITROGEN AND SULFUR FROM THE FEED STREAMS. FEEDSTOCK IS MIXED WITH HYDROGEN , HEATED, AND FED TO A REACTOR. A CATALYTIC REACTION CONVERTS THE ORGANIC SULFUR TO HYDROGEN SULFIDE AND THE NITROGEN COMPOUNDS TO AMMONIA. THE EFFLUENT STREAM IS COOLED AND EXCESS HYDROGEN REMOVED FOR RECYCLE. HYDROGEN SULFIDE IS REMOVED FROM THE HYDROGEN STREAM BY AN AMINE ABSORBER AND ROUTED TO THE SRU. NEW EQUIPMENT UNDER THE AMENDMENT INCLUDES A SECOND REACTOR, ADDITIONAL PREHEAT TRAIN, AN ADDITIONAL REACTOR PRODUCT FLASH DRUM, A HYDROGEN PURIFICATION MEMBRANE AND AN ADDITIONAL HYDROGEN MAKEUP COMPRESSOR. AS PART OF THE AMENDMENT, THE FRACTIONATOR REBOILER WILL BE RETROFIT WITH LOW NOX BURNERS. |  | Particulate Matter < 10 μ (PM10) | N |  | 0.61 | LB/H |  |  | 2.7 | T/YR
TX-0492 | VIRTEX PETROLEUM COMPANY DOERING RANCH GAS PLANT | VIRTEX PETROLEUM INC. | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-05 | 2005 | VIRTEX CURRENTLY OPERATES A GAS PLANT WHICH IS AUTHORIZED UNDER AN OIL AND GAS STANDARD PERMIT. THE MAXIMUM PRODUCTION IS CURRENTLY AUTHORIZED AT 0.3 LONG TONS PER DAY OF SULFUR. THEY ARE REQUESTING AUTHORIZATION TO MODIFY THE EXISTING FACILITY TO PROCESS SOUR GAS FROM NEW FIELD WELLS AND INCREASE MAXIMUM PRODUCTION TO 0.75 LONG TONS PER DAY OF SULFUR (4.0 MMSDFD OF GAS WITH AN H2S CONTENT OF 8.000 PPM). MODIFICATIONS INCLUDE THE INSTALLATION OF NEW COMPRESSORS, AUTHORIZING AN AMINE SWEETENING UNIT, A LARGER CAPACITY GLYCOL DEHYDRATOR, AND ALL ASSOCIATED PIPING. THE INCREASE IN SO2 REQUIRES PSD ANALYSIS. | 1.8 MMBTU AMINE REBOILER | 12.39 | SWEET NATURAL GAS | 1.8 | MMBTU |  |  | Particulate Matter < 10 μ (PM10) | N |  | 0.01 | LB/H |  |  | 0.06 | T/YR
TX-0475 | FORMOSA POINT COMFORT PLANT | FORMOSA PLASTICS CORPORATION TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-09 | 2005 |  | PYROLYSIS FURNACE (1010B) | 12.39 | FUEL GAS | 250 | MMBtu/H |  |  | Particulate Matter < 10 μ (PM10) | N |  | 0.5 | LB/H |  | N/A | 2.2 | T/YR
TX-0475 | FORMOSA POINT COMFORT PLANT | FORMOSA PLASTICS CORPORATION TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-09 | 2005 |  | REBOILER (1 AND 2) | 12.39 | FUEL GAS | 250 | MMBtu |  |  | Particulate Matter < 10 μ (PM10) | N |  | 0.03 | LB/H |  | N/A | 0.13 | T/YR
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-07-27 | 2005 | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | BOILERS A & B (U-1 & U-2) | 12.39 |  | 250 | MMBTU/H |  |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES AND USE OF GASEOUS FUEL | 0.005 | LB/MMBTU | THREE ONE-HOUR TEST AVERAGE | OPERATING PERMIT |  |  |  | 0.005 | LB/MMBTU
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-07-27 | 2005 | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | BOILERS C & D (U-3 & U-4) | 12.39 |  | 250 | MMBTU/H |  |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES AND USE OF NATURAL GAS AS FUEL | 0.005 | LB/MMBTU |  | OPERATING PERMIT |  |  |  | 0.005 | LB/MMBTU | THREE ONE-HOUR TEST AVERAGE
NC-0101 | FORSYTH ENERGY PLANT | FORSYTH ENERGY PROJECTS, LLC | NC | FORSYTH COUNTY ENV AFFAIRS DEPT, NC | 2005-09-29 | 2005 | THREE COMBINED-CYCLE COMBUSTION TURBINE GENERATORS, EACH WITH A HEAT RECOVERY STEAM GENERATORS (HRSG) ALONG WITH NATURAL GAS-FIRED DUCT BURNERS TO MEET PEAK DEMAND. THE STEAM GENERATED THROUGH THE THREE HRSGS WILL DRIVE A STEAM TURBINE. THE ENTIRE PLANT WILL BE CAPABLE OF GENERATING A NOMINAL POWER OUTPUT OF 812 MEGAWATTS. | AUXILLIARY BOILER | 12.31 | NATURAL GAS | 110.2 | MMBTU/H |  |  | Particulate Matter < 10 μ (PM10) | N | LOW-NOX BURNERS, GOOD COMBUSTION CONTROL AND CLEAN BURNING, LOW-SULFUR FUEL (NATURAL GAS). | 0.82 | LB/H | based on 3-hour average |  |  |  |  | 0.007 | LB/MMBTU | calculated
*TX-0496 | INEOS CHOCOLATE BAYOU FACILITY | INEOS USA LLC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-08-29 | 2006 | THE NO. 1 AND NO. 2 OLEFINS UNITS USE PYROLYSIS FURNACES TO CRACK FEEDSTOCKS INTO LOW MOLECULAR WEIGHT HYDROCARBONS THAT CONTAIN OLEFINS. PRODUCTS ARE ETHYLENE, PROPYLENE, PYROLYSIS GASOLINE, CRUDE C4, FUEL OIL, AND HYDROGEN. FEED FOR THE OLEFINS CRACKING FURNACES IS EITHER GAS FEED (ETHANE-RICH OR PROPANE-RICH FEED) OR LIQUID FEED (REFINERY RAFFINATE AND DEBUTANIZED NATURAL GASOLINE (DNG). THE LIQUID FEEDSTOCKS ARE STORED PRIOR TO PROCESSING IN LARGE FLOATING-ROOF TANKS EQUIPPED WITH SECONDARY SEALS. ETHYLENE PRODUCT IS TRANSFERRED OFF-SITE BY PIPELINE. PROPYLENE IS SHIPPED VIA RAILCAR, BARGE, OR SENT TO AN EXISTING POLYPROPYLENE UNIT AT THE CHOCOLATE BAYOU PLANT FOR FURTHER PROCESSING. CRUDE C4 STOCK IS SENT TO THE BUTADIENE EXTRACTION UNIT (BEU) TO PRODUCE HIGH PURITY BUTADIENE WHICH IS SOLD. BUTADIENE PRODUCT IS SHIPPED OFF-SITE VIA RAILCAR OR BARGE. THE RAW PYROLYSIS GASOLINE IS FURTHER HYDROTREATED TO PYROLYSIS GASOLINE PRODUCT FOR SHIPMENT OFF SITE | FURNACE EMISSION CAPS | 12.39 |  |  |  | EMISSION CAPS FOR FURNACES ARE NOT CHANGED IN THIS PERMIT ACTION. SPECIAL CONDITION NO. 13 IS CHANGED TO CLARIFY BACT SHALL BE DEMONSTRATED FOR EACH NEW FURNACE (EQUIPPED WITH SCR) AND ALLOW EXCEPTION WHEN THE UNIT IS IN DECOKING. SPECIAL CONDITION NO. 51 IS CHANGED TO ALLOW BACT FOR OLD FURNACES TO BE DEMONSTRATED AT THE LEVELS WHEN THE FLEXIBLE PERMIT WAS ISSUED. COMBUSTION STAFF WAS CONSULTED AND CONCURRED WITH THE CHANGE. |  | Particulate Matter < 10 μ (PM10) | N |  | 32.65 | LB/H |  |  | 143 | T/YR
NV-0043 | LASCO BATHWARE | LASCO BATHWARE | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2006-10-25 | 2006 | A BATHWARE MANUFACTURING FACILITY | FUEL BURNING FOR THERMOSETTING | 12.31 | PROPANE | 6.3 | MMBTU/H | THERMOSETTING IS THE HEATING PROCESS TO HARDEN THE BATHROOM FIXTURES AFTER THEY ARE MOLDED INTO SHAPE. THERE ARE TWO HEATERS FOR EACH PRODUCTION LINE. ADDITIONALLY THERE ARE FIVE AIR HEATERS AT THE CURE TUNNEL. THE TOTAL HEAT INPUT CAPACITY FOR THE FUEL BURNING EQUIPMENT IS 27.56 MMBTU/HR. THE ANNUAL CONSUMPTION OF PROPANE FOR OPERATING THE FUEL BURNING EQUIPMENT IS LIMITED TO 662,645 GALLONS PER YEAR. MOST EMISSIONS COME FROM FUEL COMBUSTION, NOT FROM THE BATHROOM FIXTURES BEING HARDENED. THE EXHAUST OF THE HEATER DESIGNATED IN THE PERMIT AS A02 IS CHOSEN AS THE TYPICAL EMISSION UNIT FOR REPORTING THE PROCESS DATA. THIS HEATER IS SUBJECT TO THE LIMIT OF ANNUAL OPERATING TIME OF 2,200 HOURS PER YEAR. |  | Particulate Matter < 10 μ (PM10) | N | N/A | 0.03 | LB/H |  | SIP | 0.03 | T/YR
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | A & B VACUUM TOWER HEATERS (3-08 & 4-08) | 12.39 | REFINERY FUEL GAS | 155.2 | MMBTU/H EA. |  |  | Particulate Matter < 10 μ (PM10) | P | PROPER DESIGN, OPERATION, AND GOOD ENGINEERING PRACTICES |  |  |  | SIP |  |  |  | 0.0075 | LB/MMBTU | 3-HOUR AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | NAPHTHA HYDROTREATER STRIPPER REBOILER HEATER (6-08) & KHT STRIPPER REBOILER HEATER (10-08) | 12.39 | REFINERY FUEL GAS |  |  | 6-08: 138.4 MMBTU/H 10-08: 121.8 MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | PROPER DESIGN, OPERATION, AND GOOD ENGINEERING PRACTICES |  |  |  | SIP |  |  |  | 0.0075 | LB/MMBTU | 3-HOUR AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | SATS GAS PLANT HOT OIL HEATER (14-08) | 12.39 | REFINERY FUEL GAS | 183.3 | MMBTU/H |  |  | Particulate Matter < 10 μ (PM10) | P | PROPER DESIGN, OPERATION, AND GOOD ENGINEERING PRACTICES |  |  |  | SIP |  |  |  | 0.0075 | LB/MMBTU | 3-HOUR AVERAGE
*LA-0213 | ST. CHARLES REFINERY | VALERO REFINING - NEW ORLEANS, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2007-02-08 | 2007 | PETROLEUM REFINERY. PROJECT INVOLVES INCREASE IN CAPACITY FROM 220,000 TO 380,000 BARRELS PER DAY. | REBOILER 2005-18 & HEATERS F-15-02 (6-81), 2005-14, 2005-17, 2005-29, 2005-32, & 2005-37 | 12.39 | REFINERY FUEL GAS |  |  | 6-81: 135 MM BTU/HR 2005-14: 195 MM BTU/HR 2005-17: 159 MM BTU/HR 2005-18: 231 MM BTU/HR 2005-29: 195 MM BTU/HR 2005-32: 159 MM BTU/HR 2005-37: 173 MM BTU/HR SOURCES ALSO FIRE NATURAL GAS. |  | Particulate Matter < 10 μ (PM10) | P | PROPER EQUIPMENT DESIGN AND OPERATION, GOOD COMBUSTION PRACTICES, AND USE OF GASEOUS FUELS | 0.0074 | LB/MMBTU | ANNUAL AVERAGE | SIP
*IA-0089 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-08-08 | 2007 | 170 MILLION GALLON PER ROLLING 12-MONTH PERIOD DRY MILL ETHANOL PLANT. THE PROCESS WILL USE GASIFICATION TECHNOLOGY TO PRODUCE SYNGAS AS THE SOURCE FOR ENERGY. WILL USE 60,714,286 BUSHELS OF CORN PER ROLLING 12-MONTH PERIOD PRODUCING EITHER 1.411 MILLION TONS OF WDGS OR 552,500 TONS OF DDGS PER ROLLING 12-MONTH PERIOD. THE GASIFICATION PROCESS COULD USE UP TO 298, 213 TONS OF COAL PER ROLLING 12-MONTH PERIOD. PROJECT NUMBER (PN) 06-672, 28 PERMITS ISSUED | THERMAL OXIDIZER FOR HRSG FROM DRYERS AND GASIFICATION - TWO SYSTEMS, S10 AND S11 (07-A-955P AND 07-A-956P) | 12.3 | SYNGAS | 250 | MM BTU / hr | THE THERMAL OXIDIZER IS 150 MM BTU / HR AND EACH DRYER (TWO TOTAL FOR THIS EMISSION POINT) IS 50 MM BTU / HR. |  | Particulate Matter < 10 μ (PM10) | N |  | 0.01 | LB/MMBTU | BACT | OTHER | 0.03 | LB/MMBTU | NSPS | 0.1 | GR/DSCF | 23.3(2)
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Particulate Matter < 10 μ (PM10) | A | WET SCRUBBER & CYCLONE | 0.0044 | GR/DSCF |  |  | 0.9 | LB/H |  |  |  |  | THIS COVERS PM10 FOR THE ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA 22).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Particulate Matter < 10 μ (PM10) | A | WET SCRUBBER & CYCLONE | 0.0044 | GR/DSCF |  |  | 0.9 | LB/H |  |  |  |  | THIS COVERS PM10 FOR THE FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA 23).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Particulate Matter < 10 μ (PM10) | A | BAGHOUSE | 0.005 | GR/DSCF |  |  | 0.18 | LB/H |  |  |  |  | THIS COVERS PM10 FOR THE PLATE SHOTBLASTER WITH BAGHOUSE (LA28).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0076 | LB/MMBTU |  |  | 1.28 | LB/H |  |  |  |  | THIS COVERS PM10 FOR THE NATURAL GAS-FIRED REHEAT FURNACE (LA 21).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0076 | LB/MMBTU |  |  | 0.046 | LB/H |  |  |  |  | THIS COVERS PM10 FOR THE 3 COIL DRUM FURNACES (LA24-LA26).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0076 | LB/MMBTU |  |  | 0.13 | LB/H |  |  |  |  | THIS COVERS PM10 FOR THE PLATE ANNEALING FURNACE (LA27).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS -FIRED ANNEALING FURNACE (LA43) (MULTIPLE EMISSION POINTS) | 12.31 | NATURAL GAS | 196.4 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X016: SULFURIC ACID PICKLING WITH CAUSTIC SCRUBBER (LA46) - RBLC PROCESS CODE - 81.290 PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0076 | LB/MMBTU |  |  | 1.5 | LB/H |  |  |  |  | THIS COVERS PM10 FOR THE NATURAL GAS-FIRED ANNEALING FURNACE (LA43).
*NM-0050 | ARTESIA REFINERY | NAVAJO REFINING COMPANY LLC | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2007-12-14 | 2007 | 115,000 - 125,000 BBL/DAY NOMINALLY RATED PETROLEUM REFINERY. | ROSE 2 HOT OIL HEATER | 12.3 | REFINERY FUEL GAS | 120 | mmbtu/hr |  |  | Particulate Matter < 10 μ (PM10) | P | GASEOUS FUEL COMBUSTION ONLY | 0.0075 | LB/MMBTU | HOURLY
NV-0043 | LASCO BATHWARE | LASCO BATHWARE | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2006-10-25 | 2006 | A BATHWARE MANUFACTURING FACILITY | FUEL BURNING FOR THERMOSETTING | 12.31 | PROPANE | 6.3 | MMBTU/H | THERMOSETTING IS THE HEATING PROCESS TO HARDEN THE BATHROOM FIXTURES AFTER THEY ARE MOLDED INTO SHAPE. THERE ARE TWO HEATERS FOR EACH PRODUCTION LINE. ADDITIONALLY THERE ARE FIVE AIR HEATERS AT THE CURE TUNNEL. THE TOTAL HEAT INPUT CAPACITY FOR THE FUEL BURNING EQUIPMENT IS 27.56 MMBTU/HR. THE ANNUAL CONSUMPTION OF PROPANE FOR OPERATING THE FUEL BURNING EQUIPMENT IS LIMITED TO 662,645 GALLONS PER YEAR. MOST EMISSIONS COME FROM FUEL COMBUSTION, NOT FROM THE BATHROOM FIXTURES BEING HARDENED. THE EXHAUST OF THE HEATER DESIGNATED IN THE PERMIT AS A02 IS CHOSEN AS THE TYPICAL EMISSION UNIT FOR REPORTING THE PROCESS DATA. THIS HEATER IS SUBJECT TO THE LIMIT OF ANNUAL OPERATING TIME OF 2,200 HOURS PER YEAR. |  | Styrene | N | N/A | 0.02 | LB/H |  | SIP | 0.02 | T/YR
IN-0075 | GRAIN PROCESSING CORP. | GRAIN PROCESSING CORP. | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1997-06-10 | 1997 |  | BOILERS NO. 1 & 2 | 12.39 | NATURAL GAS/ALCOHOL | 244 | MMBTU/H (EACH) | STACK TEST REQUIRED BY PERMIT, NOT YET CONSTRUCTED. BOILER NO.1 (UP51A), BOILER NO.2 (UP51B). |  | Sulfur Dioxide (SO2) | P | GOOD COMBUSTION PRACTICES | 0.64 | T/YR (EACH) | [7 empty] | NOT AVAILABLE
NJ-0041 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-10-08 | 1997 |  | DUCT BURNER ONLY | 12.31 | NATURAL GAS | 234 | MMBTU/H | TOTAL NATURAL GAS BURNED IN THE HEAT RECOVERY BOILER SHALL NOT EXCEED 1153.2 MILLION CUBIC FEET PER CALENDAR YEAR |  | Sulfur Dioxide (SO2) | P | LOW NOX BURNER | 1.6 | LB/H |  |  | 0.007 | LB/MMBTU |  | 0.007 | LB/MMBTU
SC-0075 | NUCOR STEEL- DARLINGTON COUNTY | NUCOR STEEL CORPORATION | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 1998-01-08 | 1998 | STEEL MILL | REHEAT FURNACE #1 | 12.31 | NATURAL GAS | 140 | MMBTU/H | MAIN FUEL IS NATURAL GAS, PROPANE AS A BACK-UP. UTILIZES LOW NOX BURNERS. NATURAL GAS AND PROPANE USAGE IS RESTRICTED TO AN EQUIVALENT OF 1150 X MMSCF PER YEAR AT ESTABLISHED BTU CONTENTS OF 1000 BTU/CF AND 90500 BTU/GALLON RESPECTIVELY. SUBJECT TO PSD. |  | Sulfur Dioxide (SO2) | N |  | 0.12 | LB/H |  |  | 0.53 | T/YR |  | 0.0009 | LB/MMBTU
SC-0075 | NUCOR STEEL- DARLINGTON COUNTY | NUCOR STEEL CORPORATION | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 1998-01-08 | 1998 | STEEL MILL | REHEAT FURNACE #2 | 12.31 | NATURAL GAS | 125 | MMBTU/H | NATURAL GAS IS MAIN FUEL, PROPANE AS BACK UP. UTILIZES LOW NOX BURNERS AND EXTERNAL FLUE GAS RECIRCULATION. NATURAL GAS AND PROPANE USAGE IS RESTRICTED TO AN EQUIVALENT OF 1095 MMSCF PER YEAR AS ESTABLISHED BTU CONTENTS OF 1000 BTU/CF AND 90500 BTU/GAL RESPECTIVELY. SUBJECT TO PSD. |  | Sulfur Dioxide (SO2) | N | NONE INDICATED | 0.08 | LB/H |  |  | 0.4 | T/YR |  | 0.0006 | LB/MMBTU
TX-0259 | FREEPORT COGENERATION FACILITY | BASF CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-06-26 | 1998 | CONSTRUCTION OF A COGENERATION UNIT | BOILER, B-20A | 12.39 | H2 WASTE & NAT GAS | 213 | MMBTU/H | HYDROGEN WASTE GAS AND PIPELINE QUALITY, SWEET NAT GAS CONTAINING NO >0.25 GR H2S AND 5 GR TOTAL S/100 DSCF. SCC CODE FOR NATURAL GAS CHOSEN FOR THE PURPOSE OF THIS DATABASE. |  | Sulfur Dioxide (SO2) | P | USE OF GOOD COMBUSTION. | 0.01 | LB/H |  | NSPS | 0.04 | T/YR |  | 0.0001 | LB/MMBTU | CALCULATED | EMISSION LIMIT IN STANDARDIZED UNITS CALCULATED FROM THE HOURLY EMISSION LIMIT AND THE THROUGHPUT.
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | 1998 | VEGETABLE OIL PLANT | BOILER, TRANE MURRAY, NAT GAS | 12.31 | NATURAL GAS | 189 | MMBTU/H | No add-on controls. See separate process for backup fuel (No. 2 oil) requirements. |  | Sulfur Dioxide (SO2) | P | NATURAL GAS | 0.2 | LB/MMBTU | [5 empty] | 0.2 | LB/MMBTU
OH-0245 | REPUBLIC TECHNOLOGIES INTERNATIONAL | REPUBLIC TECHNOLOGIES INTERNATIONAL/CANTON | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 1999-01-27 | 1999 | STEEL MILL. THIS PLANT IS PSD FOR PM, SO2, NOX, CO, AND VOC. THIS MODIFICATION IS A SIGNIFICANT INCREASE FOR NOX. | BLOOM REHEAT FURNACE | 12.31 | NATURAL GAS | 196.2 | MMBTU/H | STACK TEST 0.0489 LB NOX/HR |  | Sulfur Dioxide (SO2) | N |  | 0.12 | LB/H |  | SIP | 0.52 | T/YR |  | 0.0006 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 4 (NAT GAS) | 12.31 | NATURAL GAS | 118 | MMBTU/H | MFR. IS BABCOCK & WILCOX. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Sulfur Dioxide (SO2) | N | NONE LISTED | 0.1 | LB/H | [5 empty] | 0.0008 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 2 (NAT GAS) | 12.31 | NATURAL GAS | 134 | MMBTU/H | MFR. IS COMBUSTION ENGINEERING. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Sulfur Dioxide (SO2) | N | NONE LISTED | 0.1 | LB/H | [5 empty] | 0.0007 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 3 (NAT GAS) | 12.31 | NATURAL GAS | 152 | MMBTU/H | MFR. IS BABCOCK & WILCOX. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Sulfur Dioxide (SO2) | N | NONE LISTED | 0.1 | LB/H | [5 empty] | 0.0007 | LB/MMBTU
TX-0414 | ATOFINA PETROCHEMICALS PORT ARTHUR COMPLEX | FINA OIL & CHEMICAL COPMANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1999-04-22 | 1999 | FACILITY WANTS TO INSTALL A COGENERATION FACILITY CONSISTING OF 2 TURBINES AND SUPPLEMENTAL BOILER TO SUBSTITUTE FOR 2 AUXILIARY STEAM BOILERS | SUPPLEMENTAL BOILER | 12.31 | NATURAL GAS | 227 | MMBTU/H | BOILER PRODUCES AS MUCH AS 150,000 LB/H OF STEAM. |  | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL | 0.61 | LB/H |  |  | 0.73 | T/YR |  | 0.0027 | LB/MMBTU | CALCULATED
AR-0026 | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1999-05-05 | 1999 | COMBUSTION TURBINE COMBINED CYCLE COGENERATION FACILITY | DUCT BURNER | 12.31 | NATURAL GAS | 315 | MMBTU/H | TURBINE AND DUCT BURNER EMISSIONS COMBINED IN ONE STACK. DUCT BURNER ALWAYS FIRES NATURAL GAS. |  | Sulfur Dioxide (SO2) | P | CLEAN FUEL | 0.0006 | LB/MMBTU | [5 empty] | 0.0006 | LB/MMBTU
AR-0026 | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1999-05-05 | 1999 | COMBUSTION TURBINE COMBINED CYCLE COGENERATION FACILITY | BOILER, NATURAL GAS | 12.31 | NATURAL GAS | 362 | MMBTU/H | BOILER FIRES NATURAL GAS AND FUEL OIL. BOILER WILL PROVIDE STEAM FOR STEAM TURBINE AND INTERNATIONAL PAPER MILL. |  | Sulfur Dioxide (SO2) | P | COMBUSTION OF LOW SULFUR FUELS (< 0.05% BY WT S) | 0.0006 | LB/MMBTU | [5 empty] | 0.0006 | LB/MMBTU
SC-0049 | SKYGEN | BROAD RIVER ENERGY, LLC | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 1999-12-02 | 1999 |  | THREE NATURAL GAS FIRED BOILERS (UTILITY) | 12.31 | NATURAL GAS | 230 | MMBTU/H | 1700 H/YR MAX OPERATION PER BOILER. |  | Sulfur Dioxide (SO2) | P | LOW SULFUR FUELS | 0.0006 | LB/MMBTU | [5 empty] | 0.0006 | LB/MMBTU
AK-0037 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFIDE CONTENT TO 0.01% FROM 0.001%, AN INCREASE IN OPERATING HOURS OF P708C FROM 200 TO 600 HOURS PER YEAR, THE REMOVAL OF PERCENT EFFICIENCY REQUIREMENTS FOR AS1310 AND 1320, AND USE OF THERMAL OXIDATION TO CONTROL EMISSIONS FROM AS1320. | CRUDE HEATER, H101A | 12.39 | NATURAL GAS* | 140 | MMBTU/H | INSTALLED PRIOR TO 1975, THEREFORE NOT REQUIRED TO COMPLY WITH THE PSD PROGRAM. DESIGN CAPACITY OF 140.0 MMBTU/H AUTHORIZED RATED CAPACITY IS 1 MMBTU/H. *FUELS ARE NATURAL GAS, REFINERY GAS AND LPG. NO INDICATION IS PROVIDED AS TO WHICH IS THE PRIMARY FUEL. |  | Sulfur Dioxide (SO2) | N | NONE INDICATED AS SOURCE WAS INSTALLED PRIOR TO 1975 AND IS NOT SUBJECT TO BACT-PSD. | [10 empty] | SOURCE IS NOT SUBJECT TO PSD REQUIREMENTS BECAUSE IT WAS INSTALLED PRIOR TO 1975. ESTIMATED EMISSIONS ARE 18.4 T/YR, BUT THIS IS NOT AN EMISSION LIMIT.
AK-0037 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFIDE CONTENT TO 0.01% FROM 0.001%, AN INCREASE IN OPERATING HOURS OF P708C FROM 200 TO 600 HOURS PER YEAR, THE REMOVAL OF PERCENT EFFICIENCY REQUIREMENTS FOR AS1310 AND 1320, AND USE OF THERMAL OXIDATION TO CONTROL EMISSIONS FROM AS1320. | CRUDE HEATER, H101B | 12.39 | NATURAL GAS* | 165 | MMBTU/H | DESIGN CAPACITY IS 165.0 MMBTU/H BUT AUTHORIZED RATED CAPACITY IS 1 MMBTU/H. *SOURCE BURNS COMBINATION OF REFINERY GAS, NATURAL GAS, AND LIQUID PETROLEUM GAS. IT IS NOT SPECIFIIED WHICH TYPE OF FUEL IS PRIMARY. |  | Sulfur Dioxide (SO2) | P | FUEL SULFUR CONTENT LIMITS AS FOLLOWS: DIESEL, 0.35% SULFUR; NATURAL GAS, 0.01% SULFUR; LPG, 0.01% SULFUR; REFINERY GAS, 168 PPMV H2S. GAS, 168 PPMV H2S. |  |  | SEE POLLUTANT NOTES | [7 empty] | EMISSIONS INFORMATION IS PROVIDED FOR SO2 AND H2S TOGETHER. THIS SOURCE IS ALSO SUBJECT TO NSPS FOR SO2. LIMITS ARE PROVIDED BASED ON FUEL CONTENT (SEE POLLUTION PREVENTION DESCRIPTION). ESTIMATED EMISSIONS ARE 21.7 T/YR, BUT THIS IS NOT A LIMIT. ADDITIONAL LIMIT IS A PRORATED CONCENTRATION OF THE FOLLOWING: 230 MG H2S/DSCF FOR EQUIPMENT FIRED ON REFINERY GAS, AND 500 PPM SO2 FOR EQUIPMENT NOT FIRED ON REFINERY GAS.
TX-0395 | DIAMOND SHAMROCK MCKEE PLANT | DIAMOND SHAMROCK REFINING COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-05-23 | 2000 |  | NO. 1 REFORMER CHARGE HEATER | 12.39 | REFINERY GAS | 248 | MMBTU/H |  |  | Sulfur Dioxide (SO2) | N |  | 9.33 | LB/H |  |  | 12.26 | T/YR
TX-0395 | DIAMOND SHAMROCK MCKEE PLANT | DIAMOND SHAMROCK REFINING COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-05-23 | 2000 |  | NO 1 INTERHEATER | 12.39 | REFINERY GAS | 147.2 | MMBTU/H |  |  | Sulfur Dioxide (SO2) | N |  | 5.54 | LB/H |  |  | 7.28 | T/YR
TN-0146 | FLORIM, USA, INC. | FLORIM, USA, INC. | TN | TENNESSEE DIV OF AIR POLLUTION CONTROL | 2000-12-20 | 2000 | CERAMIC TILE MANUFACTURING PROCESS CONSISTING OF RAW MATERIAL HANDLING, SPRAY DRYING, TILE PREPARATION, AND TILE FIRING OPERATIONS. THE COMPANY APPLIED FOR A PSD PERMIT TO INCREASE THE MATERIAL INPUT RATE THROUGH THE FACILITY'S TILE KILNS. | GAS-FIRED KILNS | 12.31 | NATURAL GAS | 125 | MMBTU/H | Seven (7) gas-fired tile kilns and one (1) gas-fired trim kiln with lime injection/coated baghouse controls. |  | Sulfur Dioxide (SO2) | A | COATED BAGHOUSE, HYDRATED CALCIUM MEDIUM. | 0.266 | LB/MMBTU |  |  | 33.3 | LB/H |  | 0.266 | LB/MMBTU |  | The facility must meet compliance with production limits and recordkeeeping requirements to demonstrate compliance with emission limits.
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | 2001 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORIZED FIRING RATE WILL BE 481 MMBTU/H ON A ROLLING 12 MONTH AVERAGE, AND 502 MMBTU/H MAXIMUM HOURLY FIRING RATE. THE ADDITION OF THE NEW FURNACE TRIGGERED PSD REVIEW. | FURNACE HF-01 | 12.39 | ETHANE | 238 | MMBTU/H | 200 MMBTU/H AVE. FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% THEANE/PROPANE MIXTURE. |  | Sulfur Dioxide (SO2) | N | NONE INDICATED | 1.1 | LB/H |  |  | 0.17 | T/YR |  | 0.005 | LB/MMBTU | CALCULATED USING MAX THROUGHPUT
IN-0085 | PSEG LAWRENCEBURG ENERGY FACILITY | PSEG LAWRENCEBURG ENERGY FACILITY | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-06-07 | 2001 |  | AUXILIARY BOILER, NATURAL GAS | 12.31 | NATURAL GAS | 124.6 | MMBTU/H | AUXILIARY BOILER IS LIMITED TO 1000 H/YR OF OPERATION |  | Sulfur Dioxide (SO2) | P | LOW SULFUR NATURAL GAS (LESS THAN %0.8 BY WEIGHT) | 0.006 | LB/MMBTU |  |  | 0.7 | LB/H |  | 0.006 | LB/MMBTU
OK-0045 | REDBUD POWER PLT | REDBUD ENERGY LP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-15 | 2001 | ELECTRICAL GENERATION FACILITY | BOILER, AUXILIARY | 12.31 | NATURAL GAS | 20 | MMBTU/H | boiler operates < 3000 hours per year |  | Sulfur Dioxide (SO2) | P | PIPELINE QUALITY NATURAL GAS FUEL | 0.0006 | LB/MMBTU | [5 empty] | 0.0006 | LB/MMBTU
AR-0057 | TENASKA ARKANSAS PARTNERS, LP | TENASKA ARKANSAS PARTNERS, LP | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-10-09 | 2001 | ELECTRIC POWER GENERATING STATION. FACILITY WAS NEVER CONSTRUCTED AND THE PERMIT WAS VOIDED 1/07/03. ADDITIONAL PLANTWIDE EMISSIONS: PM10 858 T/YR, AMMONIA 844 T/YR. | BOILER, NATURAL GAS, (2) | 12.31 | NATURAL GAS | 122 | MMBTU/H | Throughput for each boiler. |  | Sulfur Dioxide (SO2) | P | FUEL SPECIFICATION: NATURAL GAS. | 0.006 | LB/MMBTU | [5 empty] | 0.006 | LB/MMBTU
AR-0055 | NUCOR YAMATO STEEL (ARMOREL) | NUCOR YAMATO STEEL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-10-10 | 2001 | STEEL MILL. | REHEAT FURNACE | 12.31 | NATURAL GAS | 225 | MMBTU/H |  |  | Sulfur Dioxide (SO2) | P | CLEAN FUELS | 0.0006 | LB/MMBTU | [5 empty] | 0.0006 | LB/MMBTU
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | 2001 | ELECTRICITY GENERATION | AUXILIARY BOILER | 12.31 | NATURAL GAS | 120 | MMBTU/H |  |  | Sulfur Dioxide (SO2) | P | NATURAL GAS FUEL | 0.514 | LB/H |  |  | 0.926 | T/YR |  | 0.0043 | LB/MMBTU
FL-0251 | OKEELANTA CORPORATION SUGAR MILL | NEW HOPE POWER PARTNERSHIP | FL | FLORIDA DEPT. OF ENVIRONMENTLA PROTECTION | 2001-10-29 | 2001 | SUGAR MILL | BOILER, NATURAL GAS | 12.31 | NATURAL GAS | 211 | MMBTU/H | State SIP rule requires a BACT for SO2 and PM emissions regardless of increase. The efficient combustion of clean fuels will minimize emissions of CO, PM/PM10, SO2, and VOC. The installation of low NOx burners with flue gas recirculation will reduce NOx emissions. |  | Sulfur Dioxide (SO2) | P | FUEL SPECIFICATIONS | [9 empty] | see notes | BACT is pipeline natural gas. State BACT, Rule 62- 296.406 FAC
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BOILER NO. 12 | 12.39 |  | 245 | MMBTU/H | EMISSION PT NO: BOILER-12. SHALL BE SHUTDOWN. |  | Sulfur Dioxide (SO2) | P | LOW S FUEL: FUEL GAS WITH H2S CONTENT NO MORE THAN 0.1 GR/DSCF OVER A 3 H ROLLING BASIS, OR NATURAL GAS WITH H2S CONTENT NO MORE THAN 0.25 GR/100 DSCF AND TOTAL S CONTENT NO MORE THAN 5.0 GR/ 100 DSCF. | 6.3 | LB/H |  |  | 27.6 | T/YR |  | 0.026 | LB/MMBTU | CALCULATED
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BTU-NO. 1 REACTOR FEED HEATER | 12.39 |  | 121.74 | MMBTU/H | EMISSION POINT NO. BTU-HF103. |  | Sulfur Dioxide (SO2) | P | LOW S FUEL: FUEL GAS WITH H2S CONTENT NO MORE THAN 0.1 GR/DSCF OVER A 3 H ROLLING BASIS, OR NATURAL GAS WITH H2S CONTENT NO MORE THAN 0.25 GR/100 DSCF AND TOTAL S CONTENT NO MORE THAN 5.0 GR/ 100 DSCF. | 3.1 | LB/H |  |  | 13.7 | T/YR |  | 0.025 | LB/MMBTU | CALCULATED
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ISOM II WEST REACTOR FEED HEATER | 12.39 |  | 104.25 | MMBTU/H | EMISSION POINT NO. BTU-HF106. |  | Sulfur Dioxide (SO2) | P | LOW S FUEL: FUEL GAS WITH H2S CONTENT NO MORE THAN 0.1 GR/DSCF OVER A 3 H ROLLING BASIS, OR NATURAL GAS WITH H2S CONTENT NO MORE THAN 0.25 GR/100 DSCF AND TOTAL S CONTENT NO MORE THAN 5.0 GR/ 100 DSCF. | 2.7 | LB/H |  |  | 11.7 | T/YR |  | 0.026 | LB/MMBTU | CALCULATED
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ORTHOXYLENE II HEATER | 12.39 |  | 226.42 | MMBTU/H | EMISSION POINT NO.: ORTHOII-H2. |  | Sulfur Dioxide (SO2) | P | LOW SULFUR CONTENT FUEL: USE REFINERY FUEL GAS WITH NO MORE THAN 0.1 GR/DSCF H2S OR USE NATURAL GAS WITH NO MORE THAN 0.25 GR/100 DSCF H2S AND NO MORE THAN 5.0 GR/100 DSCF TOTAL S. | 5.8 | LB/H |  |  | 25.5 | T/YR |  | 0.026 | LB/MMBTU | CALCULATED
TX-0386 | AMELLA ENERGY CENTER | CALPINE CONSTRUCTION FINANCE CO. LP | TX | CITY OF HOUSTON BUREAU AIR QUAL CTRL, TX | 2002-03-26 | 2002 |  | AUXILIARY BOILER | 12.31 | NATURAL GAS | 155 | MMBTU/H |  |  | Sulfur Dioxide (SO2) | N |  | 0.843 | LB/H | [5 empty] | 0.005 | LB/MMBTU
NJ-0043 | LIBERTY GENERATING STATION | LIBERTY GENERATING STATION | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2002-03-28 | 2002 | ELECTRICITY GENERATION | AUXILIARY BOILER | 12.31 | NATURAL GAS | 200 | MMBTU/H | NATURAL GAS USAGE RESTRICTED TO 181.0 MILLION SCF/YR (EQUIVALENT TO A 10% ANNUAL CAPACITY FACTOR) |  | Sulfur Dioxide (SO2) | N | NONE | 0.8 | LB/H | [5 empty] | 0.004 | LB/MMBTU |  | BASIS OF LIMIT IS STATE.
VA-0270 | VCU EAST PLANT | VIRGINIA COMMONWEALTH UNIVERSITY | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-31 | 2003 |  | BOILER NATUAL GAS | 12.31 | NATURAL GAS | 150 | MMBTU/H | This is one of 3 boilers |  | Sulfur Dioxide (SO2) | P | GOOD COMBUSTION PRACTICES. LOW SULFUR FUELS. | 0.1 | LB/H | each unit 3hr rolling avg |  |  |  |  | 0.001 | LB/MMBTU
VA-0278 | VCU EAST PLANT | Virginia Commonwealth University | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-31 | 2003 | STEAM GENERATING PLANT AT UNIVERSITY | BOILER, NATURAL GAS, (3) | 12.31 | NATURAL GAS | 150.6 | MMBTU/H | Throughput for each. The 3 boilers shall consume no more than 3,500 million cf of natural gas per year |  | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL | 0.1 | LB/H | [5 empty] | 0.0007 | LB/MMBTU | calculated
LA-0197 | ALLIANCE REFINERY | CONOCOPHILLIPS CO | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2003-10-03 | 2003 | CLEAN FUELS PROJECT TO COMPLY WITH TIER 2 SULFUR STANDARDS. PROJECT INVOLVES CONSTRUCTION OF A CHARGE HEATER, A REBOILER, 3 INTERMEDIATE GASOLINE STORAGE TANKS, AND PIPING AND FUGITIVE COMPONENTS. ALSO, STEAM PRODUCTION FROM THE EXISTING BOILERS, COOLING TOWER RECIRCULATION RATE, SULFUR PRODUCTION AT THE SULFUR RECOVERY UNITS, AND WASTEWATER THROUGHPUT WILL ALSO INCREASE. | LOW SULFUR GASOLINE FEED HEATER NO. 1 | 12.39 | FUEL GAS | 138.12 | MMBTU/H | AVERAGE HEAT INPUT = 115.10 MMBTU/H |  | Sulfur Dioxide (SO2) | P | COMBUSTION OF LOW SULFUR (NSPS J COMPLIANT) FUELS | 3.1 | LB/H | HOURLY MAXIMUM | OPERATING PERMIT | 13.56 | T/YR | ANNUAL MAXIMUM | 0.0269 | LB/MMBTU | ANNUAL AVERAGE
PA-0231 | UNITED REFINERY CO. | UNITED REFINERY CO | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2003-10-09 | 2003 | THE MODIFICATIONS INCLUDE THE INSTALLATION OF THREE NEW SOURCES AND MODS TO EXISTING SOURCES, THIS PERMIT ACTION IS SUBJECT TO SUBPARTS J,GGG QQQ OF THE NSPS, MACT SUBPARTS CC AND UUU AND NESHAPS SUBPARTS FF AND IS PSD FOR CO. | NORTH CRUDE HEATER | 12.39 | REFINERY GAS | 147 | MMBTU/H | The north crude heater was modified by installing low NOx burners. The reduction of NOx emissions reduces the overall increase below significant levels allowing the project to net out" of NSR and PSD for NOx." |  | Sulfur Dioxide (SO2) | P | USE OF DESULFURIZED REFINERY GAS | 46.22 | LB/H |  |  | 202.5 | T/YR |  | 0.3 | LB/MMBTU | Calculated using heat input | Best available technology (BAT) review done.
PA-0231 | UNITED REFINERY CO. | UNITED REFINERY CO | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2003-10-09 | 2003 | THE MODIFICATIONS INCLUDE THE INSTALLATION OF THREE NEW SOURCES AND MODS TO EXISTING SOURCES, THIS PERMIT ACTION IS SUBJECT TO SUBPARTS J,GGG QQQ OF THE NSPS, MACT SUBPARTS CC AND UUU AND NESHAPS SUBPARTS FF AND IS PSD FOR CO. | DELAYED COKER UNIT, HEATER | 12.39 | REFINERY GAS | 116 | MMBTU/H | The unit is subject to the NSPS 40 CFR Subpart J, Subpart GGG, Subpart QQQ. The unit is also subject to MACT standards in 40 CFR 63 Subpart CC, and NESHAP requirements in 40 CFR 61 Subpart FF. |  | Sulfur Dioxide (SO2) | P | LOW SULFUR REFINERY GAS | 2.71 | LB/H |  |  | 11.9 | T/YR |  | 0.023 | LB/MMBTU | Calculated using heat input | Best available technology (BAT) review done.
WV-0023 | MAIDSVILLE | LONGVIEW POWER, LLC | WV | WEST VIRGINIA AIR POLLUTION CONTROL COMM | 2004-03-02 | 2004 | PULVERIZED COAL-FIRED STEAM GENERATOR CAPABLE OF GENERATING 600MW OF ELECTRIC POWER. THIS FACILITY IS A GREEN FIELD SITE, WHICH INCLUDES A 6,114 MMBTU COAL-FIRED BOILER, 225 MMBTU NATURAL GAS-FIRED AUX BOILER, EMERGENCY GENERATOR, FIRE WATER PUMP ENGINE, COOLING TOWERS, AND MATERIAL HANDLING SYSTEMS. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 225 | mmbtu/h | LIMITED TO NATURAL GAS USE AND 3,000 HOURS OF OPERATION PER YEAR |  | Sulfur Dioxide (SO2) | P | LOW SULFUR NATURAL GAS FUEL | 0.004 | LB/H | 3 HOUR ROLLING AVERAGE | SIP |  |  |  | 1.8 | E-5 LB/MMBTU | 3 HOUR ROLLING AVERAGE | LIMITED TO USE OF NATURAL GAS AND 3,000 HOURS OF OPERATION PER YEAR
OH-0241 | MILLER BREWING COMPANY - TRENTON | MILLER BREWING COMPANY | OH | HAMILTON CO-SOUTHWESTERN OH APCA | 2004-05-27 | 2004 | BEER BREWING AND PACKAGING. | BOILER (2), NATURAL GAS | 12.31 | NATURAL GAS | 238 | MMBTU/H | TWO BOILERS, CAPABLE OF BURNING AND WITH LIMITS FOR COAL, NATURAL GAS, NUMBERS 2 AND 6 FUEL OILS. POUND PER HOUR LIMITS ARE FOR EACH BOILER; AND EXCEPT FOR VOC AND CO, ALL T/YR LIMITS ARE FOR BOTH BOILERS COMBINED. THESE LIMITS FOR THE NATURAL GAS. |  | Sulfur Dioxide (SO2) | N |  | 1.6 | LB/MMBTU |  | SIP | 2758 | T/YR | BOTH BOILERS TOGETHER, PER ROLLING 12-MO | 1.6 | LB/MMBTU
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | AUXILLIARY NAT. GAS FIRED BOILER (B25, S25) | 12.31 | NATURAL GAS | 229.8 | MMBTU/H | THE AUXILIARY BOILER WILL BE USED TO PREHEAT STEAM TURBINE, PROVIDE PLANT HEATING AND PROVIDE SUPPLEMENTAL STEAM TO AUXILIARY EQUIPMENT WHEN THE MAIN SCPC BOILER IS OFFLINE. THE AUXILIARY BOILER WILL BE PACKAGED BOILER THAT WILL COMBUST ONLY NATURAL GAS. THE HOURS OF THE OPERATION OF THE AUXILIARY BOILER WILL BE LIMITED TO 2,000 HOURS IN ANY 12 CONSECUTIVE MONTHS. |  | Sulfur Dioxide (SO2) | P | NATURAL GAS | 0.0006 | LB/MMBTU | 2000 H / 12 MO. ROLLING LIMIT | NSPS | 0.14 | LB/H
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | VACUUM CRUDE CHARGE HEATER | 12.39 | REFINERY FUEL GAS OR NG | 101 | MMBTU/H | THIS UNIT IS IDENTIFIED BY EQUIPMENT ID # B-02100 |  | Sulfur Dioxide (SO2) | N |  | 35 | PPMV | DAILY AVERAGE | NSPS | [5 empty] | NOT AVAILABLE | THIS LIMIT IS FOR SULFUR, AS H2S, AND IS A LIMIT ON THE INLET CONCENTRATION OF THE REFINERY FUEL GAS.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | HYDROCRACKER UNIT MAIN FRACTIONATOR HEATER | 12.39 | REFINERY FUEL GAS OR NG | 211 | MMBTU/H | THIS UNIT IS IDENTIFIED BY EQUIPMENT ID # B-10500 |  | Sulfur Dioxide (SO2) | P | S LIMITED TO 35 PPM. | 35 | PPMV | DAILY AVERAGE | NSPS | [5 empty] | NOT AVAILABLE | THIS LIMIT ON SULFUR, AS H2S, IS A RESTRICTION ON THE INLET CONCENTRATION OF THE REFINERY FUEL GAS.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT CHARGE HEATER | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 122 | MMBTU/H | THIS UNIT IS IDENTIFIED BY EQUIPMENT ID # B-05110 |  | Sulfur Dioxide (SO2) | P | SULFUR LIMITED TO 35 PPM IN FUEL. | 35 | PPMV | DAILY AVERAGE | NSPS | [5 empty] | NOT AVAILABLE | THE 35 PPMV SULFUR LIMIT, AS H2S, IS A RESTRICTION ON THE INLET CONCENTRATION OF THE REFINERY FUEL GAS BEING FIRED IN THE UNIT.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT INTERHEATER NO. 1 | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 192 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY EQUIPMENT ID # B-05120 |  | Sulfur Dioxide (SO2) | P | S LIMITED TO 35 PPM. | 35 | PPMV | DAILY AVERAGE | NSPS | [5 empty] | NOT AVAILABLE | THE 35 PPMV SULFUR LIMIT, AS H2S, IS A RESTRICTION ON THE INLET CONCENTRATION OF THE REFINERY FUEL GAS BEING FIRED IN THE UNIT.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | CATALYTIC REFORMING UNIT INTERHEATER NO. 2 | 12.39 | REFINERY FUEL GAS OR NATURAL GAS | 129 | MMBTU/H | THIS EQUIPMENT IS IDENTIFIED BY ID # B-05130 |  | Sulfur Dioxide (SO2) | P | S LIMITED TO 35 PPM. | 35 | PPMV | DAILY AVERAGE | NSPS | [5 empty] | NOT AVAILABLE | THIS SULFUR LIMIT, AS H2S, IS A LIMIT ON THE INLET CONCENTRATION OF THE REFINERY FUEL GAS.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | DISTILLATE HYDROTREATER SPLITTER REBOILER | 12.39 | REFINERY FUEL GAS OR NATURAL GAS | 117 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY ID # B-08509 |  | Sulfur Dioxide (SO2) | P | S LIMITED TO 35 PPM. | 35 | PPMV | DAILY AVERAGE | NSPS | [5 empty] | NOT AVAILABLE | THIS SULFUR LIMIT, AS H2S, IS A LIMIT ON THE INLET CONCENTRATION OF THE REFINERY FUEL GAS.
AZ-0046 | ARIZONA CLEAN FUELS YUMA | ARIZONA CLEAN FUELS YUMA LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2005-04-14 | 2005 | OIL REFINERY | BUTANE CONVERSION UNIT ISOSTRIPPER REBOILER | 12.39 | REFINERY FUEL GAS AND NATURAL GAS | 222 | MMBTU/H | THIS EQUIPMENT IDENTIFIED BY ID # B-15110 |  | Sulfur Dioxide (SO2) | P | SULFUR LIMITED TO 35 PPM IN FUEL BURNED. | 35 | PPMV | DAILY AVERAGE | NSPS | [5 empty] | NOT AVAILABLE | THIS SULFUR LIMIT, AS H2S, IS A LIMIT ON THE INLET CONCENTRATION OF THE REFINERY FUEL GAS.
TX-0478 | CITGO CORPUS CHRISTI REFINERY - WEST PLANT | CITGO REFINING AND CHEMICALS COMAPNY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-04-20 | 2005 |  | MIXED DISTILLATE HYDROHEATER REBOILER HEATER | 12.39 | REFINERY FUEL GAS | 82 | MMBTU/H | THE MDH UNIT REMOVES ORGANIC NITROGEN AND SULFUR FROM THE FEED STREAMS. FEEDSTOCK IS MIXED WITH HYDROGEN , HEATED, AND FED TO A REACTOR. A CATALYTIC REACTION CONVERTS THE ORGANIC SULFUR TO HYDROGEN SULFIDE AND THE NITROGEN COMPOUNDS TO AMMONIA. THE EFFLUENT STREAM IS COOLED AND EXCESS HYDROGEN REMOVED FOR RECYCLE. HYDROGEN SULFIDE IS REMOVED FROM THE HYDROGEN STREAM BY AN AMINE ABSORBER AND ROUTED TO THE SRU. NEW EQUIPMENT UNDER THE AMENDMENT INCLUDES A SECOND REACTOR, ADDITIONAL PREHEAT TRAIN, AN ADDITIONAL REACTOR PRODUCT FLASH DRUM, A HYDROGEN PURIFICATION MEMBRANE AND AN ADDITIONAL HYDROGEN MAKEUP COMPRESSOR. AS PART OF THE AMENDMENT, THE FRACTIONATOR REBOILER WILL BE RETROFIT WITH LOW NOX BURNERS. |  | Sulfur Dioxide (SO2) | N |  | 5.7 | LB/H |  |  | 25 | T/YR
TX-0492 | VIRTEX PETROLEUM COMPANY DOERING RANCH GAS PLANT | VIRTEX PETROLEUM INC. | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-05 | 2005 | VIRTEX CURRENTLY OPERATES A GAS PLANT WHICH IS AUTHORIZED UNDER AN OIL AND GAS STANDARD PERMIT. THE MAXIMUM PRODUCTION IS CURRENTLY AUTHORIZED AT 0.3 LONG TONS PER DAY OF SULFUR. THEY ARE REQUESTING AUTHORIZATION TO MODIFY THE EXISTING FACILITY TO PROCESS SOUR GAS FROM NEW FIELD WELLS AND INCREASE MAXIMUM PRODUCTION TO 0.75 LONG TONS PER DAY OF SULFUR (4.0 MMSDFD OF GAS WITH AN H2S CONTENT OF 8.000 PPM). MODIFICATIONS INCLUDE THE INSTALLATION OF NEW COMPRESSORS, AUTHORIZING AN AMINE SWEETENING UNIT, A LARGER CAPACITY GLYCOL DEHYDRATOR, AND ALL ASSOCIATED PIPING. THE INCREASE IN SO2 REQUIRES PSD ANALYSIS. | 1.8 MMBTU AMINE REBOILER | 12.39 | SWEET NATURAL GAS | 1.8 | MMBTU |  |  | Sulfur Dioxide (SO2) | N |  | 0.01 | LB/H |  |  | 0.01 | T/YR
TX-0475 | FORMOSA POINT COMFORT PLANT | FORMOSA PLASTICS CORPORATION TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-09 | 2005 |  | PYROLYSIS FURNACE (1010B) | 12.39 | FUEL GAS | 250 | MMBtu/H |  |  | Sulfur Dioxide (SO2) | N |  | 0.41 | LB/H |  | N/A | 1.78 | T/YR
TX-0475 | FORMOSA POINT COMFORT PLANT | FORMOSA PLASTICS CORPORATION TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-09 | 2005 |  | REBOILER (1 AND 2) | 12.39 | FUEL GAS | 250 | MMBtu |  |  | Sulfur Dioxide (SO2) | N |  | 0.02 | LB/H |  | N/A | 0.1 | T/YR
*TX-0499 | SANDY CREEK ENERGY STATION | SANDY CREEK ENERGY ASSOCIATES | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-07-24 | 2006 | THE PROPOSED SCES IS A GRASSROOTS NEW, 860 MW GROSS (800 MW NET) ELECTRIC OUTPUT, PC BOILER STEAM ELECTRIC GENERATING FACILITY. THE MAXIMUM HEAT INPUT IS 8,185 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTU/HR). ONLY PRELIMINARY ENGINEERING DESIGN HAS BEEN COMPLETED AT THIS TIME AND THE PERMIT APPLICATION NET PLANT EFFICIENCY OF 10,231 BTU/KWHR (HEAT ENERGY INPUT DIVIDED BY NET ELECTRIC ENERGY OUTPUT) WILL NOT BE FINALIZED UNTIL PROJECT FUNDING IS COMPLETE. THE BOILER MAY BE DESIGNED AS A SUBCRITICAL STEAM PRESSURE UNIT, OR A MORE EFFICIENT, HIGHER PRESSURE, SUPERCRITICAL STEAM UNIT. THE ELECTRIC GENERATING PROCESS IS THE STANDARD RANKINE CLOSED CYCLE: BOILER FEEDWATER IS PUMPED, CONVERTED TO STEAM IN THE BOILER, PASSED THROUGH STEAM TURBINES WHICH TURN ELECTRIC GENERATORS, AND CONDENSED IN WATER-COOLED CONDENSERS TO AGAIN BECOME BOILER FEEDWATER. HEAT IS REMOVED FROM THE TURBINE CONDENSERS VIA A WET COOLING TOWER WHICH EVAPORATES TO THE ATMOSPHERE WATER OBTAINED FROM WACO’S MUNICIPAL WASTE WATER TREATMENT FACILITY. | AUXILLARY BOILER | 12.31 | NATURAL GAS | 175 | MMBTU/H |  |  | Sulfur Dioxide (SO2) | N |  | 0.11 | LB/H
*TX-0496 | INEOS CHOCOLATE BAYOU FACILITY | INEOS USA LLC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-08-29 | 2006 | THE NO. 1 AND NO. 2 OLEFINS UNITS USE PYROLYSIS FURNACES TO CRACK FEEDSTOCKS INTO LOW MOLECULAR WEIGHT HYDROCARBONS THAT CONTAIN OLEFINS. PRODUCTS ARE ETHYLENE, PROPYLENE, PYROLYSIS GASOLINE, CRUDE C4, FUEL OIL, AND HYDROGEN. FEED FOR THE OLEFINS CRACKING FURNACES IS EITHER GAS FEED (ETHANE-RICH OR PROPANE-RICH FEED) OR LIQUID FEED (REFINERY RAFFINATE AND DEBUTANIZED NATURAL GASOLINE (DNG). THE LIQUID FEEDSTOCKS ARE STORED PRIOR TO PROCESSING IN LARGE FLOATING-ROOF TANKS EQUIPPED WITH SECONDARY SEALS. ETHYLENE PRODUCT IS TRANSFERRED OFF-SITE BY PIPELINE. PROPYLENE IS SHIPPED VIA RAILCAR, BARGE, OR SENT TO AN EXISTING POLYPROPYLENE UNIT AT THE CHOCOLATE BAYOU PLANT FOR FURTHER PROCESSING. CRUDE C4 STOCK IS SENT TO THE BUTADIENE EXTRACTION UNIT (BEU) TO PRODUCE HIGH PURITY BUTADIENE WHICH IS SOLD. BUTADIENE PRODUCT IS SHIPPED OFF-SITE VIA RAILCAR OR BARGE. THE RAW PYROLYSIS GASOLINE IS FURTHER HYDROTREATED TO PYROLYSIS GASOLINE PRODUCT FOR SHIPMENT OFF SITE | FURNACE EMISSION CAPS | 12.39 |  |  |  | EMISSION CAPS FOR FURNACES ARE NOT CHANGED IN THIS PERMIT ACTION. SPECIAL CONDITION NO. 13 IS CHANGED TO CLARIFY BACT SHALL BE DEMONSTRATED FOR EACH NEW FURNACE (EQUIPPED WITH SCR) AND ALLOW EXCEPTION WHEN THE UNIT IS IN DECOKING. SPECIAL CONDITION NO. 51 IS CHANGED TO ALLOW BACT FOR OLD FURNACES TO BE DEMONSTRATED AT THE LEVELS WHEN THE FLEXIBLE PERMIT WAS ISSUED. COMBUSTION STAFF WAS CONSULTED AND CONCURRED WITH THE CHANGE. |  | Sulfur Dioxide (SO2) | N |  | 61.37 | LB/H |  |  | 13.44 | T/YR
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | A & B VACUUM TOWER HEATERS (3-08 & 4-08) | 12.39 | REFINERY FUEL GAS | 155.2 | MMBTU/H EA. |  |  | Sulfur Dioxide (SO2) | N | USE OF LOW SULFUR REFINERY FUEL GAS |  |  |  | OPERATING PERMIT |  |  |  | 25 | PPMV AS H2S | ANNUAL AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | NAPHTHA HYDROTREATER STRIPPER REBOILER HEATER (6-08) & KHT STRIPPER REBOILER HEATER (10-08) | 12.39 | REFINERY FUEL GAS |  |  | 6-08: 138.4 MMBTU/H 10-08: 121.8 MMBTU/H |  | Sulfur Dioxide (SO2) | N | USE OF LOW SULFUR REFINERY FUEL GAS |  |  |  | OPERATING PERMIT |  |  |  | 25 | PPMV AS H2S | ANNUAL AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | SATS GAS PLANT HOT OIL HEATER (14-08) | 12.39 | REFINERY FUEL GAS | 183.3 | MMBTU/H |  |  | Sulfur Dioxide (SO2) | N | USE OF LOW SULFUR REFINERY FUEL GAS |  |  |  | OPERATING PERMIT |  |  |  | 25 | PPMV AS H2S | ANNUAL AVERAGE
*LA-0213 | ST. CHARLES REFINERY | VALERO REFINING - NEW ORLEANS, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2007-02-08 | 2007 | PETROLEUM REFINERY. PROJECT INVOLVES INCREASE IN CAPACITY FROM 220,000 TO 380,000 BARRELS PER DAY. | REBOILER 2005-18 & HEATERS F-15-02 (6-81), 2005-14, 2005-17, 2005-29, 2005-32, & 2005-37 | 12.39 | REFINERY FUEL GAS |  |  | 6-81: 135 MM BTU/HR 2005-14: 195 MM BTU/HR 2005-17: 159 MM BTU/HR 2005-18: 231 MM BTU/HR 2005-29: 195 MM BTU/HR 2005-32: 159 MM BTU/HR 2005-37: 173 MM BTU/HR SOURCES ALSO FIRE NATURAL GAS. |  | Sulfur Dioxide (SO2) | N | USE OF PIPELINE QUALITY NATURAL GAS OR REFINERY FUEL GASES WITH AN H2S CONCENTRATION LESS THAN 100 PPMV (ANNUAL AVERAGE). |  |  | SEE NOTE | OPERATING PERMIT | [6 empty] | NO EMISSION LIMITS
*IA-0089 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-08-08 | 2007 | 170 MILLION GALLON PER ROLLING 12-MONTH PERIOD DRY MILL ETHANOL PLANT. THE PROCESS WILL USE GASIFICATION TECHNOLOGY TO PRODUCE SYNGAS AS THE SOURCE FOR ENERGY. WILL USE 60,714,286 BUSHELS OF CORN PER ROLLING 12-MONTH PERIOD PRODUCING EITHER 1.411 MILLION TONS OF WDGS OR 552,500 TONS OF DDGS PER ROLLING 12-MONTH PERIOD. THE GASIFICATION PROCESS COULD USE UP TO 298, 213 TONS OF COAL PER ROLLING 12-MONTH PERIOD. PROJECT NUMBER (PN) 06-672, 28 PERMITS ISSUED | THERMAL OXIDIZER FOR HRSG FROM DRYERS AND GASIFICATION - TWO SYSTEMS, S10 AND S11 (07-A-955P AND 07-A-956P) | 12.3 | SYNGAS | 250 | MM BTU / hr | THE THERMAL OXIDIZER IS 150 MM BTU / HR AND EACH DRYER (TWO TOTAL FOR THIS EMISSION POINT) IS 50 MM BTU / HR. |  | Sulfur Dioxide (SO2) | P | H2S REMOVAL SYSTEM AFTER THE GASIFICATION PROCESS AND PRIOR TO THE USE IN THE DRYERS OR THERMAL OXIDIZERS | 0.034 | LB/MMBTU | 30-DAY ROLLING, BACT OVERALL SO2 | OTHER | 0.014 | LB/MMBTU | 30-DAY ROLLING AVERAGE, BACT FOR SYN GAS | 0.2 | LB/MMBTU | 30-DAY ROLLING, NSPS | FOR THE SYN-GAS MADE FROM COAL, THE SO2 IS LIMITED TO 0.014 LB / MM BTU AND THE SO2 FROM THE PROCESS IS LIMITED TO 0.02 LB / MM BTU EACH BASED ON 250 MM BTU / HR HEAT INPUT.
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Sulfur Dioxide (SO2) | N |  | 0.0006 | LB/MMBTU |  |  | 0.1 | LB/H |  |  |  |  | THIS COVERS SO2 FOR THE NATURAL GAS-FIRED REHEAT FURNACE (LA 21).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Sulfur Dioxide (SO2) | N |  | 0.0006 | LB/MMBTU |  |  | 0.004 | LB/H |  |  |  |  | THIS COVERS SO2 FOR THE 3 COIL DRUM FURNACES (LA24-LA26).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Sulfur Dioxide (SO2) | N |  | 0.0006 | LB/MMBTU |  |  | 0.01 | LB/H |  |  |  |  | THIS COVERS SO2 FOR THE PLATE ANNEALING FURNACE (LA27).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS -FIRED ANNEALING FURNACE (LA43) (MULTIPLE EMISSION POINTS) | 12.31 | NATURAL GAS | 196.4 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X016: SULFURIC ACID PICKLING WITH CAUSTIC SCRUBBER (LA46) - RBLC PROCESS CODE - 81.290 PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Sulfur Dioxide (SO2) | N |  | 0.0006 | LB/MMBTU |  |  | 0.12 | LB/H |  |  |  |  | THIS COVERS SO2 FOR THE NATURAL GAS-FIRED ANNEALING FURNACE (LA43).
*NM-0050 | ARTESIA REFINERY | NAVAJO REFINING COMPANY LLC | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2007-12-14 | 2007 | 115,000 - 125,000 BBL/DAY NOMINALLY RATED PETROLEUM REFINERY. | ROSE 2 HOT OIL HEATER | 12.3 | REFINERY FUEL GAS | 120 | mmbtu/hr |  |  | Sulfur Dioxide (SO2) | P | REFINERY FUEL GAS SULFUR REMOVAL | 60 | PPMV | 365-DAY ROLLING AVERAGE | NSPS | 160 | PPMV | HOURLY MAXIMUM |  |  |  | THIS SULFUR LIMIT, AS H2S, IS A LIMIT ON THE INLET CONCENTRATION OF THE REFINERY FUEL GAS.
CA-1024 | AES HUNTINGTON BEACH | AES HUNTINGTON BEACH | CA | SOUTH COAST AQMD, CA | 2002-08-01 | 2002 |  | BOILER: >= 50 MMBTU/HR | 12.31 | NATURAL GAS | 225 | MW | EQUIP: ELECTRIC UTILITY BOILER, MFR: BABCOCK & WILCOX, TYPE: MULTI-WALL FIRED, MODEL: , FUNC EQUIP: USE IS CURRENTLY FOR PEAK POWER DEMAND PERIODS, FUEL_TYPE: , SCHEDULE: VARIABLE, H/D: 24, D/W: 5, W/Y: 20, NOTES: FACILITY APPLIED TO BRING THIS RETIRED BOILER BACK INTO SERVICE. FACILITY IS EXPERIENCING DIFFICULTY MEETING NOX AND AMMONIA LIMITS ON ONE- HOUR AVERAGING BASIS, AND DISTRICT IS CONSIDERING REQUEST FOR LONGER AVERAGING TIME. SOURCE TEST RESULTS: PPM@3%O2, GR/DSCF: 225 MW: NOX-3.5, CO-0.0, VOC- 4.2, NH3-3.1, PM-.001. 169 MW: NOX-4.2, NH3-1.6, PM-.002. 115MW: NOX-3.8, NH3-0.5. 90 MW: NOX-4.5, NH3-0.7, PM-.004 |  | Sulfur Oxides (SOx) | N | SULFUR IN FUEL | 0.2 | LB/MMBTU |  | N/A |  |  |  | 0.2 | LB/MMBTU
NC-0101 | FORSYTH ENERGY PLANT | FORSYTH ENERGY PROJECTS, LLC | NC | FORSYTH COUNTY ENV AFFAIRS DEPT, NC | 2005-09-29 | 2005 | THREE COMBINED-CYCLE COMBUSTION TURBINE GENERATORS, EACH WITH A HEAT RECOVERY STEAM GENERATORS (HRSG) ALONG WITH NATURAL GAS-FIRED DUCT BURNERS TO MEET PEAK DEMAND. THE STEAM GENERATED THROUGH THE THREE HRSGS WILL DRIVE A STEAM TURBINE. THE ENTIRE PLANT WILL BE CAPABLE OF GENERATING A NOMINAL POWER OUTPUT OF 812 MEGAWATTS. | AUXILLIARY BOILER | 12.31 | NATURAL GAS | 110.2 | MMBTU/H |  |  | Sulfur Oxides (SOx) | P | LOW-NOX BURNERS, GOOD COMBUSTION CONTROL AND CLEAN BURNING, LOW-SULFUR FUEL (NATURAL GAS). | 0.61 | LB/H | based on 3-hour average |  |  |  |  | 0.0055 | LB/MMBTU | calculated
MN-0035 | LSP - COTTAGE GROVE, L.P. | LSP - COTTAGE GROVE, L.P. | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 1998-11-10 | 1998 |  | BOILERS, AUXILIARY, 2, NAT GAS | 12.31 | NATURAL GAS | 114 | MMBTU/H (NAT GAS) | A SEPARETLY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING FUEL OIL. |  | Sulfuric Acid (mist, vapors, etc) | P | NATURAL GAS LIMIT AND DISTILLATE FUEL OIL LIMIT. | 0 | LB/MMBTU | [5 empty] | 0
TX-0386 | AMELLA ENERGY CENTER | CALPINE CONSTRUCTION FINANCE CO. LP | TX | CITY OF HOUSTON BUREAU AIR QUAL CTRL, TX | 2002-03-26 | 2002 |  | AUXILIARY BOILER | 12.31 | NATURAL GAS | 155 | MMBTU/H |  |  | Sulfuric Acid (mist, vapors, etc) | N |  | 0.129 | LB/H
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | AUXILLIARY NAT. GAS FIRED BOILER (B25, S25) | 12.31 | NATURAL GAS | 229.8 | MMBTU/H | THE AUXILIARY BOILER WILL BE USED TO PREHEAT STEAM TURBINE, PROVIDE PLANT HEATING AND PROVIDE SUPPLEMENTAL STEAM TO AUXILIARY EQUIPMENT WHEN THE MAIN SCPC BOILER IS OFFLINE. THE AUXILIARY BOILER WILL BE PACKAGED BOILER THAT WILL COMBUST ONLY NATURAL GAS. THE HOURS OF THE OPERATION OF THE AUXILIARY BOILER WILL BE LIMITED TO 2,000 HOURS IN ANY 12 CONSECUTIVE MONTHS. |  | Sulfuric Acid (mist, vapors, etc) | P | NATURAL GAS | 0.021 | LB/H | 2000 H / 12 MO. ROLLING LIMIT | [7 empty] | REGULATED POLLUTANT IS SULFURIC ACID MIST.
OR-0046 | TURNER ENERGY CENTER, LLC | CALPINE | OR | OREGON DEPT OF ENVIRONMENTAL QUALITY | 2005-01-06 | 2005 | 620 MW TOTAL COMBINED CYCLE GAS TURBINES (2 TURBINES WITH HRSGS) | AUXILIARY BOILER | 12.31 | NATURAL GAS | 417904 | MMBTU/YR | BOILER USED TO PROVIDE AUXILIARY STEAM FOR STANDBY AND STARTUP CONDITIONS WILL BE OPERATED A MAXIMUM OF 3000 HOURS/YR. |  | Sulfuric Acid (mist, vapors, etc) | N | USE OF NATURAL GAS |  |  | SEE NOTE | [7 empty] | REGULATED POLLUTANT IS SULFURIC ACID MIST. USE OF NATURAL GAS IS RACT.
*IA-0089 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-08-08 | 2007 | 170 MILLION GALLON PER ROLLING 12-MONTH PERIOD DRY MILL ETHANOL PLANT. THE PROCESS WILL USE GASIFICATION TECHNOLOGY TO PRODUCE SYNGAS AS THE SOURCE FOR ENERGY. WILL USE 60,714,286 BUSHELS OF CORN PER ROLLING 12-MONTH PERIOD PRODUCING EITHER 1.411 MILLION TONS OF WDGS OR 552,500 TONS OF DDGS PER ROLLING 12-MONTH PERIOD. THE GASIFICATION PROCESS COULD USE UP TO 298, 213 TONS OF COAL PER ROLLING 12-MONTH PERIOD. PROJECT NUMBER (PN) 06-672, 28 PERMITS ISSUED | THERMAL OXIDIZER FOR HRSG FROM DRYERS AND GASIFICATION - TWO SYSTEMS, S10 AND S11 (07-A-955P AND 07-A-956P) | 12.3 | SYNGAS | 250 | MM BTU / hr | THE THERMAL OXIDIZER IS 150 MM BTU / HR AND EACH DRYER (TWO TOTAL FOR THIS EMISSION POINT) IS 50 MM BTU / HR. |  | Sulfuric Acid (mist, vapors, etc) | N |  | 1.6 | LB/H | [8 empty] | LIMIT ESTABLISHED FOR FACILITY TO STAY SYNTHETIC MINOR FOR NESHAP / MACT APPLICABLILITY
NJ-0041 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-10-08 | 1997 |  | DUCT BURNER ONLY | 12.31 | NATURAL GAS | 234 | MMBTU/H | TOTAL NATURAL GAS BURNED IN THE HEAT RECOVERY BOILER SHALL NOT EXCEED 1153.2 MILLION CUBIC FEET PER CALENDAR YEAR |  | Total Suspended Particulates | P | LOW NOX BURNER | 5.2 | LB/H |  |  | 0.022 | LB/MMBTU |  | 0.022 | LB/MMBTU
NJ-0043 | LIBERTY GENERATING STATION | LIBERTY GENERATING STATION | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2002-03-28 | 2002 | ELECTRICITY GENERATION | AUXILIARY BOILER | 12.31 | NATURAL GAS | 200 | MMBTU/H | NATURAL GAS USAGE RESTRICTED TO 181.0 MILLION SCF/YR (EQUIVALENT TO A 10% ANNUAL CAPACITY FACTOR) |  | Total Suspended Particulates | N |  | 1.6 | LB/H | [5 empty] | 0.008 | LB/MMBTU |  | BASIS OF LIMIT IS STATE.
PA-0231 | UNITED REFINERY CO. | UNITED REFINERY CO | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2003-10-09 | 2003 | THE MODIFICATIONS INCLUDE THE INSTALLATION OF THREE NEW SOURCES AND MODS TO EXISTING SOURCES, THIS PERMIT ACTION IS SUBJECT TO SUBPARTS J,GGG QQQ OF THE NSPS, MACT SUBPARTS CC AND UUU AND NESHAPS SUBPARTS FF AND IS PSD FOR CO. | DELAYED COKER UNIT, HEATER | 12.39 | REFINERY GAS | 116 | MMBTU/H | The unit is subject to the NSPS 40 CFR Subpart J, Subpart GGG, Subpart QQQ. The unit is also subject to MACT standards in 40 CFR 63 Subpart CC, and NESHAP requirements in 40 CFR 61 Subpart FF. |  | Total Suspended Particulates | P | SPRAY CHAMBER, GOOD COMBUSTION PRACTICE | 0.75 | LB/H |  |  | 3.3 | T/YR |  | 0.0065 | LB/MMBTU | Calculated using heat input | Best available technology (BAT) review done.
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, NAT GAS | 12.31 | NATURAL GAS | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Visible Emissions (VE) | A |  | 10 | % OPACITY | [5 empty] | 10 | % OPACITY
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, HYDROGEN | 12.39 | HYDROGEN | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Visible Emissions (VE) | A |  | 10 | % OPACITY | [5 empty] | 10 | % OPACITY
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, COMBINED FUEL (NAT GAS/HYDROGEN) | 12.39 | NAT GAS/HYDRO COMBO | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Visible Emissions (VE) | A |  | 10 | % OPACITY | [5 empty] | 10 | % OPACITY
SC-0075 | NUCOR STEEL- DARLINGTON COUNTY | NUCOR STEEL CORPORATION | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 1998-01-08 | 1998 | STEEL MILL | REHEAT FURNACE #1 | 12.31 | NATURAL GAS | 140 | MMBTU/H | MAIN FUEL IS NATURAL GAS, PROPANE AS A BACK-UP. UTILIZES LOW NOX BURNERS. NATURAL GAS AND PROPANE USAGE IS RESTRICTED TO AN EQUIVALENT OF 1150 X MMSCF PER YEAR AT ESTABLISHED BTU CONTENTS OF 1000 BTU/CF AND 90500 BTU/GALLON RESPECTIVELY. SUBJECT TO PSD. |  | Visible Emissions (VE) | N | NONE INDICATED | 20 | % OPACITY | [5 empty] | 20 | % OPACITY
SC-0075 | NUCOR STEEL- DARLINGTON COUNTY | NUCOR STEEL CORPORATION | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 1998-01-08 | 1998 | STEEL MILL | REHEAT FURNACE #2 | 12.31 | NATURAL GAS | 125 | MMBTU/H | NATURAL GAS IS MAIN FUEL, PROPANE AS BACK UP. UTILIZES LOW NOX BURNERS AND EXTERNAL FLUE GAS RECIRCULATION. NATURAL GAS AND PROPANE USAGE IS RESTRICTED TO AN EQUIVALENT OF 1095 MMSCF PER YEAR AS ESTABLISHED BTU CONTENTS OF 1000 BTU/CF AND 90500 BTU/GAL RESPECTIVELY. SUBJECT TO PSD. |  | Visible Emissions (VE) | N |  | 20 | % OPACITY | [5 empty] | 20 | % OPACITY
TX-0259 | FREEPORT COGENERATION FACILITY | BASF CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-06-26 | 1998 | CONSTRUCTION OF A COGENERATION UNIT | BOILER, B-20A | 12.39 | H2 WASTE & NAT GAS | 213 | MMBTU/H | HYDROGEN WASTE GAS AND PIPELINE QUALITY, SWEET NAT GAS CONTAINING NO >0.25 GR H2S AND 5 GR TOTAL S/100 DSCF. SCC CODE FOR NATURAL GAS CHOSEN FOR THE PURPOSE OF THIS DATABASE. |  | Visible Emissions (VE) | N | NONE INDICATED | 20 | % OPACITY | 6 MIN AVER | SIP |  |  |  | 20 | % OPACITY | 6 MIN AVER
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | 1998 | VEGETABLE OIL PLANT | BOILER, TRANE MURRAY, NAT GAS | 12.31 | NATURAL GAS | 189 | MMBTU/H | No add-on controls. See separate process for backup fuel (No. 2 oil) requirements. |  | Visible Emissions (VE) | N |  | 20 | % OPACITY | [5 empty] | 20 | % OPACITY
OH-0245 | REPUBLIC TECHNOLOGIES INTERNATIONAL | REPUBLIC TECHNOLOGIES INTERNATIONAL/CANTON | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 1999-01-27 | 1999 | STEEL MILL. THIS PLANT IS PSD FOR PM, SO2, NOX, CO, AND VOC. THIS MODIFICATION IS A SIGNIFICANT INCREASE FOR NOX. | BLOOM REHEAT FURNACE | 12.31 | NATURAL GAS | 196.2 | MMBTU/H | STACK TEST 0.0489 LB NOX/HR |  | Visible Emissions (VE) | A | BAGHOUSE | 5 | % OPACITY | 6 minute average | SIP |  |  |  | 5 | % OPACITY | 6 minute average
AK-0037 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFIDE CONTENT TO 0.01% FROM 0.001%, AN INCREASE IN OPERATING HOURS OF P708C FROM 200 TO 600 HOURS PER YEAR, THE REMOVAL OF PERCENT EFFICIENCY REQUIREMENTS FOR AS1310 AND 1320, AND USE OF THERMAL OXIDATION TO CONTROL EMISSIONS FROM AS1320. | CRUDE HEATER, H101A | 12.39 | NATURAL GAS* | 140 | MMBTU/H | INSTALLED PRIOR TO 1975, THEREFORE NOT REQUIRED TO COMPLY WITH THE PSD PROGRAM. DESIGN CAPACITY OF 140.0 MMBTU/H AUTHORIZED RATED CAPACITY IS 1 MMBTU/H. *FUELS ARE NATURAL GAS, REFINERY GAS AND LPG. NO INDICATION IS PROVIDED AS TO WHICH IS THE PRIMARY FUEL. |  | Visible Emissions (VE) | N | NONE INDICATED | 20 | % OPACITY | EXCEPT FOR 3 MINUTES IN AN ANY ONE HOUR | SIP |  |  |  | 20 | % OPACITY | EXCEPT FOR 3 MINUTES IN AN ANY ONE HOUR | SOURCE IS SUBJECT TO STATE EMISSION LIMITS FOR VE.
AK-0037 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFIDE CONTENT TO 0.01% FROM 0.001%, AN INCREASE IN OPERATING HOURS OF P708C FROM 200 TO 600 HOURS PER YEAR, THE REMOVAL OF PERCENT EFFICIENCY REQUIREMENTS FOR AS1310 AND 1320, AND USE OF THERMAL OXIDATION TO CONTROL EMISSIONS FROM AS1320. | CRUDE HEATER, H101B | 12.39 | NATURAL GAS* | 165 | MMBTU/H | DESIGN CAPACITY IS 165.0 MMBTU/H BUT AUTHORIZED RATED CAPACITY IS 1 MMBTU/H. *SOURCE BURNS COMBINATION OF REFINERY GAS, NATURAL GAS, AND LIQUID PETROLEUM GAS. IT IS NOT SPECIFIIED WHICH TYPE OF FUEL IS PRIMARY. |  | Visible Emissions (VE) | N | NONE INDICATED. | 20 | % OPACITY | EXCEPT FOR 3 MINUTES IN ANY ONE HOUR | SIP |  |  |  | 20 | % OPACITY | EXCEPT FOR 3 MINUTES IN ANY ONE HOUR | ALL SOURCES ARE SUBJECT TO VE LIMITATIONS BY THE STATE OF ALASKA.
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BOILER NO. 12 | 12.39 |  | 245 | MMBTU/H | EMISSION PT NO: BOILER-12. SHALL BE SHUTDOWN. |  | Visible Emissions (VE) | N | NONE INDICATED | 5 | % OPACITY |  | SIP |  |  |  | 5 | % OPACITY
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BTU-NO. 1 REACTOR FEED HEATER | 12.39 |  | 121.74 | MMBTU/H | EMISSION POINT NO. BTU-HF103. |  | Visible Emissions (VE) | N | NONE INDICATED | 5 | % OPACITY |  | SIP |  |  |  | 5 | % OPACITY
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ISOM II WEST REACTOR FEED HEATER | 12.39 |  | 104.25 | MMBTU/H | EMISSION POINT NO. BTU-HF106. |  | Visible Emissions (VE) | N | NONE INDICATED | 5 | % OPACITY |  | SIP |  |  |  | 5 | % OPACITY
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ORTHOXYLENE II HEATER | 12.39 |  | 226.42 | MMBTU/H | EMISSION POINT NO.: ORTHOII-H2. |  | Visible Emissions (VE) | N |  | 5 | % OPACITY |  | SIP |  |  |  | 5 | % OPACITY
VA-0278 | VCU EAST PLANT | Virginia Commonwealth University | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-31 | 2003 | STEAM GENERATING PLANT AT UNIVERSITY | BOILER, NATURAL GAS, (3) | 12.31 | NATURAL GAS | 150.6 | MMBTU/H | Throughput for each. The 3 boilers shall consume no more than 3,500 million cf of natural gas per year |  | Visible Emissions (VE) | N |  | 10 | % OPACITY |  |  | 20 | % OPACITY | 6-min period per hour | 10 | % OPACITY
WV-0023 | MAIDSVILLE | LONGVIEW POWER, LLC | WV | WEST VIRGINIA AIR POLLUTION CONTROL COMM | 2004-03-02 | 2004 | PULVERIZED COAL-FIRED STEAM GENERATOR CAPABLE OF GENERATING 600MW OF ELECTRIC POWER. THIS FACILITY IS A GREEN FIELD SITE, WHICH INCLUDES A 6,114 MMBTU COAL-FIRED BOILER, 225 MMBTU NATURAL GAS-FIRED AUX BOILER, EMERGENCY GENERATOR, FIRE WATER PUMP ENGINE, COOLING TOWERS, AND MATERIAL HANDLING SYSTEMS. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 225 | mmbtu/h | LIMITED TO NATURAL GAS USE AND 3,000 HOURS OF OPERATION PER YEAR |  | Visible Emissions (VE) | P | CLEAN FUELS AND GOOD COMBUSTION PRACTICES | 10 | % OPACITY |  | SIP |  |  |  | 10 | % OPACITY |  | LIMITED TO USE OF NATURAL GAS AND 3,000 HOURS OF OPERATION PER YEAR
NE-0024 | CARGILL - BLAIR PLANT | CARGILL, INC. | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2004-06-22 | 2004 | WET CORN MILLING, ETHANOL, FRUCTOSE, CORN OIL, CLUTEN MEAL AND OTHER CORN BY- PRODUCTS. | BOILERS A, B & C | 12.31 | NATURAL GAS | 198 | MMBTU/H |  |  | Visible Emissions (VE) | N |  | 20 | % OPACITY | [5 empty] | 20 | % OPACITY
*IA-0089 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-08-08 | 2007 | 170 MILLION GALLON PER ROLLING 12-MONTH PERIOD DRY MILL ETHANOL PLANT. THE PROCESS WILL USE GASIFICATION TECHNOLOGY TO PRODUCE SYNGAS AS THE SOURCE FOR ENERGY. WILL USE 60,714,286 BUSHELS OF CORN PER ROLLING 12-MONTH PERIOD PRODUCING EITHER 1.411 MILLION TONS OF WDGS OR 552,500 TONS OF DDGS PER ROLLING 12-MONTH PERIOD. THE GASIFICATION PROCESS COULD USE UP TO 298, 213 TONS OF COAL PER ROLLING 12-MONTH PERIOD. PROJECT NUMBER (PN) 06-672, 28 PERMITS ISSUED | THERMAL OXIDIZER FOR HRSG FROM DRYERS AND GASIFICATION - TWO SYSTEMS, S10 AND S11 (07-A-955P AND 07-A-956P) | 12.3 | SYNGAS | 250 | MM BTU / hr | THE THERMAL OXIDIZER IS 150 MM BTU / HR AND EACH DRYER (TWO TOTAL FOR THIS EMISSION POINT) IS 50 MM BTU / HR. |  | Visible Emissions (VE) | N |  | 0 | % | SIX MINUTE AVERAGE
IN-0075 | GRAIN PROCESSING CORP. | GRAIN PROCESSING CORP. | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1997-06-10 | 1997 |  | BOILERS NO. 1 & 2 | 12.39 | NATURAL GAS/ALCOHOL | 244 | MMBTU/H (EACH) | STACK TEST REQUIRED BY PERMIT, NOT YET CONSTRUCTED. BOILER NO.1 (UP51A), BOILER NO.2 (UP51B). |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 1.82 | T/YR (EACH) | [7 empty] | NOT AVAILABLE
NJ-0041 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-10-08 | 1997 |  | DUCT BURNER ONLY | 12.31 | NATURAL GAS | 234 | MMBTU/H | TOTAL NATURAL GAS BURNED IN THE HEAT RECOVERY BOILER SHALL NOT EXCEED 1153.2 MILLION CUBIC FEET PER CALENDAR YEAR |  | Volatile Organic Compounds (VOC) | N | REFLECTS NO CONTROLS FEASIBLE" FOR LACK OF OTHER INFO." | 8.4 | LB/H |  |  | 27 | PPMVD @ 15% O2 |  | 0.036 | LB/MMBTU
LA-0114 | ST. JAMES STYRENE PLANT | CHEVRON CHEMICAL COMPANY | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1997-12-10 | 1997 | MODIFICATION TO THE EXISTING STYRENE PRODUCTION FACILITY | SUPERHEATER | 12.31 | NATURAL GAS | 165 | MMBTU/H |  |  | Volatile Organic Compounds (VOC) | P | PROPER OPERATING TECHNIQUES WITH AUTOMATIC CONTROLS, 3% EXCESS O2 | 0.004 | LB/MMBTU | [5 empty] | 0.004 | LB/MMBTU
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, NAT GAS | 12.31 | NATURAL GAS | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Volatile Organic Compounds (VOC) | A |  | 1 | LB/H | [7 empty] | NOT AVAILABLE
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, HYDROGEN | 12.39 | HYDROGEN | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Volatile Organic Compounds (VOC) | A |  | 1.7 | LB/H
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | BOILER, COMBINED FUEL (NAT GAS/HYDROGEN) | 12.39 | NAT GAS/HYDRO COMBO | 190 | MMBTU/H | NATURAL GAS IS PRIMARY FUEL WITH FUEL OIL, USED OIL AND HYDROGEN BACKUP. SEPARATELY LISTED PROCESSES SHOW EMISSION LIMITS WHEN FIRING ALTERNATIVE FUELS. |  | Volatile Organic Compounds (VOC) | A |  | 1.7 | LB/H
AL-0115 | ALABAMA POWER COMPANY | ALABAMA POWER COMPANY | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-12-17 | 1997 |  | DUCT BURNER | 12.39 | NAT GAS/HYDROGEN | 260 | MMBTU/H |  |  | Volatile Organic Compounds (VOC) | P |  | 3.4 | LB/H
MO-0051 | PROCTOR & GAMBLE PAPER PRODUCTS | Proctor & Gamble Paper Products | MO | MISSOURI DNR, AIR POLL CONTROL PROGRAM | 1998-01-01 | 1998 | SANITARY TISSUE & TOWEL BUSINESS, EXPANSION TO EXISTING DIAPER MANUFACTURING PLANT | BOILERS, NATURAL GAS, (3) | 12.31 | NATURAL GAS | 1095 | MMCF/YR | ADDITIONAL THROUGHPUT INFORMATION: 125 MMBTU/H, EACH. |  | Volatile Organic Compounds (VOC) | P | LOW NOX FUEL, W/O FLUE GAS RECIRC.,GOOD COMBUSTION | 0.052 | LB/MMBTU | [5 empty] | 0.052 | LB/MMBTU
TX-0259 | FREEPORT COGENERATION FACILITY | BASF CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-06-26 | 1998 | CONSTRUCTION OF A COGENERATION UNIT | BOILER, B-20A | 12.39 | H2 WASTE & NAT GAS | 213 | MMBTU/H | HYDROGEN WASTE GAS AND PIPELINE QUALITY, SWEET NAT GAS CONTAINING NO >0.25 GR H2S AND 5 GR TOTAL S/100 DSCF. SCC CODE FOR NATURAL GAS CHOSEN FOR THE PURPOSE OF THIS DATABASE. |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.3 | LB/H |  |  | 1.31 | T/YR
TX-0237 | PORT ARTHUR REFINERY | FINA OIL AND CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-09-08 | 1998 | CHEMICAL AND OIL COMPANY, 2.2 BILLION LB/YR ETHYLENE CRACKING UNIT & ASSOCIATED FACILITIES. LOCATED AT INTERSECTION OF HWY 366 & 32ND ST. | DUCT BURNERS (2) | 12.31 | NATURAL GAS | 310.4 | MMBTU/H |  |  | Volatile Organic Compounds (VOC) | P | LOW NOX BURNERS | 0.01 | LB/MMBTU
TX-0237 | PORT ARTHUR REFINERY | FINA OIL AND CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-09-08 | 1998 | CHEMICAL AND OIL COMPANY, 2.2 BILLION LB/YR ETHYLENE CRACKING UNIT & ASSOCIATED FACILITIES. LOCATED AT INTERSECTION OF HWY 366 & 32ND ST. | BOILER, SUPPLEMENTAL, STEAM | 12.31 | NATURAL GAS | 227 | mmbtu/h | THIS SUPPLEMENTAL STEAM BOILER IS PART OF THE COGENERATION PACKAGE INCLUDING 2 COMBINED CYCLE TURBINES AND 2 DUCT BURNERS. |  | Volatile Organic Compounds (VOC) | P | LOW-NOX BURNERS | 0.007 | LB/MMBTU
TX-0305 | PARIS GENERATING STATION | PANDA PARIS LLC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-10-28 | 1998 | PANDA PARIS, LLC, PROPOSES TO CONSTRUCT A NATURAL GAS-FIRED COMBINED- CYCLE POWER GENERATION FACILITY TO BE KNOWN AS THE PARIS GENERATING STATION, LOCATED IN LAMAR COUNTY. THE PROPOSED FACILITY WILL CONSIST OF FOUR 170 MW GENERAL ELECTRIC 7241FA COMBUSTION TURBINES AND ASSOCIATED HEAT RECOVERY STEAM GENERATORS WITH 200 MMBTU/H DUCT BURNERS EACH. THE TURBINES AND DUCT BURNERS WILL BE FIRED WITH PIPELINE NAT GAS. PROCESS STEAM FROM THE HRSGS WILL BE USED TO GENERATE ADDITIONAL ELECTRICITY FROM TWO 160 MW STEAM TURBINES. THE COMBINED UNITS WILL HAVE A NOMINAL CAPACITY OF 1000 MW. THERE WILL BE TWO 2000 DIESEL FUEL- FIRED BLACK START EMERGENCY GENERATORS, ONE 400 KW DIESEL FUEL- FIRED EMERGENCY ELECTRICAL GENERATOR TO PROVIDE GENERAL SITE POWER, ONE 260- HP DIESEL FUEL-FIRED EMERGENCY FIRE WATER PUMP AND ANCILLARY EQUIPMENT INCLUDING RAW AND DEMINERALIZED WATER STORAGE TANKS. A LETTER DATED AUGUST 20, 1998 FROM THE COMPANY'S CONSULTANT (ECT) ALSO REQUESTED THESE DIESEL- FIRED ENGINES BE EXEMPT UNDER 30 TAC SECTION 106.511 AND 106.512 AND NOT HAVE THEM INCLUDED IN THIS PERMIT. | (4) DUCT BURNERS | 12.31 | NAT GAS | 200 | MMBTU/H, EA | THE TOTAL ANNUAL HEAT INPUT TO ALL DUCT BURNERS SHALL NOT EXCEED 3,200,000 MMBTU FOR THE FACILITY SITE. |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION DESIGN AND OPERATIONS | 0.01 | LB/MMBTU | EACH UNIT
MN-0035 | LSP - COTTAGE GROVE, L.P. | LSP - COTTAGE GROVE, L.P. | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 1998-11-10 | 1998 |  | BOILERS, AUXILIARY, 2, NAT GAS | 12.31 | NATURAL GAS | 114 | MMBTU/H (NAT GAS) | A SEPARETLY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING FUEL OIL. |  | Volatile Organic Compounds (VOC) | P | NATURAL GAS LIMIT AND DISTILLATE FUEL OIL LIMIT. | 0.005 | LB/MMBTU | [5 empty] | 0.005 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 4 (NAT GAS) | 12.31 | NATURAL GAS | 118 | MMBTU/H | MFR. IS BABCOCK & WILCOX. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Volatile Organic Compounds (VOC) | N | NONE LISTED | 0.2 | LB/H |  |  | 3.1 | PPMVD @ 7% O2 |  | 0.002 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 2 (NAT GAS) | 12.31 | NATURAL GAS | 134 | MMBTU/H | MFR. IS COMBUSTION ENGINEERING. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Volatile Organic Compounds (VOC) | N | NONE LISTED | 0.2 | LB/H |  |  | 2.7 | PPMVD @ 7% O2 |  | 0.001 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 3 (NAT GAS) | 12.31 | NATURAL GAS | 152 | MMBTU/H | MFR. IS BABCOCK & WILCOX. ONLY NATURAL GAS AND NO. 2 OIL SHALL BE FIRED IN THIS BOILER. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. |  | Volatile Organic Compounds (VOC) | N | NONE LISTED | 0.2 | LB/H |  |  | 2.4 | PPMVD @ 7% O2 |  | 0.001 | LB/MMBTU
AL-0128 | ALABAMA POWER COMPANY - THEODORE COGENERATION | ALABAMA POWER COMPANY - THEODORE COGENERATION | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1999-03-16 | 1999 |  | BOILER | 12.31 | NATURAL GAS | 220 | MMBTU/H |  |  | Volatile Organic Compounds (VOC) | P | EFFICIENT COMBUSTION | 0.005 | LB/MMBTU |  |  | 36.3 | LB/H |  | 0.005 | LB/MMBTU
TX-0414 | ATOFINA PETROCHEMICALS PORT ARTHUR COMPLEX | FINA OIL & CHEMICAL COPMANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1999-04-22 | 1999 | FACILITY WANTS TO INSTALL A COGENERATION FACILITY CONSISTING OF 2 TURBINES AND SUPPLEMENTAL BOILER TO SUBSTITUTE FOR 2 AUXILIARY STEAM BOILERS | SUPPLEMENTAL BOILER | 12.31 | NATURAL GAS | 227 | MMBTU/H | BOILER PRODUCES AS MUCH AS 150,000 LB/H OF STEAM. |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICE | 1.59 | LB/H |  |  | 1.89 | T/YR |  |  |  |  | ADDITIONAL LIMIT: .007 LB/MMBTU
AR-0026 | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1999-05-05 | 1999 | COMBUSTION TURBINE COMBINED CYCLE COGENERATION FACILITY | DUCT BURNER | 12.31 | NATURAL GAS | 315 | MMBTU/H | TURBINE AND DUCT BURNER EMISSIONS COMBINED IN ONE STACK. DUCT BURNER ALWAYS FIRES NATURAL GAS. |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICE | 0.019 | LB/MMBTU | [5 empty] | 0.019 | LB/MMBTU
AR-0026 | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | PINE BLUFF ENERGY LLC - PINE BLUFF ENERGY CENTER | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1999-05-05 | 1999 | COMBUSTION TURBINE COMBINED CYCLE COGENERATION FACILITY | BOILER, NATURAL GAS | 12.31 | NATURAL GAS | 362 | MMBTU/H | BOILER FIRES NATURAL GAS AND FUEL OIL. BOILER WILL PROVIDE STEAM FOR STEAM TURBINE AND INTERNATIONAL PAPER MILL. |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.002 | LB/MMBTU | [5 empty] | 0.002 | LB/MMBTU
TX-0294 | GATEWAY POWER PROJECT | GATEWAY POWER PROJECT LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-03-20 | 2000 | THIS IS A GRASS-ROOTS ELECTRICAL GENERATION FACILITY. THE PRIMARY EQUIPMENT CONSISTS OF THREE COMBUSTION TURBINES DRIVING ELECTRICAL GENERATORS, WHERE EACH GENERATOR IS RATED NOMINALLY AT 170 MW. THE TURBINES OPERATE IN COMBINED CYCLE MODE IN WHICH A SUPPLEMENTARY FIRED HEAT RECOVERY STEAM GENERATOR (HRSG) WILL BE UTILIZED. THE ASSOCIATED DUCT BURNERS WILL EACH HAVE A MAXIMUM RATING OF 290 MMBTU/H HEAT INPUT. THE TURBINES AND DUCT BURNERS WILL BE FIRED WITH PIPELINE-QUALITY NAT GAS ONLY. PROCESS STEAM FROM THE HRSGS WILL BE USED BY THREE STEAM TURBINES TO GENERATE UP TO 90 MW ADDITIONAL ELECTRICITY EACH. THE THREE COMBINED CTG-HRSG UNITS WILL HAVE A NOMINAL CAPACITY OF 800 MW. | (3) DUCT BURNERS | 12.31 | NAT GAS | 160 | MMBTU/H, EA | PERMIT INDICATES STANDARD EMISSION LIMITS FOR NOX, CO, AND VOC SEPARATELY FOR THIS PROCESS, HOWEVER THEY ARE CONSIDERED AS A COMBINED PROCESS WITH THE TURBINES. |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION DESIGN AND OPERATIONS | 0.012 | LB/MMBTU | EACH UNIT
TX-0395 | DIAMOND SHAMROCK MCKEE PLANT | DIAMOND SHAMROCK REFINING COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-05-23 | 2000 |  | NO. 1 REFORMER CHARGE HEATER | 12.39 | REFINERY GAS | 248 | MMBTU/H |  |  | Volatile Organic Compounds (VOC) | N |  | 0.98 | LB/H |  |  | 4.26 | T/YR
TX-0395 | DIAMOND SHAMROCK MCKEE PLANT | DIAMOND SHAMROCK REFINING COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-05-23 | 2000 |  | NO 1 INTERHEATER | 12.39 | REFINERY GAS | 147.2 | MMBTU/H |  |  | Volatile Organic Compounds (VOC) | N |  | 0.58 | LB/H |  |  | 2.53 | T/YR
TN-0146 | FLORIM, USA, INC. | FLORIM, USA, INC. | TN | TENNESSEE DIV OF AIR POLLUTION CONTROL | 2000-12-20 | 2000 | CERAMIC TILE MANUFACTURING PROCESS CONSISTING OF RAW MATERIAL HANDLING, SPRAY DRYING, TILE PREPARATION, AND TILE FIRING OPERATIONS. THE COMPANY APPLIED FOR A PSD PERMIT TO INCREASE THE MATERIAL INPUT RATE THROUGH THE FACILITY'S TILE KILNS. | GAS-FIRED KILNS | 12.31 | NATURAL GAS | 125 | MMBTU/H | Seven (7) gas-fired tile kilns and one (1) gas-fired trim kiln with lime injection/coated baghouse controls. |  | Volatile Organic Compounds (VOC) | N |  | 0.192 | LB/MMBTU |  |  | 23.96 | LB/H |  | 0.192 | LB/MMBTU |  | The facility must meet compliance with production limits and recordkeeeping requirements to demonstrate compliance with emission limits.
TX-0339 | BAYTOWN OLEFINS PLANT | EXXON MOBIL CHEMICAL COMPANY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-04-05 | 2001 | THE COMPANY PROPOSES TO ADD A NEW CRACKING FURNACE, FURNACE XGF-01, AND RELATED EQUIPMENT AT THE BAYTOWN OLEFINS PLANT (BOP). THE NEW FURNACE WILL ALLOW THE COMPANY TO INCREASE ETHYLENE PRODUCTION. THIS WILL BE EMISSION POINT NUMBER XGF-01-ST. THE AUTHORIZED FIRING RATE WILL BE 481 MMBTU/H ON A ROLLING 12 MONTH AVERAGE, AND 502 MMBTU/H MAXIMUM HOURLY FIRING RATE. THE ADDITION OF THE NEW FURNACE TRIGGERED PSD REVIEW. | FURNACE HF-01 | 12.39 | ETHANE | 238 | MMBTU/H | 200 MMBTU/H AVE. FEEDSTOCK FOR THE FURNACES IS USUALLY ETHANE OR A 70%/30% THEANE/PROPANE MIXTURE. |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 0.3 | LB/H |  |  | 1.2 | T/YR
IN-0085 | PSEG LAWRENCEBURG ENERGY FACILITY | PSEG LAWRENCEBURG ENERGY FACILITY | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-06-07 | 2001 |  | AUXILIARY BOILER, NATURAL GAS | 12.31 | NATURAL GAS | 124.6 | MMBTU/H | AUXILIARY BOILER IS LIMITED TO 1000 H/YR OF OPERATION |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION. NATURAL GAS ONLY | 0.0054 | LB/MMBTU |  |  | 0.672 | LB/H |  | 0.0054 | LB/MMBTU
OK-0045 | REDBUD POWER PLT | REDBUD ENERGY LP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-15 | 2001 | ELECTRICAL GENERATION FACILITY | BOILER, AUXILIARY | 12.31 | NATURAL GAS | 20 | MMBTU/H | boiler operates < 3000 hours per year |  | Volatile Organic Compounds (VOC) | P | GOOD OPERATING PRACTICES | 0.005 | LB/MMBTU
AR-0057 | TENASKA ARKANSAS PARTNERS, LP | TENASKA ARKANSAS PARTNERS, LP | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-10-09 | 2001 | ELECTRIC POWER GENERATING STATION. FACILITY WAS NEVER CONSTRUCTED AND THE PERMIT WAS VOIDED 1/07/03. ADDITIONAL PLANTWIDE EMISSIONS: PM10 858 T/YR, AMMONIA 844 T/YR. | BOILER, NATURAL GAS, (2) | 12.31 | NATURAL GAS | 122 | MMBTU/H | Throughput for each boiler. |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES. | 0.004 | LB/MMBTU | [5 empty] | 0.004 | LB/MMBTU
AR-0055 | NUCOR YAMATO STEEL (ARMOREL) | NUCOR YAMATO STEEL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-10-10 | 2001 | STEEL MILL. | REHEAT FURNACE | 12.31 | NATURAL GAS | 225 | MMBTU/H |  |  | Volatile Organic Compounds (VOC) | P | CLEAN FUELS | 0.0054 | LB/MMBTU | [5 empty] | 0.0054 | LB/MMBTU
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | 2001 | ELECTRICITY GENERATION | AUXILIARY BOILER | 12.31 | NATURAL GAS | 120 | MMBTU/H |  |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.48 | LB/H |  |  | 0.864 | T/YR |  |  |  |  | ADDITIONAL EMISSION LIMIT: 0.004 LB/MMBTU.
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BOILER NO. 12 | 12.39 |  | 245 | MMBTU/H | EMISSION PT NO: BOILER-12. SHALL BE SHUTDOWN. |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 1.32 | LB/H |  | NSPS | 5.79 | T/YR
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | BTU-NO. 1 REACTOR FEED HEATER | 12.39 |  | 121.74 | MMBTU/H | EMISSION POINT NO. BTU-HF103. |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 0.66 | LB/H |  | NSPS | 2.88 | T/YR
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ISOM II WEST REACTOR FEED HEATER | 12.39 |  | 104.25 | MMBTU/H | EMISSION POINT NO. BTU-HF106. |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 0.56 | LB/H |  | NSPS | 2.46 | T/YR
TX-0375 | LYONDELL - CITGO REFINING, LP | LYONDELL - CITGO REFINING, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-03-14 | 2002 | LYONDELL-CITGO PROPOSES TO CONSTRUCT NEW FACILITIES AND MODIFY EXISTING FACILITIES TO IMPLEMENT THEIR CLEAN AIR PROJECT, ENABLING THE FACILITY TO MANUFACTURE LOW SULFUR GASOLINE AND DIESEL FUEL IN COMPLIANCE WITH EPA AND STATE REGULATIONS. THE SCOPE OF THE PROJECT WILL INCLUDE THE CONSTRUCTION OF SEVERAL NEW TREATING UNITS, MODIFICATION OF EXISTING TREATING UNITS, INSTALLATION OF POLLUTION CONTROLS ON EXISTING EQUIPMENT, AND THE SHUTDOWN OF OTHER EQUIPMENT THAT CANNOT BE REASONABLY CONTROLLED TO MEET THE NEW NOX REQURIEMENTS DICTATED BY THE SIP. THIS CONTINUOUS CONSTRUCTION CAMPAIGN IS SCHEDULED TO CONTINUE UNTIL COMPLETION IN 2007. | ORTHOXYLENE II HEATER | 12.39 |  | 226.42 | MMBTU/H | EMISSION POINT NO.: ORTHOII-H2. |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 1.22 | LB/H |  | NSPS | 5.35 | T/YR
TX-0386 | AMELLA ENERGY CENTER | CALPINE CONSTRUCTION FINANCE CO. LP | TX | CITY OF HOUSTON BUREAU AIR QUAL CTRL, TX | 2002-03-26 | 2002 |  | AUXILIARY BOILER | 12.31 | NATURAL GAS | 155 | MMBTU/H |  |  | Volatile Organic Compounds (VOC) | N |  | 3.1 | LB/H
NJ-0043 | LIBERTY GENERATING STATION | LIBERTY GENERATING STATION | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2002-03-28 | 2002 | ELECTRICITY GENERATION | AUXILIARY BOILER | 12.31 | NATURAL GAS | 200 | MMBTU/H | NATURAL GAS USAGE RESTRICTED TO 181.0 MILLION SCF/YR (EQUIVALENT TO A 10% ANNUAL CAPACITY FACTOR) |  | Volatile Organic Compounds (VOC) | A | CO CATALYST | 50 | PPMVD @ 7% O2 |  |  | 1.6 | LB/H |  |  |  |  | BASIS OF LIMIT IS STATE. Calculated emission rate 0.008 LB/MMBTU
AR-0070 | GENOVA ARKANSAS I, LLC | GENOVA ARKANSAS I, LLC | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-08-23 | 2002 | COMBINED CYCLE POWER PLANT | DUCT BURNERS | 12.31 | NATURAL GAS | 200 | MMBTU/H | 2 DUCT BURNERS UNDER ANY SCENARIO. INFORMATION PROVIDED IS FOR EACH UNIT. |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICE | 0.06 | LB/MMBTU
VA-0270 | VCU EAST PLANT | VIRGINIA COMMONWEALTH UNIVERSITY | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-31 | 2003 |  | BOILER NATUAL GAS | 12.31 | NATURAL GAS | 150 | MMBTU/H | This is one of 3 boilers |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES. | 2.1 | LB\H | each unit
VA-0278 | VCU EAST PLANT | Virginia Commonwealth University | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-31 | 2003 | STEAM GENERATING PLANT AT UNIVERSITY | BOILER, NATURAL GAS, (3) | 12.31 | NATURAL GAS | 150.6 | MMBTU/H | Throughput for each. The 3 boilers shall consume no more than 3,500 million cf of natural gas per year |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICE | 2.1 | LB/H
WI-0204 | UWGP - FUEL GRADE ETHANOL PLANT | UNITED WISCONSIN GRAIN PRODUCERS | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2003-08-14 | 2003 | FERMENTATION BASED PROCESS WITH DISTILLATION, MOLECULAR SIEVES FOR FINAL WATER REMOVAL. ETHANOL DENATURED USING GASOLINE. | BOILER /OXIDIZER ( DRYER / DISTILLATION), P10 | 12.31 | NATURAL GAS | 140 | MMBTU/H | Boiler works as control device. RECEIVES VOC'S FROM DISTILLATION AND RELATED PROCESSES AND FROM Distillers dried grain with solubles (DDGS) DRYER (85 MMBTU/HR.). SUBJECT TO DB |  | Volatile Organic Compounds (VOC) | N | PROCESS IS THE CONTROL FOR OTHER SOURCES LISTED IN PROCESS ENTRY. | 6.7 | LB/H |  |  | 0.365 | LB /T | TON DDGS AT 11% MOISTURE |  |  |  | SYNTHETIC MINOR SOURCE. PROPOSED TO AVOID PSD / TITLE V MAJOR SOURCE STATUS. BOILER / OXIDIZER GENERATES STEAM AND CONSUMES VOC'S FROM DISTILLATION, DDGS DRYING AND OTHER OPERATIONS; EST. 99% DEST.; 98% OVERALL CONTROL.
LA-0197 | ALLIANCE REFINERY | CONOCOPHILLIPS CO | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2003-10-03 | 2003 | CLEAN FUELS PROJECT TO COMPLY WITH TIER 2 SULFUR STANDARDS. PROJECT INVOLVES CONSTRUCTION OF A CHARGE HEATER, A REBOILER, 3 INTERMEDIATE GASOLINE STORAGE TANKS, AND PIPING AND FUGITIVE COMPONENTS. ALSO, STEAM PRODUCTION FROM THE EXISTING BOILERS, COOLING TOWER RECIRCULATION RATE, SULFUR PRODUCTION AT THE SULFUR RECOVERY UNITS, AND WASTEWATER THROUGHPUT WILL ALSO INCREASE. | LOW SULFUR GASOLINE FEED HEATER NO. 1 | 12.39 | FUEL GAS | 138.12 | MMBTU/H | AVERAGE HEAT INPUT = 115.10 MMBTU/H |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES AND GOOD ENGINEERING DESIGN | 0.62 | LB/H | HOURLY MAXIMUM | OPERATING PERMIT | 2.72 | TYR | ANNUAL MAXIMUM |  |  |  | ADDITIONAL LIMIT: 0.0054 LB/MMBTU ANNUAL AVERAGE
PA-0231 | UNITED REFINERY CO. | UNITED REFINERY CO | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2003-10-09 | 2003 | THE MODIFICATIONS INCLUDE THE INSTALLATION OF THREE NEW SOURCES AND MODS TO EXISTING SOURCES, THIS PERMIT ACTION IS SUBJECT TO SUBPARTS J,GGG QQQ OF THE NSPS, MACT SUBPARTS CC AND UUU AND NESHAPS SUBPARTS FF AND IS PSD FOR CO. | DELAYED COKER UNIT, HEATER | 12.39 | REFINERY GAS | 116 | MMBTU/H | The unit is subject to the NSPS 40 CFR Subpart J, Subpart GGG, Subpart QQQ. The unit is also subject to MACT standards in 40 CFR 63 Subpart CC, and NESHAP requirements in 40 CFR 61 Subpart FF. |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICE | 0.545 | LB/H |  |  | 2.4 | T/YR |  |  |  |  | Best available technology (BAT) review done.
WV-0023 | MAIDSVILLE | LONGVIEW POWER, LLC | WV | WEST VIRGINIA AIR POLLUTION CONTROL COMM | 2004-03-02 | 2004 | PULVERIZED COAL-FIRED STEAM GENERATOR CAPABLE OF GENERATING 600MW OF ELECTRIC POWER. THIS FACILITY IS A GREEN FIELD SITE, WHICH INCLUDES A 6,114 MMBTU COAL-FIRED BOILER, 225 MMBTU NATURAL GAS-FIRED AUX BOILER, EMERGENCY GENERATOR, FIRE WATER PUMP ENGINE, COOLING TOWERS, AND MATERIAL HANDLING SYSTEMS. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 225 | mmbtu/h | LIMITED TO NATURAL GAS USE AND 3,000 HOURS OF OPERATION PER YEAR |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES AND USE OF NATURAL GAS | 0.0054 | LB/MMBTU | 3 HOUR ROLLING AVERAGE | NSPS | [6 empty] | LIMITED TO USE OF NATURAL GAS AND 3,000 HOURS OF OPERATION PER YEAR
OH-0241 | MILLER BREWING COMPANY - TRENTON | MILLER BREWING COMPANY | OH | HAMILTON CO-SOUTHWESTERN OH APCA | 2004-05-27 | 2004 | BEER BREWING AND PACKAGING. | BOILER (2), NATURAL GAS | 12.31 | NATURAL GAS | 238 | MMBTU/H | TWO BOILERS, CAPABLE OF BURNING AND WITH LIMITS FOR COAL, NATURAL GAS, NUMBERS 2 AND 6 FUEL OILS. POUND PER HOUR LIMITS ARE FOR EACH BOILER; AND EXCEPT FOR VOC AND CO, ALL T/YR LIMITS ARE FOR BOTH BOILERS COMBINED. THESE LIMITS FOR THE NATURAL GAS. |  | Volatile Organic Compounds (VOC) | N |  | 2.6 | LB/H | EACH BOILER | SIP | 11.5 | T/YR | EACH BOILER, ON A ROLLING 12-MO.
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | AUXILLIARY NAT. GAS FIRED BOILER (B25, S25) | 12.31 | NATURAL GAS | 229.8 | MMBTU/H | THE AUXILIARY BOILER WILL BE USED TO PREHEAT STEAM TURBINE, PROVIDE PLANT HEATING AND PROVIDE SUPPLEMENTAL STEAM TO AUXILIARY EQUIPMENT WHEN THE MAIN SCPC BOILER IS OFFLINE. THE AUXILIARY BOILER WILL BE PACKAGED BOILER THAT WILL COMBUST ONLY NATURAL GAS. THE HOURS OF THE OPERATION OF THE AUXILIARY BOILER WILL BE LIMITED TO 2,000 HOURS IN ANY 12 CONSECUTIVE MONTHS. |  | Volatile Organic Compounds (VOC) | P | NATURAL GAS, GOOD COMBUSTION PRACTICES, LOW NOX BURNERS | 0.0054 | LB/MMBTU | 2000 H / 12 MO. ROLLING |  | 1.24 | LB/H
LA-0194 | SABINE PASS LNG IMPORT TERMINAL | SABINE PASS LNG, LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2004-11-24 | 2004 | LNG TO BE TRANSFERRED FROM MARINE VESSELS INTO PRESSURIZED TANKS FOR STORAGE, THEN REGASIFIED USING VAPORIZERS. THE VAPORIZED NATURAL GAS WILL BE MEASURED AND SENT TO TRANSMISSION PIPELINES. | SUBMERGED COMBUSTION VAPORIZERS (24) | 12.31 |  | 108 | MMBTU/H |  |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES AND THE USE OF NATURAL GAS AS FUEL | 0.32 | LB/H | HOURLY MAXIMUM | OPERATING PERMIT | 1.42 | T/YR | ANNUAL MAXIMUM | 0.003 | LB/MMBTU
OR-0046 | TURNER ENERGY CENTER, LLC | CALPINE | OR | OREGON DEPT OF ENVIRONMENTAL QUALITY | 2005-01-06 | 2005 | 620 MW TOTAL COMBINED CYCLE GAS TURBINES (2 TURBINES WITH HRSGS) | AUXILIARY BOILER | 12.31 | NATURAL GAS | 417904 | MMBTU/YR | BOILER USED TO PROVIDE AUXILIARY STEAM FOR STANDBY AND STARTUP CONDITIONS WILL BE OPERATED A MAXIMUM OF 3000 HOURS/YR. |  | Volatile Organic Compounds (VOC) | A | OXIDATION CATALYST | 0.0044 | LB/MMBTU | 3-H BLOCK | [7 empty] | VOC AS METHANE.
TX-0478 | CITGO CORPUS CHRISTI REFINERY - WEST PLANT | CITGO REFINING AND CHEMICALS COMAPNY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-04-20 | 2005 |  | MIXED DISTILLATE HYDROHEATER REBOILER HEATER | 12.39 | REFINERY FUEL GAS | 82 | MMBTU/H | THE MDH UNIT REMOVES ORGANIC NITROGEN AND SULFUR FROM THE FEED STREAMS. FEEDSTOCK IS MIXED WITH HYDROGEN , HEATED, AND FED TO A REACTOR. A CATALYTIC REACTION CONVERTS THE ORGANIC SULFUR TO HYDROGEN SULFIDE AND THE NITROGEN COMPOUNDS TO AMMONIA. THE EFFLUENT STREAM IS COOLED AND EXCESS HYDROGEN REMOVED FOR RECYCLE. HYDROGEN SULFIDE IS REMOVED FROM THE HYDROGEN STREAM BY AN AMINE ABSORBER AND ROUTED TO THE SRU. NEW EQUIPMENT UNDER THE AMENDMENT INCLUDES A SECOND REACTOR, ADDITIONAL PREHEAT TRAIN, AN ADDITIONAL REACTOR PRODUCT FLASH DRUM, A HYDROGEN PURIFICATION MEMBRANE AND AN ADDITIONAL HYDROGEN MAKEUP COMPRESSOR. AS PART OF THE AMENDMENT, THE FRACTIONATOR REBOILER WILL BE RETROFIT WITH LOW NOX BURNERS. |  | Volatile Organic Compounds (VOC) | N |  | 0.44 | LB/H |  |  | 1.9 | T/YR
TX-0492 | VIRTEX PETROLEUM COMPANY DOERING RANCH GAS PLANT | VIRTEX PETROLEUM INC. | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-05 | 2005 | VIRTEX CURRENTLY OPERATES A GAS PLANT WHICH IS AUTHORIZED UNDER AN OIL AND GAS STANDARD PERMIT. THE MAXIMUM PRODUCTION IS CURRENTLY AUTHORIZED AT 0.3 LONG TONS PER DAY OF SULFUR. THEY ARE REQUESTING AUTHORIZATION TO MODIFY THE EXISTING FACILITY TO PROCESS SOUR GAS FROM NEW FIELD WELLS AND INCREASE MAXIMUM PRODUCTION TO 0.75 LONG TONS PER DAY OF SULFUR (4.0 MMSDFD OF GAS WITH AN H2S CONTENT OF 8.000 PPM). MODIFICATIONS INCLUDE THE INSTALLATION OF NEW COMPRESSORS, AUTHORIZING AN AMINE SWEETENING UNIT, A LARGER CAPACITY GLYCOL DEHYDRATOR, AND ALL ASSOCIATED PIPING. THE INCREASE IN SO2 REQUIRES PSD ANALYSIS. | 1.8 MMBTU AMINE REBOILER | 12.39 | SWEET NATURAL GAS | 1.8 | MMBTU |  |  | Volatile Organic Compounds (VOC) | N |  | 0.01 | LB/H |  |  | 0.04 | T/YR
TX-0475 | FORMOSA POINT COMFORT PLANT | FORMOSA PLASTICS CORPORATION TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-09 | 2005 |  | PYROLYSIS FURNACE (1010B) | 12.39 | FUEL GAS | 250 | MMBtu/H |  |  | Volatile Organic Compounds (VOC) | N |  | 2.31 | LB/H |  | N/A | 10.13 | T/YR
TX-0475 | FORMOSA POINT COMFORT PLANT | FORMOSA PLASTICS CORPORATION TEXAS | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2005-05-09 | 2005 |  | REBOILER (1 AND 2) | 12.39 | FUEL GAS | 250 | MMBtu |  |  | Volatile Organic Compounds (VOC) | N |  | 0.08 | LB/H |  | N/A | 0.36 | T/YR
NC-0101 | FORSYTH ENERGY PLANT | FORSYTH ENERGY PROJECTS, LLC | NC | FORSYTH COUNTY ENV AFFAIRS DEPT, NC | 2005-09-29 | 2005 | THREE COMBINED-CYCLE COMBUSTION TURBINE GENERATORS, EACH WITH A HEAT RECOVERY STEAM GENERATORS (HRSG) ALONG WITH NATURAL GAS-FIRED DUCT BURNERS TO MEET PEAK DEMAND. THE STEAM GENERATED THROUGH THE THREE HRSGS WILL DRIVE A STEAM TURBINE. THE ENTIRE PLANT WILL BE CAPABLE OF GENERATING A NOMINAL POWER OUTPUT OF 812 MEGAWATTS. | AUXILLIARY BOILER | 12.31 | NATURAL GAS | 110.2 | MMBTU/H |  |  | Volatile Organic Compounds (VOC) | P | LOW-NOX BURNERS, GOOD COMBUSTION CONTROL AND CLEAN BURNING, LOW-SULFUR FUEL (NATURAL GAS). | 0.59 | LB/H | based on 3-hour average
*TX-0499 | SANDY CREEK ENERGY STATION | SANDY CREEK ENERGY ASSOCIATES | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-07-24 | 2006 | THE PROPOSED SCES IS A GRASSROOTS NEW, 860 MW GROSS (800 MW NET) ELECTRIC OUTPUT, PC BOILER STEAM ELECTRIC GENERATING FACILITY. THE MAXIMUM HEAT INPUT IS 8,185 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTU/HR). ONLY PRELIMINARY ENGINEERING DESIGN HAS BEEN COMPLETED AT THIS TIME AND THE PERMIT APPLICATION NET PLANT EFFICIENCY OF 10,231 BTU/KWHR (HEAT ENERGY INPUT DIVIDED BY NET ELECTRIC ENERGY OUTPUT) WILL NOT BE FINALIZED UNTIL PROJECT FUNDING IS COMPLETE. THE BOILER MAY BE DESIGNED AS A SUBCRITICAL STEAM PRESSURE UNIT, OR A MORE EFFICIENT, HIGHER PRESSURE, SUPERCRITICAL STEAM UNIT. THE ELECTRIC GENERATING PROCESS IS THE STANDARD RANKINE CLOSED CYCLE: BOILER FEEDWATER IS PUMPED, CONVERTED TO STEAM IN THE BOILER, PASSED THROUGH STEAM TURBINES WHICH TURN ELECTRIC GENERATORS, AND CONDENSED IN WATER-COOLED CONDENSERS TO AGAIN BECOME BOILER FEEDWATER. HEAT IS REMOVED FROM THE TURBINE CONDENSERS VIA A WET COOLING TOWER WHICH EVAPORATES TO THE ATMOSPHERE WATER OBTAINED FROM WACO’S MUNICIPAL WASTE WATER TREATMENT FACILITY. | AUXILLARY BOILER | 12.31 | NATURAL GAS | 175 | MMBTU/H |  |  | Volatile Organic Compounds (VOC) | N |  | 0.7 | LB/H
*TX-0496 | INEOS CHOCOLATE BAYOU FACILITY | INEOS USA LLC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2006-08-29 | 2006 | THE NO. 1 AND NO. 2 OLEFINS UNITS USE PYROLYSIS FURNACES TO CRACK FEEDSTOCKS INTO LOW MOLECULAR WEIGHT HYDROCARBONS THAT CONTAIN OLEFINS. PRODUCTS ARE ETHYLENE, PROPYLENE, PYROLYSIS GASOLINE, CRUDE C4, FUEL OIL, AND HYDROGEN. FEED FOR THE OLEFINS CRACKING FURNACES IS EITHER GAS FEED (ETHANE-RICH OR PROPANE-RICH FEED) OR LIQUID FEED (REFINERY RAFFINATE AND DEBUTANIZED NATURAL GASOLINE (DNG). THE LIQUID FEEDSTOCKS ARE STORED PRIOR TO PROCESSING IN LARGE FLOATING-ROOF TANKS EQUIPPED WITH SECONDARY SEALS. ETHYLENE PRODUCT IS TRANSFERRED OFF-SITE BY PIPELINE. PROPYLENE IS SHIPPED VIA RAILCAR, BARGE, OR SENT TO AN EXISTING POLYPROPYLENE UNIT AT THE CHOCOLATE BAYOU PLANT FOR FURTHER PROCESSING. CRUDE C4 STOCK IS SENT TO THE BUTADIENE EXTRACTION UNIT (BEU) TO PRODUCE HIGH PURITY BUTADIENE WHICH IS SOLD. BUTADIENE PRODUCT IS SHIPPED OFF-SITE VIA RAILCAR OR BARGE. THE RAW PYROLYSIS GASOLINE IS FURTHER HYDROTREATED TO PYROLYSIS GASOLINE PRODUCT FOR SHIPMENT OFF SITE | FURNACE EMISSION CAPS | 12.39 |  |  |  | EMISSION CAPS FOR FURNACES ARE NOT CHANGED IN THIS PERMIT ACTION. SPECIAL CONDITION NO. 13 IS CHANGED TO CLARIFY BACT SHALL BE DEMONSTRATED FOR EACH NEW FURNACE (EQUIPPED WITH SCR) AND ALLOW EXCEPTION WHEN THE UNIT IS IN DECOKING. SPECIAL CONDITION NO. 51 IS CHANGED TO ALLOW BACT FOR OLD FURNACES TO BE DEMONSTRATED AT THE LEVELS WHEN THE FLEXIBLE PERMIT WAS ISSUED. COMBUSTION STAFF WAS CONSULTED AND CONCURRED WITH THE CHANGE. |  | Volatile Organic Compounds (VOC) | N |  | 23.63 | LB/H |  |  | 103.49 | T/YR
NV-0043 | LASCO BATHWARE | LASCO BATHWARE | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2006-10-25 | 2006 | A BATHWARE MANUFACTURING FACILITY | FUEL BURNING FOR THERMOSETTING | 12.31 | PROPANE | 6.3 | MMBTU/H | THERMOSETTING IS THE HEATING PROCESS TO HARDEN THE BATHROOM FIXTURES AFTER THEY ARE MOLDED INTO SHAPE. THERE ARE TWO HEATERS FOR EACH PRODUCTION LINE. ADDITIONALLY THERE ARE FIVE AIR HEATERS AT THE CURE TUNNEL. THE TOTAL HEAT INPUT CAPACITY FOR THE FUEL BURNING EQUIPMENT IS 27.56 MMBTU/HR. THE ANNUAL CONSUMPTION OF PROPANE FOR OPERATING THE FUEL BURNING EQUIPMENT IS LIMITED TO 662,645 GALLONS PER YEAR. MOST EMISSIONS COME FROM FUEL COMBUSTION, NOT FROM THE BATHROOM FIXTURES BEING HARDENED. THE EXHAUST OF THE HEATER DESIGNATED IN THE PERMIT AS A02 IS CHOSEN AS THE TYPICAL EMISSION UNIT FOR REPORTING THE PROCESS DATA. THIS HEATER IS SUBJECT TO THE LIMIT OF ANNUAL OPERATING TIME OF 2,200 HOURS PER YEAR. |  | Volatile Organic Compounds (VOC) | N | N/A | 0.03 | LB/H |  | SIP | 0.04 | T/YR
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | A & B VACUUM TOWER HEATERS (3-08 & 4-08) | 12.39 | REFINERY FUEL GAS | 155.2 | MMBTU/H EA. |  |  | Volatile Organic Compounds (VOC) | P | PROPER DESIGN, OPERATION, AND GOOD ENGINEERING PRACTICES |  |  |  | OPERATING PERMIT |  |  |  | 0.0015 | LB/MMBTU | 3-HOUR AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | NAPHTHA HYDROTREATER STRIPPER REBOILER HEATER (6-08) & KHT STRIPPER REBOILER HEATER (10-08) | 12.39 | REFINERY FUEL GAS |  |  | 6-08: 138.4 MMBTU/H 10-08: 121.8 MMBTU/H |  | Volatile Organic Compounds (VOC) | P | PROPER DESIGN, OPERATION, AND GOOD ENGINEERING PRACTICES |  |  |  | OPERATING PERMIT |  |  |  | 0.0015 | LB/MMBTU | 3-HOUR AVERAGE
*LA-0211 | GARYVILLE REFINERY | MARATHON PETROLEUM CO LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2006-12-27 | 2006 | PETROLEUM REFINERY. PROJECT INVOLVES ADDITION OF 8 NEW PROCESS UNITS, INCLUDING A 180,000 BBL/DAY CRUDE UNIT, TO INCREASE TOTAL REFINERY CAPACITY TO 425,000 BBL/DAY. | SATS GAS PLANT HOT OIL HEATER (14-08) | 12.39 | REFINERY FUEL GAS | 183.3 | MMBTU/H |  |  | Volatile Organic Compounds (VOC) | P | PROPER DESIGN, OPERATION, AND GOOD ENGINEERING PRACTICES |  |  |  | OPERATING PERMIT |  |  |  | 0.0015 | LB/MMBTU | 3-HOUR AVERAGE
*LA-0213 | ST. CHARLES REFINERY | VALERO REFINING - NEW ORLEANS, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2007-02-08 | 2007 | PETROLEUM REFINERY. PROJECT INVOLVES INCREASE IN CAPACITY FROM 220,000 TO 380,000 BARRELS PER DAY. | REBOILER 2005-18 & HEATERS F-15-02 (6-81), 2005-14, 2005-17, 2005-29, 2005-32, & 2005-37 | 12.39 | REFINERY FUEL GAS |  |  | 6-81: 135 MM BTU/HR 2005-14: 195 MM BTU/HR 2005-17: 159 MM BTU/HR 2005-18: 231 MM BTU/HR 2005-29: 195 MM BTU/HR 2005-32: 159 MM BTU/HR 2005-37: 173 MM BTU/HR SOURCES ALSO FIRE NATURAL GAS. |  | Volatile Organic Compounds (VOC) | P | PROPER EQUIPMENT DESIGN AND OPERATION, GOOD COMBUSTION PRACTICES, AND USE OF GASEOUS FUELS | 0.0054 | LB/MMBTU | ANNUAL AVERAGE | OPERATING PERMIT
*IA-0089 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | HOMELAND ENERGY SOLUTIONS, LLC, PN 06-672 | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-08-08 | 2007 | 170 MILLION GALLON PER ROLLING 12-MONTH PERIOD DRY MILL ETHANOL PLANT. THE PROCESS WILL USE GASIFICATION TECHNOLOGY TO PRODUCE SYNGAS AS THE SOURCE FOR ENERGY. WILL USE 60,714,286 BUSHELS OF CORN PER ROLLING 12-MONTH PERIOD PRODUCING EITHER 1.411 MILLION TONS OF WDGS OR 552,500 TONS OF DDGS PER ROLLING 12-MONTH PERIOD. THE GASIFICATION PROCESS COULD USE UP TO 298, 213 TONS OF COAL PER ROLLING 12-MONTH PERIOD. PROJECT NUMBER (PN) 06-672, 28 PERMITS ISSUED | THERMAL OXIDIZER FOR HRSG FROM DRYERS AND GASIFICATION - TWO SYSTEMS, S10 AND S11 (07-A-955P AND 07-A-956P) | 12.3 | SYNGAS | 250 | MM BTU / hr | THE THERMAL OXIDIZER IS 150 MM BTU / HR AND EACH DRYER (TWO TOTAL FOR THIS EMISSION POINT) IS 50 MM BTU / HR. |  | Volatile Organic Compounds (VOC) | A | THERMAL OXIDIZER | 0.006 | LB/MMBTU |  |  | 98 | % REDUCTION |  |  |  |  | THE FACILITY SHALL MEET EITHER THE 0.006 LB / MM BTU HEAT INPUT OR 98% REDUCTION.
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Volatile Organic Compounds (VOC) | N |  | 0.0055 | LB/MMBTU |  |  | 0.93 | LB/H |  |  |  |  | THIS COVERS VOC FOR THE NATURAL GAS-FIRED REHEAT FURNACE (LA 21).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Volatile Organic Compounds (VOC) | N |  | 0.0055 | LB/MMBTU |  |  | 0.033 | LB/H |  |  |  |  | THIS COVERS VOC FOR THE 3 COIL DRUM FURNACES (LA24-LA26).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED REHEAT FURNACE (LA21) (MULTIPLE EMISSION POINTS) | 12.3 | NATURAL GAS | 169 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X012: ROUGHING MILL WITH WET SCRUBBER & CYCLONE (LA22)- RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H FINISHING MILL WITH WET SCRUBBER & CYCLONE (LA23) - THROUGHPUT - 192 T/H 3 COIL DRUM FURNACES (LA24-LA26) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 6 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE ANNEALING FURNACE (LA27) - RBLC PROCESS CODE - 11.300; THROUGHPUT - 16.5 MMBTU/H; PRIMARY FUEL - NATURAL GAS PLATE SHOTBLASTER WITH BAGHOUSE (LA 28) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H NITRIC & HYDROFLUORIC ACID PICKLING WITH CAUSTIC SCRUBBER & DE-NOX SCR (LA29) - RBLC PROCESS CODE - 81.290; THROUGHPUT - 192 T/H PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Volatile Organic Compounds (VOC) | N |  | 0.0055 | LB/MMBTU |  |  | 0.091 | LB/H |  |  |  |  | THIS COVERS VOC FOR THE PLATE ANNEALING FURNACE (LA27).
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS -FIRED ANNEALING FURNACE (LA43) (MULTIPLE EMISSION POINTS) | 12.31 | NATURAL GAS | 196.4 | MMBTU/H | THIS PROCESS HAS MULTIPLE EMISSION POINTS, ALL OF WHICH ARE COVERED UNDER 503-0095-X016: SULFURIC ACID PICKLING WITH CAUSTIC SCRUBBER (LA46) - RBLC PROCESS CODE - 81.290 PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. |  | Volatile Organic Compounds (VOC) | N |  | 0.0055 | LB/MMBTU |  |  | 1.08 | LB/H |  |  |  |  | THIS COVERS VOC FOR THE NATURAL GAS-FIRED ANNEALING FURNACE (LA43).
*NM-0050 | ARTESIA REFINERY | NAVAJO REFINING COMPANY LLC | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2007-12-14 | 2007 | 115,000 - 125,000 BBL/DAY NOMINALLY RATED PETROLEUM REFINERY. | ROSE 2 HOT OIL HEATER | 12.3 | REFINERY FUEL GAS | 120 | mmbtu/hr |  |  | Volatile Organic Compounds (VOC) | P | GASEOUS FUEL COMBUSTION ONLY. | 0.005 | LB MMBTU | HOURLY
Year | NOX | # BACT Determinations | NOx, lb/mmbtu
1997 | 1.62 | 14 | 0.11571
1998 | 1.356 | 14 | 0.096857
1999 | 1.299 | 13 | 0.099923
2000 | 0.755 | 8 | 0.094375
2001 | 0.658 | 9 | 0.073111
2002 | 0.739 | 14 | 0.052786
2003 | 1.267 | 12 | 0.10558
2004 | 0.566 | 12 | 0.047167
2005 | 1.4316 | 17 | 0.084213
2006 | 0.37 | 6 | 0.061667
2007 | 0.0895 | 9 | 0.0099444
128

## Data- <100 MMBTU Solid Fuel
RBLCID | FACILITYNAME | CORPORATEORCOMPANYNAME | FACILITYSTATE | AGENCYNAME | PERMITDATE | FACILITYDESCRIPTION | PROCESSNAME | PROCTYPE | FUEL | THRUPUT | THRUPUTUNIT | PROCESSNOTES | POLLUTANT | CONTROLCOD | CTRLDESC | EMISLIMIT1 | EMISLIMIT1UNIT | EMISLIMIT1AVGTIMECONDITION | PCTEFFIC | EMISLIMIT2 | EMISLIMIT2UNIT | EMISLIMIT2AVGTIMECONDITION | STDEMISSLIMIT | STDUNITLIMIT | STDLIMITAVGTIMECONDITION | POLLUTANTCOMPLIANCENOTES
AL-0107 | WELLBORN CABINET INC | WELLBORN CABINET INC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1998-02-03 |  | BOILER, 2 | 13.12 | WOOD | 29.5 | MMBTU/H | WILL TEST COMPLIANCE BY TEST FOR NOX, CO, PM AND PM10 | Nitrogen Dioxide (NO2) | P | BOILER DESIGN AND COMBUSTION CONTROL: OXYGEN TRIM,STAGED COMBUSTION, STEAM INJECTION,AND OVERFIRE AIR. | 13.57 | LB/H |  | 31 | 0 |  |  | 0.23 | LB/MMBTU
AL-0107 | WELLBORN CABINET INC | WELLBORN CABINET INC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1998-02-03 |  | BOILER, 2 | 13.12 | WOOD | 29.5 | MMBTU/H | WILL TEST COMPLIANCE BY TEST FOR NOX, CO, PM AND PM10 | Nitrogen Dioxide (NO2) | P | BOILER DESIGN AND COMBUSTION CONTROL: OXYGEN TRIM,STAGED COMBUSTION, STEAM INJECTION,AND OVERFIRE AIR. | 13.57 | LB/H |  | 31 | 0 |  |  | 0.23 | LB/MMBTU
OH-0244 | DUKE SOLUTIONS EVENDALE LLC | Duke Energy | OH | HAMILTON CO-SOUTHWESTERN OH APCA | 1999-11-24 | STEAM AND ELECTRIC PRODUCING FACILITY | BOILER, WOOD WASTE | 13.12 | WOOD | 28.7 | MMBTU/H |  | Nitrogen Dioxide (NO2) | N |  | 0.604 | LB/MMBTU |  |  | 43.1 | T/YR |  | 0.604 | LB/MMBTU |  | The NOX emission rate from the stack test was 0.45 LB/MMBTU
OH-0244 | DUKE SOLUTIONS EVENDALE LLC | Duke Energy | OH | HAMILTON CO-SOUTHWESTERN OH APCA | 1999-11-24 | STEAM AND ELECTRIC PRODUCING FACILITY | BOILER, WOOD WASTE | 13.12 | WOOD | 28.7 | MMBTU/H |  | Nitrogen Dioxide (NO2) | N |  | 0.604 | LB/MMBTU |  |  | 43.1 | T/YR |  | 0.604 | LB/MMBTU |  | The NOX emission rate from the stack test was 0.45 LB/MMBTU
NC-0093 | GREENVILLE SAWMILL | WEYERHAEUSER COMPANY | NC | NORTH CAROLINA DIV OF ENV MGMT | 1997-09-26 | SAWMILL PRODUCING DIMENSION LUMBER FROM SOUTHERN YELLOW PINE | THERMAL OIL HEATER | 13.12 | WOODWASTE | 57.2 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | STAGED COMBUSTION | 0.25 | LB/MMBTU |  |  | 107 | T/YR |  | 0.25 | LB/MMBTU
NC-0093 | GREENVILLE SAWMILL | WEYERHAEUSER COMPANY | NC | NORTH CAROLINA DIV OF ENV MGMT | 1997-09-26 | SAWMILL PRODUCING DIMENSION LUMBER FROM SOUTHERN YELLOW PINE | THERMAL OIL HEATER | 13.12 | WOODWASTE | 57.2 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | STAGED COMBUSTION | 0.25 | LB/MMBTU |  |  | 107 | T/YR |  | 0.25 | LB/MMBTU
AL-0122 | GULF STATES PAPER CORP | GULF STATES PAPER CORP | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1998-10-14 |  | BOILER, WOOD FIRED | 13.12 | WOOD | 98 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 0.3 | LB/MMBTU |  | 0 | 29.4 | LB/H |  | 0.3 | LB/MMBTU
AL-0122 | GULF STATES PAPER CORP | GULF STATES PAPER CORP | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1998-10-14 |  | BOILER, WOOD FIRED | 13.12 | WOOD | 98 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 0.3 | LB/MMBTU |  | 0 | 29.4 | LB/H |  | 0.3 | LB/MMBTU
TX-0345 | DIBOLL PARTICLEBOARD OPERATION | TEMPLE-INLAND FOREST PRODUCTS CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-09-28 | TEMPLE-INLAND FOREST PRODUCTS CORP (TIFPC) OPERATES A PARTICLE BOARD PLANT. THE COMPANY REQUESTS THAT THE PERMITTED EMISSIONS RATES BE AMENDED TO MORE ACCURATELY REFLECT THE ACTUAL EMISSIONS AND PROPOSES TO INCREASE PRODUCTION THROUGH THE PARTICLEBOARD PLANT. IN ADDITION, THERE WILL BE CONTROL DEVICES ADDED TO THE DRYERS. FISCHER-KLOSTERMAN HIGH-EFFICIENCY CYCLONES WILL BE ADDED TO DRYERS 3 & 4. ALSO, A VALVELESS REGENERATIVE THERMAL OXIDIZER (VRTO) WILL FOLLOW THE PARTICULATE CONTROL DEVICE ON DRYER 3. NO VISIBLE FUGITIVE PARTICULATE EMISSIONS SHALL LEAVE THE PLANT PROPERTY. DISPOSAL OF ASH MUST BE ACCOMPLISHED IN A MANNER WHICH WILL PREVENT THE ASH FROM BECOMING AIRBORNE. THERE SHALL BE NO OUTSIDE STORAGE OF SAWDUST MATERIAL. IN ORDER TO MINIMIZE FUGITIVE DUST EMISSIONS, THE HOLDER OF THIS PERMIT SHALL PERIODICALLY CLEAN AND/OR WASH THE TRUCK DUMP AREA. ALL WOOD DUST AND WOOD WASTES COLLECTED FROM THESE AREAS SHALL BE PROPERLY HANDLED TO PREVENT RE-ENTRAINMENT OF WOOD DUST INTO THE AIR. THE BURNER COVERED BY THIS PERMIT SHALL NOT OPERATE UNLESS THE ASSOCIATED DRYER'S AIR POLLUTION ABATEMENT EQUIPMENT IS IN GOOD WORKING ORDER. IF PARTICULATE NUISANCE CONDITIONS OCCUR, ADDITIONAL CONTROLS MAY BE REQUIRED. FOR THE PURPOSE OF DETERMINING OPERATIONAL REQUIREMENTS OF THE PROPOSED PROJECT, THE PLANT MAY EXHAUST DRYER NO. 3 THROUGH THE PILOT CONTROL DEVICE. THE TESTING PROGRAM SHALL NOT CONTINUE BEYOND SIX MONTHS AFTER THE INITIAL STARTUP OF THE PILOT CONTROL DEVICE. | SANDER DUST BOILER, PB-44 | 13.12 | WOOD | 40 | MMBTU/H | FUEL: EITHER PIPELINE SWEET NAT GAS (SUPPLEMENTAL) CONTAINING NO MORE THAN 5 GR S AND 0.25 GR H2S /100 DSCF OR WOOD CONTAINING NO MORE THAN 5% MOISTURE. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 57.2 | LB/H |  |  | 250.5 | T/YR |  | 1.43 | LB/MMBTU |  | STANDARD EMISSIONS CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT
TX-0345 | DIBOLL PARTICLEBOARD OPERATION | TEMPLE-INLAND FOREST PRODUCTS CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-09-28 | TEMPLE-INLAND FOREST PRODUCTS CORP (TIFPC) OPERATES A PARTICLE BOARD PLANT. THE COMPANY REQUESTS THAT THE PERMITTED EMISSIONS RATES BE AMENDED TO MORE ACCURATELY REFLECT THE ACTUAL EMISSIONS AND PROPOSES TO INCREASE PRODUCTION THROUGH THE PARTICLEBOARD PLANT. IN ADDITION, THERE WILL BE CONTROL DEVICES ADDED TO THE DRYERS. FISCHER-KLOSTERMAN HIGH-EFFICIENCY CYCLONES WILL BE ADDED TO DRYERS 3 & 4. ALSO, A VALVELESS REGENERATIVE THERMAL OXIDIZER (VRTO) WILL FOLLOW THE PARTICULATE CONTROL DEVICE ON DRYER 3. NO VISIBLE FUGITIVE PARTICULATE EMISSIONS SHALL LEAVE THE PLANT PROPERTY. DISPOSAL OF ASH MUST BE ACCOMPLISHED IN A MANNER WHICH WILL PREVENT THE ASH FROM BECOMING AIRBORNE. THERE SHALL BE NO OUTSIDE STORAGE OF SAWDUST MATERIAL. IN ORDER TO MINIMIZE FUGITIVE DUST EMISSIONS, THE HOLDER OF THIS PERMIT SHALL PERIODICALLY CLEAN AND/OR WASH THE TRUCK DUMP AREA. ALL WOOD DUST AND WOOD WASTES COLLECTED FROM THESE AREAS SHALL BE PROPERLY HANDLED TO PREVENT RE-ENTRAINMENT OF WOOD DUST INTO THE AIR. THE BURNER COVERED BY THIS PERMIT SHALL NOT OPERATE UNLESS THE ASSOCIATED DRYER'S AIR POLLUTION ABATEMENT EQUIPMENT IS IN GOOD WORKING ORDER. IF PARTICULATE NUISANCE CONDITIONS OCCUR, ADDITIONAL CONTROLS MAY BE REQUIRED. FOR THE PURPOSE OF DETERMINING OPERATIONAL REQUIREMENTS OF THE PROPOSED PROJECT, THE PLANT MAY EXHAUST DRYER NO. 3 THROUGH THE PILOT CONTROL DEVICE. THE TESTING PROGRAM SHALL NOT CONTINUE BEYOND SIX MONTHS AFTER THE INITIAL STARTUP OF THE PILOT CONTROL DEVICE. | SANDER DUST BOILER, PB-44 | 13.12 | WOOD | 40 | MMBTU/H | FUEL: EITHER PIPELINE SWEET NAT GAS (SUPPLEMENTAL) CONTAINING NO MORE THAN 5 GR S AND 0.25 GR H2S /100 DSCF OR WOOD CONTAINING NO MORE THAN 5% MOISTURE. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 57.2 | LB/H |  |  | 250.5 | T/YR |  | 1.43 | LB/MMBTU |  | STANDARD EMISSIONS CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT
AR-0065 | WEST FRASER (SOUTH), INC. - HUTTIG MILL | WEST FRAZIER (SOUTH), INC. | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-11-07 | PINE LUMBER MILL PROCESSING 230,000 MBF/YR | BOILER, WELLONS | 13.12 | WOOD WASTE | 29.63 | MMBTU/H | WELLONS BOILER PRODUCES 20,700 LB/H OF STEAM TO BE USED IN DRYING KILNS. | Nitrogen Oxides (NOx) | P | OVERFIRE AIR/LOW NOX COMBUSTION | 0.3 | LB/MMBTU |  |  | 8.9 | LB/H |  | 0.3 | LB/MMBTU
AR-0065 | WEST FRASER (SOUTH), INC. - HUTTIG MILL | WEST FRAZIER (SOUTH), INC. | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-11-07 | PINE LUMBER MILL PROCESSING 230,000 MBF/YR | BOILER, WELLONS | 13.12 | WOOD WASTE | 29.63 | MMBTU/H | WELLONS BOILER PRODUCES 20,700 LB/H OF STEAM TO BE USED IN DRYING KILNS. | Nitrogen Oxides (NOx) | P | OVERFIRE AIR/LOW NOX COMBUSTION | 0.3 | LB/MMBTU |  |  | 8.9 | LB/H |  | 0.3 | LB/MMBTU
AL-0213 | WELLBORN CABINETS, INC. | WELLBORN CABINETS, INC. | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2003-04-16 |  | (3) WOOD WASTE BOILERS (29.5 MMBTU/HR EACH) | 13.12 | WOOD WASTE | 29.5 | mmbtu/h |  | Nitrogen Oxides (NOx) | P | BOILER DESIGN AND COMBUSTION CONTROL | 0.5 | LB/MMBTU | 3 HR TEST |  | 14.75 | LB/H |  | 0.5 | LB/MMBTU
AL-0213 | WELLBORN CABINETS, INC. | WELLBORN CABINETS, INC. | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2003-04-16 |  | (3) WOOD WASTE BOILERS (29.5 MMBTU/HR EACH) | 13.12 | WOOD WASTE | 29.5 | mmbtu/h |  | Nitrogen Oxides (NOx) | P | BOILER DESIGN AND COMBUSTION CONTROL | 0.5 | LB/MMBTU | 3 HR TEST |  | 14.75 | LB/H |  | 0.5 | LB/MMBTU
AR-0075 | DELTIC TIMBER CORPORATION | DELTIC TIMBER CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2003-08-20 | LUMBER AND CHIP MILL | BOILER, WOOD WASTE #3 | 13.12 | WOOD WASTE/BARK | 64.3 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | OVEN FIRE AIR/DRY LOW NOX COMBUSTION | 0.3 | LB/MMBTU | [5 empty] | 0.3 | LB/MMBTU
AR-0075 | DELTIC TIMBER CORPORATION | DELTIC TIMBER CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2003-08-20 | LUMBER AND CHIP MILL | BOILER, WOOD WASTE #3 | 13.12 | WOOD WASTE/BARK | 64.3 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | OVEN FIRE AIR/DRY LOW NOX COMBUSTION | 0.3 | LB/MMBTU | [5 empty] | 0.3 | LB/MMBTU
WI-0223 | LOUISIANA-PACIFIC HAYWARD | LOUISIANA-PACIFIC CORPORATION | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-06-17 | OSB MILL | THERMAL OIL HEATERS, KONUS; S11, C11, B11 & B12 | 13.12 | WOOD | 19.4 | MMBTU/H | STACK S11; CONTROL C11; BOILERS B11 & B12 - KONUS THERMAL OIL HEATERS RATED AT 19.4 MILLION BTU PER HOUR EACH WHICH BURN WOOD AS A PRIMARY FUEL AND DISTILLATE FUEL OIL AS A BACKUP FUEL. A SINGLE ELECTRIFIED FILTER BED (EFB) CONTROLS THE EMISSIONS FROM BOTH THERMAL OIL HEATERS | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICES (SEE NOTE BELOW) | 8.9 | LB/H | COMBINED |  |  |  |  | 0.23 | LB/MMBTU | CALCULATED, NOT PERMIT LIMIT | B) GOOD COMBUSTION PRACTICES FOR BURNING WOOD FUEL: I) THE TEMPERATURE OF THE EXHAUST GAS EXITING THE BOILER SHALL BE MAINTAINED AT A MINIMUM OF 1250 DEGREES FAHRENHEIT. II) THE RESIDENCE TIME OF THE BOILER SHALL BE A MINIMUM OF 1 SECOND. III) THE 8-HOUR AVERAGE CARBON MONOXIDE CONCENTRATION OF THE EXHAUST GAS EXITING THE BOILER MAY NOT EXCEED 600 PARTS PER MILLION DRY VOLUME (PPMDV), AT 7% OXYGEN (O2).
WI-0223 | LOUISIANA-PACIFIC HAYWARD | LOUISIANA-PACIFIC CORPORATION | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-06-17 | OSB MILL | THERMAL OIL HEATERS, KONUS, S21, C21, B21 & B22 - | 13.12 | WOOD | 23.8 | MMBTU/H | STACK S21; CONTROL C21; BOILERS B21 & B22 - KONUS THERMAL OIL HEATERS RATED AT 23.8 MILLION BTU PER HOUR EACH WHICH BURN WOOD AS A PRIMARY FUEL AND DISTILLATE FUEL OIL AS A BACKUP FUEL. A SINGLE ELECTRIFIED FILTER BED (EFB) CONTROLS THE EMISSIONS FROM BOTH THERMAL OIL HEATERS. | Nitrogen Oxides (NOx) | P | GOOD COMBUSTIO PRACTICES (SEE NOTES BELOW) | 16.2 | LB/H | COMBINED |  |  |  |  | 0.34 | LB/MMBTU | CALCULATED, NOT PERMIT LIMIT | B) GOOD COMBUSTION PRACTICES FOR BURNING WOOD FUEL: I) THE TEMPERATURE OF THE EXHAUST GAS EXITING THE BOILER SHALL BE MAINTAINED AT A MINIMUM OF 1250 DEGREES FAHRENHEIT. II) THE RESIDENCE TIME OF THE BOILER SHALL BE A MINIMUM OF 1 SECOND. III) THE 8-HOUR AVERAGE CARBON MONOXIDE CONCENTRATION OF THE EXHAUST GAS EXITING THE BOILER MAY NOT EXCEED 600 PARTS PER MILLION DRY VOLUME (PPMDV), AT 7% OXYGEN (O2).
WI-0223 | LOUISIANA-PACIFIC HAYWARD | LOUISIANA-PACIFIC CORPORATION | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-06-17 | OSB MILL | THERMAL OIL HEATERS, KONUS; S11, C11, B11 & B12 | 13.12 | WOOD | 19.4 | MMBTU/H | STACK S11; CONTROL C11; BOILERS B11 & B12 - KONUS THERMAL OIL HEATERS RATED AT 19.4 MILLION BTU PER HOUR EACH WHICH BURN WOOD AS A PRIMARY FUEL AND DISTILLATE FUEL OIL AS A BACKUP FUEL. A SINGLE ELECTRIFIED FILTER BED (EFB) CONTROLS THE EMISSIONS FROM BOTH THERMAL OIL HEATERS | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICES (SEE NOTE BELOW) | 8.9 | LB/H | COMBINED |  |  |  |  | 0.23 | LB/MMBTU | CALCULATED, NOT PERMIT LIMIT | B) GOOD COMBUSTION PRACTICES FOR BURNING WOOD FUEL: I) THE TEMPERATURE OF THE EXHAUST GAS EXITING THE BOILER SHALL BE MAINTAINED AT A MINIMUM OF 1250 DEGREES FAHRENHEIT. II) THE RESIDENCE TIME OF THE BOILER SHALL BE A MINIMUM OF 1 SECOND. III) THE 8-HOUR AVERAGE CARBON MONOXIDE CONCENTRATION OF THE EXHAUST GAS EXITING THE BOILER MAY NOT EXCEED 600 PARTS PER MILLION DRY VOLUME (PPMDV), AT 7% OXYGEN (O2).
WI-0223 | LOUISIANA-PACIFIC HAYWARD | LOUISIANA-PACIFIC CORPORATION | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-06-17 | OSB MILL | THERMAL OIL HEATERS, KONUS, S21, C21, B21 & B22 - | 13.12 | WOOD | 23.8 | MMBTU/H | STACK S21; CONTROL C21; BOILERS B21 & B22 - KONUS THERMAL OIL HEATERS RATED AT 23.8 MILLION BTU PER HOUR EACH WHICH BURN WOOD AS A PRIMARY FUEL AND DISTILLATE FUEL OIL AS A BACKUP FUEL. A SINGLE ELECTRIFIED FILTER BED (EFB) CONTROLS THE EMISSIONS FROM BOTH THERMAL OIL HEATERS. | Nitrogen Oxides (NOx) | P | GOOD COMBUSTIO PRACTICES (SEE NOTES BELOW) | 16.2 | LB/H | COMBINED |  |  |  |  | 0.34 | LB/MMBTU | CALCULATED, NOT PERMIT LIMIT | B) GOOD COMBUSTION PRACTICES FOR BURNING WOOD FUEL: I) THE TEMPERATURE OF THE EXHAUST GAS EXITING THE BOILER SHALL BE MAINTAINED AT A MINIMUM OF 1250 DEGREES FAHRENHEIT. II) THE RESIDENCE TIME OF THE BOILER SHALL BE A MINIMUM OF 1 SECOND. III) THE 8-HOUR AVERAGE CARBON MONOXIDE CONCENTRATION OF THE EXHAUST GAS EXITING THE BOILER MAY NOT EXCEED 600 PARTS PER MILLION DRY VOLUME (PPMDV), AT 7% OXYGEN (O2).
WI-0223 | LOUISIANA-PACIFIC HAYWARD | LOUISIANA-PACIFIC CORPORATION | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-06-17 | OSB MILL | THERMAL OIL HEATERS, KONUS; S11, C11, B11 & B12 | 13.12 | WOOD | 19.4 | MMBTU/H | STACK S11; CONTROL C11; BOILERS B11 & B12 - KONUS THERMAL OIL HEATERS RATED AT 19.4 MILLION BTU PER HOUR EACH WHICH BURN WOOD AS A PRIMARY FUEL AND DISTILLATE FUEL OIL AS A BACKUP FUEL. A SINGLE ELECTRIFIED FILTER BED (EFB) CONTROLS THE EMISSIONS FROM BOTH THERMAL OIL HEATERS | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICES (SEE NOTE BELOW) | 8.9 | LB/H | COMBINED |  |  |  |  | 0.23 | LB/MMBTU | CALCULATED, NOT PERMIT LIMIT | B) GOOD COMBUSTION PRACTICES FOR BURNING WOOD FUEL: I) THE TEMPERATURE OF THE EXHAUST GAS EXITING THE BOILER SHALL BE MAINTAINED AT A MINIMUM OF 1250 DEGREES FAHRENHEIT. II) THE RESIDENCE TIME OF THE BOILER SHALL BE A MINIMUM OF 1 SECOND. III) THE 8-HOUR AVERAGE CARBON MONOXIDE CONCENTRATION OF THE EXHAUST GAS EXITING THE BOILER MAY NOT EXCEED 600 PARTS PER MILLION DRY VOLUME (PPMDV), AT 7% OXYGEN (O2).
WI-0223 | LOUISIANA-PACIFIC HAYWARD | LOUISIANA-PACIFIC CORPORATION | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-06-17 | OSB MILL | THERMAL OIL HEATERS, KONUS, S21, C21, B21 & B22 - | 13.12 | WOOD | 23.8 | MMBTU/H | STACK S21; CONTROL C21; BOILERS B21 & B22 - KONUS THERMAL OIL HEATERS RATED AT 23.8 MILLION BTU PER HOUR EACH WHICH BURN WOOD AS A PRIMARY FUEL AND DISTILLATE FUEL OIL AS A BACKUP FUEL. A SINGLE ELECTRIFIED FILTER BED (EFB) CONTROLS THE EMISSIONS FROM BOTH THERMAL OIL HEATERS. | Nitrogen Oxides (NOx) | P | GOOD COMBUSTIO PRACTICES (SEE NOTES BELOW) | 16.2 | LB/H | COMBINED |  |  |  |  | 0.34 | LB/MMBTU | CALCULATED, NOT PERMIT LIMIT | B) GOOD COMBUSTION PRACTICES FOR BURNING WOOD FUEL: I) THE TEMPERATURE OF THE EXHAUST GAS EXITING THE BOILER SHALL BE MAINTAINED AT A MINIMUM OF 1250 DEGREES FAHRENHEIT. II) THE RESIDENCE TIME OF THE BOILER SHALL BE A MINIMUM OF 1 SECOND. III) THE 8-HOUR AVERAGE CARBON MONOXIDE CONCENTRATION OF THE EXHAUST GAS EXITING THE BOILER MAY NOT EXCEED 600 PARTS PER MILLION DRY VOLUME (PPMDV), AT 7% OXYGEN (O2).

## Data- <100 MMBTU - Liquid Fuel
RBLCID | FACILITYNAME | CORPORATEORCOMPANYNAME | FACILITYSTATE | AGENCYNAME | PERMITDATE | FACILITYDESCRIPTION | PROCESSNAME | PROCTYPE | FUEL | THRUPUT | THRUPUTUNIT | PROCESSNOTES | POLLUTANT | CONTROLCOD | CTRLDESC | EMISLIMIT1 | EMISLIMIT1UNIT | EMISLIMIT1AVGTIMECONDITION | PCTEFFIC | EMISLIMIT2 | EMISLIMIT2UNIT | EMISLIMIT2AVGTIMECONDITION | STDEMISSLIMIT | STDUNITLIMIT | STDLIMITAVGTIMECONDITION | POLLUTANTCOMPLIANCENOTES
ID-0009 | ID NAT'L ENGINEERING AND ENVT'L LAB/NUCLEAR TECH | DEPARTMENT OF ENERGY | ID | IDAHO, OTHER | 2000-06-26 | NUCLEAR AND ENVIRONMENTAL RESEARCH AND DEVELOPMENT. | (4) CPP-606 BOILERS AND (1) INTEC PORTABLE BOILER | 13.22 | DISTILLATE | 29976 | GAL/D | FOUR CPP-606 BOILERS AND 1 INTEC PORTABLE BOILER ARE INCLUDED IN THIS ENTRY. | Beryllium / Beryllium Compounds | N | NONE INDICATED | 0.126 | LB/D | COMBINED |  | 0.0023 | T/YR | COMBINED
ID-0013 | IDAHO NUCLEAR TECHNOLOGY & ENGINEERING CENTER | NATIONAL ENGINEERING & ENVIRONMENTAL LABORATORY | ID | IDAHO DEPT OF ENVIRONMENTAL QUALITY | 2000-06-26 | NUCLEAR AND ENVIRONMENTAL RESEARCH AND DEVELOPMENT | BOILERS, STATIONARY FIRETUBE, (4) | 13.22 | DISTILLATE FUEL OIL | 36.4 | MMBTU/H | TOTAL FUEL COMBUSTED FOR ALL BOILERS, INCLUDING THE PORTABLE BOILER, IS LIMITED TO 29,976 GAL/DAY. | Beryllium / Beryllium Compounds | P | DISTILLATE FUEL OIL, GOOD COMBUSTION PRACTICE | 0.0126 | LB/D |  |  | 0.0023 | T/YR
ID-0013 | IDAHO NUCLEAR TECHNOLOGY & ENGINEERING CENTER | NATIONAL ENGINEERING & ENVIRONMENTAL LABORATORY | ID | IDAHO DEPT OF ENVIRONMENTAL QUALITY | 2000-06-26 | NUCLEAR AND ENVIRONMENTAL RESEARCH AND DEVELOPMENT | BOILER, PORTABLE FIRETUBE, (1) | 13.22 | DISTILLATE FUEL OIL | 29.3 | MMBTU/H | TOTAL FUEL COMBUSTED FOR ALL BOILERS, INCLUDING THE PORTABLE BOILER, IS LIMITED TO 29,976 GAL/DAY. | Beryllium / Beryllium Compounds | P | DISTILLATE FUEL OIL, GOOD COMBUSTION PRACTICE | 0.0126 | LB/D |  |  | 0.0023 | T/YR
NJ-0045 | MERCK - RAHWAY PLANT | MERCK | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-01-14 | CHEMICAL MANUFACTURING | BOILERS - NO. 2 OIL (2) | 13.22 | NO. 2 OIL | 99.5 | MMBTU/H | NO. 2 FUEL OIL USE SHALL NOT EXCEED 3,987,183 GAL/YR BASED ON AN AVERAGE HEATING VALUE OF 138,500 BTU/GAL OF OIL | Carbon Monoxide | N | NONE | 3.6 | LB/H |  |  | 0.036 | LB/MMBTU |  | 0.036 | LB/MMBTU |  | ADDITIONAL CO LIMIT IS 50 PPMVD @7% O2.
MO-0051 | PROCTOR & GAMBLE PAPER PRODUCTS | Proctor & Gamble Paper Products | MO | MISSOURI DNR, AIR POLL CONTROL PROGRAM | 1998-01-01 | SANITARY TISSUE & TOWEL BUSINESS, EXPANSION TO EXISTING DIAPER MANUFACTURING PLANT | BOILERS, #2 FUEL OIL, (3) | 13.22 | #2 FUEL OIL | 265.7 | KGAL/YR | ADDITIONAL THROUGHPUT INFORMATION: 50 MMBTU/H EACH. # 2 FUEL OIL AS BACK-UP, LIMITED TO HEAT INPUT OF 50 MMBTU/H WHEN USED, MAX OF 744 H/YR, AND OIL MAX SULFUR CONTENT OF 0.34% | Carbon Monoxide | N |  | 0.15 | LB/MMBTU | [5 empty] | 0.15 | LB/MMBTU
TN-0054 | PROCTOR AND GAMBLE MANUFACTURING COMPANY | PROCTOR AND GAMBLE MANUFACTURING COMPANY | TN | TENNESSEE DIV OF AIR POLLUTION CONTROL | 1998-03-19 |  | BOILER | 13.22 | NO. 2 FUEL OIL | 0 |  | STACK TEST TO BE CONDUCTED PRIOR TO OBTAINING AN OPERATING PERMIT. | Carbon Monoxide | N |  | 29.3 | LB/H |  | 0 | 36 | LB/H |  | 0
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, KEWAUNEE | 13.22 | NO. 2 FUEL OIL | 13 | MMBTU/H |  | Carbon Monoxide | N |  | 0.5 | LB/H | [5 empty] | 0.038 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, NEBRASKA, BACKUP OIL | 13.22 | NATURAL GAS | 28 | MMBTU/H | This process reflects the requirements for the backup fuel (No. 2 oil). See separate process for primary fuel (natural gas) requirements. | Carbon Monoxide | N |  | 1 | LB/H | [5 empty] | 0.036 | LB/MMBTU
ME-0017 | MCCAINE FOOD INC | MCCAINE FOOD INC | ME | MAINE DEPARTMENT OF ENV PROTECTION | 1999-03-12 |  | BOILER, STEAM | 13.21 | RESIDUAL OIL | 656.7 | GAL/H | INSTALLATION OF A NEW STEAM BOILER AT 81000 LB/H. THROUGHPUT CAPACITY IS AT STANDARD OPERATING CONDITIONS. | Carbon Monoxide | N |  | 0.16 | LB/MMBTU |  | 0 | 15.8 | LB/H |  | 0
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | ELECTRICITY GENERATION | AUXILIARY BOILER- DISTILLATE OIL | 13.22 | DISTILLATE FUEL OIL | 99 | MMBTU/H | DISTILLATE OIL USED AS BACK-UP FUEL- SEE NOTES FOR NATURAL GAS IN AUX. BOILER | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 9.9 | LB/H |  |  | 3.564 | T/YR |  | 0.1 | LB/MMBTU
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | ELECTRICITY GENERATION | AUXILIARY BOILER- DISTILLATE OIL | 13.22 | DISTILLATE FUEL OIL | 99 | MMBTU/H | DISTILLATE OIL USED AS BACK-UP FUEL- SEE NOTES FOR NATURAL GAS IN AUX. BOILER | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 9.9 | LB/H |  |  | 3.564 | T/YR |  | 0.1 | LB/MMBTU
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | SOYBEAN EXTRACTION PLANT | BOILER, NO 2 FUEL OIL | 13.22 | NO 2 FUEL OIL | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. Fuel oil is backup fuel. There is a separate entry for this boiler when firing natural gas. | Carbon Monoxide | N |  | 11.8 | LB/H |  |  | 53.4 | T/YR |  | 0.14 | LB/MMBTU | calculated | Standardized limit calculated using manufacturer's emission factor of 150 lbs CO/1,000,000 lbs of air for both natural gas and fuel oil.
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | SOYBEAN EXTRACTION PLANT | BOILER, NO 2 FUEL OIL | 13.22 | NO 2 FUEL OIL | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. Fuel oil is backup fuel. There is a separate entry for this boiler when firing natural gas. | Carbon Monoxide | N |  | 11.8 | LB/H |  |  | 53.4 | T/YR |  | 0.14 | LB/MMBTU | calculated | Standardized limit calculated using manufacturer's emission factor of 150 lbs CO/1,000,000 lbs of air for both natural gas and fuel oil.
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 |  | BOILER NO.2 | 13.22 | DISTILLATE FUEL OIL | 43.2 | MMBTU | One of two units | Carbon Monoxide | B | GOOD COMBUSTION PRACTICES AND CONTINUOUS EMISSION MONITORING SYSTEM. | 3.56 | LB/H | each unit | [6 empty] | NOT AVAILABLE | One of two units
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 |  | BOILER NO.2 | 13.22 | DISTILLATE FUEL OIL | 43.2 | MMBTU | One of two units | Carbon Monoxide | B | GOOD COMBUSTION PRACTICES AND CONTINUOUS EMISSION MONITORING SYSTEM. | 3.56 | LB/H | each unit | [6 empty] | NOT AVAILABLE | One of two units
AK-0059 | USAF EARECKSON AIR STATION | USAF EARECKSON AIR STATION | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2003-09-29 |  | BOILERS, DIESEL, (5) | 13.22 | DIESEL |  |  | Boiler units numbers 78-82. Throughputs range from 2.01- 2.79 mmBtu/h. Boiler 78 fires a blend of diesel and reclaimed oil, 2:1 ratio. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES |  |  | see note | [7 empty] | BACT is good combustion practices. No emission rate limits.
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, DISTILLATE OIL (1) | 13.22 | #2 FUEL OIL | 40 | MMBTU/H | AUXILIARY BOILER. | Carbon Monoxide | P | GOOD COMBUSTION. | 0.036 | LB/MMBTU | 3 HOUR AVERAGE |  |  |  |  | 0.036 | LB/MMBTU
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, DISTILLATE OIL (1) | 13.22 | #2 FUEL OIL | 40 | MMBTU/H | AUXILIARY BOILER. | Carbon Monoxide | P | GOOD COMBUSTION. | 0.036 | LB/MMBTU | 3 HOUR AVERAGE |  |  |  |  | 0.036 | LB/MMBTU
VA-0299 | UNITED STATES GYPSUM COMPANY | UNITED STATES GYPSUM COMPANY | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2006-06-19 | GYPSUM WALLBOARD, PLASTER, AND INDUSTRIAL GYPSUM PRODUCTS MANUFACTURING FACILITY. | BOILER, MIXER HOT WATER | 13.22 |  | 2.6 | MMBTU/H |  | Carbon Monoxide | N |  | 0.2 | LB/H | [5 empty] | 0.077 | LB/MMBTU
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NO. 2 FUEL OIL | 13.22 | FUEL OIL #2 | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. USING NATURAL GAS WITH #2 OIL BACKUP. TWO SET OF LIMITS, THIS ONE FOR #2 OIL. EACH BOILER IS RESTRICTED TO 250,000 GALLONS OF FUEL OIL PER ROLLING 12-MONTHS. | Carbon Monoxide | N |  | 0.73 | LB/H |  |  | 7.5 | T/YR |  | 0.036 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NO. 2 FUEL OIL | 13.22 | FUEL OIL #2 | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. USING NATURAL GAS WITH #2 OIL BACKUP. TWO SET OF LIMITS, THIS ONE FOR #2 OIL. EACH BOILER IS RESTRICTED TO 250,000 GALLONS OF FUEL OIL PER ROLLING 12-MONTHS. | Carbon Monoxide | N |  | 0.73 | LB/H |  |  | 7.5 | T/YR |  | 0.036 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 |  | BOILER NO.2 | 13.22 | DISTILLATE FUEL OIL | 43.2 | MMBTU | One of two units | Nitrogen Dioxide (NO2) | B | FLUE GAS RECIRCULATION WITH LOW NOX BURNER. GOOD COMBUSTION PRACTICES. CONTINUOUS EMISSION MONITORING SYSTEM. | 6.17 | LB/H | each unit |  |  |  |  | 0.14282 | LB/MMBTU | NOT AVAILABLE | one of two units
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 |  | BOILER NO.2 | 13.22 | DISTILLATE FUEL OIL | 43.2 | MMBTU | One of two units | Nitrogen Dioxide (NO2) | B | FLUE GAS RECIRCULATION WITH LOW NOX BURNER. GOOD COMBUSTION PRACTICES. CONTINUOUS EMISSION MONITORING SYSTEM. | 6.17 | LB/H | each unit |  |  |  |  | 0.14282 | LB/MMBTU | NOT AVAILABLE | one of two units
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, DISTILLATE OIL (1) | 13.22 | #2 FUEL OIL | 40 | MMBTU/H | AUXILIARY BOILER. | Nitrogen Dioxide (NO2) | P | LOW NOX BURNER AND FGR. | 0.058 | LB/MMBTU | 3 HOUR AVERAGE |  |  |  |  | 0.058 | LB/MMBTU
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, DISTILLATE OIL (1) | 13.22 | #2 FUEL OIL | 40 | MMBTU/H | AUXILIARY BOILER. | Nitrogen Dioxide (NO2) | P | LOW NOX BURNER AND FGR. | 0.058 | LB/MMBTU | 3 HOUR AVERAGE |  |  |  |  | 0.058 | LB/MMBTU
NJ-0045 | MERCK - RAHWAY PLANT | MERCK | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-01-14 | CHEMICAL MANUFACTURING | BOILERS - NO. 2 OIL (2) | 13.22 | NO. 2 OIL | 99.5 | MMBTU/H | NO. 2 FUEL OIL USE SHALL NOT EXCEED 3,987,183 GAL/YR BASED ON AN AVERAGE HEATING VALUE OF 138,500 BTU/GAL OF OIL | Nitrogen Oxides (NOx) | P | LNB | 10 | LB/H |  |  | 0.1 | LB/MMBTU |  | 0.1 | LB/MMBTU
KY-0068 | TOYOTA MOTOR MANUFACTURING, USA, INC | TOYOTA MOTOR MANUFACTURING, USA, INC | KY | KENTUCKY DEP, DIV FOR AIR QUALITY | 1997-05-29 | MODIFICATION OF AN AUTOMOBILE ASSEMBLY PLANT (THIRD REVISION OF PERMIT) | BOILER (FUEL OIL) | 13.22 | NO.2 FUEL OIL | 96 | MMBTU/H | A SEPARATELY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING NATURAL GAS (PRIMARY FUEL). WHEN FIRING NO.2 FUEL OIL, ANNUAL OPERATING HOURS SHALL NOT EXCEED 2628 H/YR, 685.97 GAL/YR, AND 1.803 MMGAL/YR. THE ANNUAL HOURS OF OPERATION LIMIT AND THE ANNUAL F | Nitrogen Oxides (NOx) | N | N/A | 0.2 | LB/MMBTU | [5 empty] | 0.2 | LB/MMBTU
MO-0051 | PROCTOR & GAMBLE PAPER PRODUCTS | Proctor & Gamble Paper Products | MO | MISSOURI DNR, AIR POLL CONTROL PROGRAM | 1998-01-01 | SANITARY TISSUE & TOWEL BUSINESS, EXPANSION TO EXISTING DIAPER MANUFACTURING PLANT | BOILERS, #2 FUEL OIL, (3) | 13.22 | #2 FUEL OIL | 265.7 | KGAL/YR | ADDITIONAL THROUGHPUT INFORMATION: 50 MMBTU/H EACH. # 2 FUEL OIL AS BACK-UP, LIMITED TO HEAT INPUT OF 50 MMBTU/H WHEN USED, MAX OF 744 H/YR, AND OIL MAX SULFUR CONTENT OF 0.34% | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS, W/O FLUE GAS RECIRC., GOOD COMBUSTION | 0.17 | LB/MMBTU | [5 empty] | 0.17 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, KEWAUNEE | 13.22 | NO. 2 FUEL OIL | 13 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 0.5 | LB/H | [5 empty] | 0.038 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, NEBRASKA, BACKUP OIL | 13.22 | NATURAL GAS | 28 | MMBTU/H | This process reflects the requirements for the backup fuel (No. 2 oil). See separate process for primary fuel (natural gas) requirements. | Nitrogen Oxides (NOx) | N |  | 5.8 | LB/H | [5 empty] | 0.21 | LB/MMBTU
ME-0017 | MCCAINE FOOD INC | MCCAINE FOOD INC | ME | MAINE DEPARTMENT OF ENV PROTECTION | 1999-03-12 |  | BOILER, STEAM | 13.21 | RESIDUAL OIL | 656.7 | GAL/H | INSTALLATION OF A NEW STEAM BOILER AT 81000 LB/H. THROUGHPUT CAPACITY IS AT STANDARD OPERATING CONDITIONS. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS, STAGED AIR, FLUE GAS RECIRCULA- TION. 3,4 AND 5 RANKED OPTIONS ARE SELECTED FROM 5 OPTIO | 0.3 | LB/MMBTU |  | 0 | 29.6 | LB/H |  | 0.3 | LB/MMBTU
AK-0033 | COMINCO RED DOG MINE | COMINCO ALASKA, INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-12-10 |  | HEATERS, ABCO, 3 UNITS | 13.22 | ARCTIC DIESEL | 13.4 | MMBTU/H | 3 ABCO HEATERS OF 13.4 MMBTU/HR EACH. ONLY NOX AND VE FOR THIS PROCESS. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.084 | LB/MMBTU | [5 empty] | 0.084 | LB/MMBTU
ID-0009 | ID NAT'L ENGINEERING AND ENVT'L LAB/NUCLEAR TECH | DEPARTMENT OF ENERGY | ID | IDAHO, OTHER | 2000-06-26 | NUCLEAR AND ENVIRONMENTAL RESEARCH AND DEVELOPMENT. | (4) CPP-606 BOILERS AND (1) INTEC PORTABLE BOILER | 13.22 | DISTILLATE | 29976 | GAL/D | FOUR CPP-606 BOILERS AND 1 INTEC PORTABLE BOILER ARE INCLUDED IN THIS ENTRY. | Nitrogen Oxides (NOx) | A | FLUE GAS RECIRCULATION | 599.5 | LB/D | COMBINED |  | 98.6 | T/YR | COMBINED | 0.14 | LB/MMBTU | COMBINED
ID-0013 | IDAHO NUCLEAR TECHNOLOGY & ENGINEERING CENTER | NATIONAL ENGINEERING & ENVIRONMENTAL LABORATORY | ID | IDAHO DEPT OF ENVIRONMENTAL QUALITY | 2000-06-26 | NUCLEAR AND ENVIRONMENTAL RESEARCH AND DEVELOPMENT | BOILERS, STATIONARY FIRETUBE, (4) | 13.22 | DISTILLATE FUEL OIL | 36.4 | MMBTU/H | TOTAL FUEL COMBUSTED FOR ALL BOILERS, INCLUDING THE PORTABLE BOILER, IS LIMITED TO 29,976 GAL/DAY. | Nitrogen Oxides (NOx) | P | FLUE GAS RECIRCULATION | 599.5 | LB/D |  | 44 | 98.6 | T/YR |  | 0.69 | LB/MMBTU
ID-0013 | IDAHO NUCLEAR TECHNOLOGY & ENGINEERING CENTER | NATIONAL ENGINEERING & ENVIRONMENTAL LABORATORY | ID | IDAHO DEPT OF ENVIRONMENTAL QUALITY | 2000-06-26 | NUCLEAR AND ENVIRONMENTAL RESEARCH AND DEVELOPMENT | BOILER, PORTABLE FIRETUBE, (1) | 13.22 | DISTILLATE FUEL OIL | 29.3 | MMBTU/H | TOTAL FUEL COMBUSTED FOR ALL BOILERS, INCLUDING THE PORTABLE BOILER, IS LIMITED TO 29,976 GAL/DAY. | Nitrogen Oxides (NOx) | P | FLUE GAS RECIRCULATION | 599.5 | LB/D |  | 44 | 98.6 | T/YR |  | 0.85 | LB/MMBTU
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | ELECTRICITY GENERATION | AUXILIARY BOILER- DISTILLATE OIL | 13.22 | DISTILLATE FUEL OIL | 99 | MMBTU/H | DISTILLATE OIL USED AS BACK-UP FUEL- SEE NOTES FOR NATURAL GAS IN AUX. BOILER | Nitrogen Oxides (NOx) | P | LIMIT BOILER USE TO 3600 H/YR | 0.1 | LB/MMBTU |  |  | 9.9 | LB/H |  | 0.1 | LB/MMBTU
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | ELECTRICITY GENERATION | AUXILIARY BOILER- DISTILLATE OIL | 13.22 | DISTILLATE FUEL OIL | 99 | MMBTU/H | DISTILLATE OIL USED AS BACK-UP FUEL- SEE NOTES FOR NATURAL GAS IN AUX. BOILER | Nitrogen Oxides (NOx) | P | LIMIT BOILER USE TO 3600 H/YR | 0.1 | LB/MMBTU |  |  | 9.9 | LB/H |  | 0.1 | LB/MMBTU
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | SOYBEAN EXTRACTION PLANT | BOILER, NO 2 FUEL OIL | 13.22 | NO 2 FUEL OIL | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. Fuel oil is backup fuel. There is a separate entry for this boiler when firing natural gas. | Nitrogen Oxides (NOx) | P | USE OF LOW NOX BURNERS | 9.21 | LB/H |  |  | 22.7 | T/YR |  | 0.106 | LB/MMBTU |  | Limits based on manufacturer's emission factors: .0352 lb/MMBtu for natural gas and 0.106 lb/MMBtu for fuel oil.
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | SOYBEAN EXTRACTION PLANT | BOILER, NO 2 FUEL OIL | 13.22 | NO 2 FUEL OIL | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. Fuel oil is backup fuel. There is a separate entry for this boiler when firing natural gas. | Nitrogen Oxides (NOx) | P | USE OF LOW NOX BURNERS | 9.21 | LB/H |  |  | 22.7 | T/YR |  | 0.106 | LB/MMBTU |  | Limits based on manufacturer's emission factors: .0352 lb/MMBtu for natural gas and 0.106 lb/MMBtu for fuel oil.
LA-0137 | NORTH BEND CARBON BLACK PLANT | COLUMBIAN CHEMICALS COMPANY | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-05-22 | CARBON BLACK PLANT THAT PRODUCES RUBBER GRADE CARBON BLACK IN 3 UNITS AND INDUSTRIAL GRADE CARBON BLACK IN 5 UNITS AND THE HIGH FINENESS AREA. CARBON BLACK IS PRODUCED FROM FUEL OIL IN REACTORS AND COLLECTED IN BAGHOUSES. VENTS FROM THE BAGHOUSES ARE BURN | STEAM BOILER | 13.29 | FEEDSTOCK OIL | 15 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 20.93 | LB/H | HOURLY MAXIMUM |  |  |  |  | 1.4 | LB/MMBTU | CALCULATED BY CATC | *AS IMPOSED BY PSD-LA-580(M-4), ISSUED JULY 11, 2005. ANNUAL NOX LIMIT FOR THE DRYER STACK (59), STEAM BOILER (62), MAIN COMBUSTION STACK (81), DRYER STACK (84), AND NEW TAIL GAS FLARE (123) ESTABLISHED AT 4140.30 TPY (ANNUAL MAXIMUM). PSD-LA-580(M-3) SET
OK-0092 | VALERO ARDMORE REFINERY | TPI PETROLEUM | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2003-01-13 | PETROLEUM REFINERY | CRUDE OIL HEATER - UNIT 102A | 13.21 | FUEL OIL | 145 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 0.045 | LB/MMBTU |  | 84 | 28.6 | T/YR |  | 0.045 | LB/MMBTU
OK-0092 | VALERO ARDMORE REFINERY | TPI PETROLEUM | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2003-01-13 | PETROLEUM REFINERY | CRUDE OIL HEATER - UNIT 102B | 13.21 | FUEL OIL | 135 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 0.059 | LB/MMBTU |  | 79 | 34.9 | T/YR |  | 0.059 | LB/MMBTU
MI-0355 | ABBOTT LABORATORIES, STURGIS PLANT | ABBOTT LABORATORIES, ROSS PRODUCTS DIVISION | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 2003-09-16 | NUTRITIONAL PRODUCTS MANUFACTURER. | BOILER, FUEL OIL | 13.22 | #2 FUEL OIL | 98.51 | MMBTU/H | FUEL OIL USED AS BACKUP | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 0.14 | LB/MMBTU | [5 empty] | 0.14 | LB/MMBTU |  | Limit is based on combustion of #2 fuel oil. Limit for burning natural gas is 0.08 lb/MMbtu.
MI-0355 | ABBOTT LABORATORIES, STURGIS PLANT | ABBOTT LABORATORIES, ROSS PRODUCTS DIVISION | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 2003-09-16 | NUTRITIONAL PRODUCTS MANUFACTURER. | BOILER, FUEL OIL | 13.22 | #2 FUEL OIL | 98.51 | MMBTU/H | FUEL OIL USED AS BACKUP | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 0.14 | LB/MMBTU | [5 empty] | 0.14 | LB/MMBTU |  | Limit is based on combustion of #2 fuel oil. Limit for burning natural gas is 0.08 lb/MMbtu.
AK-0060 | DUTCH HARBOR SEAFOOD PROCESSING FACILITY | WESTWARD SEAFOODS, INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2003-10-10 | FISH PROCESSING PLANT | BOILER, FUEL OIL, (2) | 13.29 | DISTILLATE OIL | 29.3 | MMBTU/H | Throughput for each. Cleaver-Brooks firetube boiler, Model No. NCB-100-700-200. Boilers use a mixture of distillate fuel oil, fish oil, used oil. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND GOOD COMBUSTION PRACTICE | 4.4 | LB/H | each |  |  |  |  | 0.15 | LB/MMBTU | calculated
WA-0313 | HANFORD | UNITED STATES DEPARTMENT OF ENERGY | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2003-11-13 | RADIOACTIVE WASTE TREATMENT PLANT | BOILERS, STEAM PLANT, (6) | 13.21 | #2 FUEL OIL | 50.2 | MMBTU/H | SIX HORIZONTAL-PACKAGED FIRE TUBE BOILERS. THREE ARE PERMITTED TO OPERATE 8760 H/YR EACH, AND THREE ARE PERMITTED TO OPERATE 3679 H/YR TOTAL. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS, FLUE GAS RECIRCULATION, AND STEAM ATOMIZATION | 0.09 | LB/MMBTU | @ 3% O2 | 76 | 4.52 | LB/H |  | 0.09 | LB/MMBTU | @ 3% O2
*NE-0023 | BEATRICE POWER STATION | NEBRASKA PUBLIC POWER DISTRICT | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2004-06-22 | PERMIT TO CONSTRUCT: 2-NG TURBINES, 250 MW TOTAL AND ONE AUX. BOILER, 73 MMBTU/HR, OIL FIRED | AUXILIARY BOILER (OIL) | 13.22 | NATURAL GAS | 73.3 | MMBTU/H | THIS UNIT CAN BURN UP TO 289,000 GAL/YR OF DISTILATE OIL. THE LIMITS INDICATED HERE ARE FOR BURNING OIL. SEE THE PROCEESS AUXILIARY BOILER (NG) FOR EMISSION LIMITS WHILE BURNING NATURAL GAS. | Nitrogen Oxides (NOx) | N | OPERATION LIMITED TO 500 HOURS PER YEAR. | 0.1 | LB/MMBTU | 3 HOUR TEST AVG |  |  |  |  | 0.1 | LB/MMBTU | 3 HOUR TEST AVG | OPERATION LIMITED TO 500 HOURS PER YEAR. THIS UNIT CAN BURN UP TO 289,000 GAL/YR OF DISTILATE OIL. THE LIMITS INDICATED HERE ARE FOR BURNING OIL. SEE THE PROCEESS AUXILIARY BOILER (NG) FOR EMISSION LIMITS WHILE BURNING NATURAL GAS.
*NE-0023 | BEATRICE POWER STATION | NEBRASKA PUBLIC POWER DISTRICT | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2004-06-22 | PERMIT TO CONSTRUCT: 2-NG TURBINES, 250 MW TOTAL AND ONE AUX. BOILER, 73 MMBTU/HR, OIL FIRED | AUXILIARY BOILER (OIL) | 13.22 | NATURAL GAS | 73.3 | MMBTU/H | THIS UNIT CAN BURN UP TO 289,000 GAL/YR OF DISTILATE OIL. THE LIMITS INDICATED HERE ARE FOR BURNING OIL. SEE THE PROCEESS AUXILIARY BOILER (NG) FOR EMISSION LIMITS WHILE BURNING NATURAL GAS. | Nitrogen Oxides (NOx) | N | OPERATION LIMITED TO 500 HOURS PER YEAR. | 0.1 | LB/MMBTU | 3 HOUR TEST AVG |  |  |  |  | 0.1 | LB/MMBTU | 3 HOUR TEST AVG | OPERATION LIMITED TO 500 HOURS PER YEAR. THIS UNIT CAN BURN UP TO 289,000 GAL/YR OF DISTILATE OIL. THE LIMITS INDICATED HERE ARE FOR BURNING OIL. SEE THE PROCEESS AUXILIARY BOILER (NG) FOR EMISSION LIMITS WHILE BURNING NATURAL GAS.
VA-0299 | UNITED STATES GYPSUM COMPANY | UNITED STATES GYPSUM COMPANY | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2006-06-19 | GYPSUM WALLBOARD, PLASTER, AND INDUSTRIAL GYPSUM PRODUCTS MANUFACTURING FACILITY. | BOILER, MIXER HOT WATER | 13.22 |  | 2.6 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 0.3 | LB/H | [5 empty] | 0.115 | LB/MMBTU
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NO. 2 FUEL OIL | 13.22 | FUEL OIL #2 | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. USING NATURAL GAS WITH #2 OIL BACKUP. TWO SET OF LIMITS, THIS ONE FOR #2 OIL. EACH BOILER IS RESTRICTED TO 250,000 GALLONS OF FUEL OIL PER ROLLING 12-MONTHS. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 1.5 | LB/H |  |  | 3.5 | T/YR |  | 0.072 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NO. 2 FUEL OIL | 13.22 | FUEL OIL #2 | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. USING NATURAL GAS WITH #2 OIL BACKUP. TWO SET OF LIMITS, THIS ONE FOR #2 OIL. EACH BOILER IS RESTRICTED TO 250,000 GALLONS OF FUEL OIL PER ROLLING 12-MONTHS. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 1.5 | LB/H |  |  | 3.5 | T/YR |  | 0.072 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
KY-0068 | TOYOTA MOTOR MANUFACTURING, USA, INC | TOYOTA MOTOR MANUFACTURING, USA, INC | KY | KENTUCKY DEP, DIV FOR AIR QUALITY | 1997-05-29 | MODIFICATION OF AN AUTOMOBILE ASSEMBLY PLANT (THIRD REVISION OF PERMIT) | BOILER (FUEL OIL) | 13.22 | NO.2 FUEL OIL | 96 | MMBTU/H | A SEPARATELY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING NATURAL GAS (PRIMARY FUEL). WHEN FIRING NO.2 FUEL OIL, ANNUAL OPERATING HOURS SHALL NOT EXCEED 2628 H/YR, 685.97 GAL/YR, AND 1.803 MMGAL/YR. THE ANNUAL HOURS OF OPERATION LIMIT AND THE ANNUAL F | Particulate Matter (PM) | A | FABRIC FILTER | 0.1 | LB/MMBTU | [5 empty] | 0.1 | LB/MMBTU |  | THE OUTLET PARTICULATE CONCENTRATION FROM EACH FABRIC FILTER CONTROL DEVICE SHALL NOT EXCEED 0.003 GR PER ACF.
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, KEWAUNEE | 13.22 | NO. 2 FUEL OIL | 13 | MMBTU/H |  | Particulate Matter (PM) | N |  | 0.2 | LB/H | [5 empty] | 0.015 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, NEBRASKA, BACKUP OIL | 13.22 | NATURAL GAS | 28 | MMBTU/H | This process reflects the requirements for the backup fuel (No. 2 oil). See separate process for primary fuel (natural gas) requirements. | Particulate Matter (PM) | N |  | 2.4 | LB/H |  |  | 0.1 | LB/MMBTU |  | 0.1 | LB/MMBTU
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | GLYCOL SKID HEATER (DIESEL), UNIT NO. 14 | 13.22 | DIESEL | 1.05 | LB/MMBTU | GLYCOL SKID HEATER ALSO USES NATURAL GAS AS FUEL, LISTED SEPARATELY. MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 1000 H/YR. | Particulate Matter (PM) | N | NONE INDICATED | 0.05 | GR/DSCF | AV OVER 3 H
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | PORTABLE HEATER, UNIT NO. 105-107 | 13.22 | DIESEL | 1 | MMBTU/H | TYPICAL OPERATION DURING COMMISSIONING PERIOD; 1848 H, TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 8760 H/YR. PORTABLE HEATER AND BLOWER ENGINE ON PORTABLE HEATER ARE LISTED SEPARATELY FOR DATABASE. | Particulate Matter (PM) | P | GOOD OPERATIONS PRACTICES | 0.05 | GR/DSCF | AVERAGED OVER 3 H
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | MISCELLANEOUS HEATERS | 13.22 | DIESEL | 13 | MMBTU/H | EQUIPMENT PART OF CONSTRUCTION RESERVE POOL. TYPICAL OPERATION, 1440 H/YR. | Particulate Matter (PM) | P | GOOD OPERATIONS PRACTICES | 0.05 | GR/DSCF | AV OVER 3 H
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | RIG BOILER, DIESEL, UNIT 206, 207 | 13.22 | DIESEL | 6.3 | MMBTU/H | PERMIT LISTS UNIT 6 AND 7 AS BOTH BURNING NATURAL GAS AND DIESEL-- LISTED SEPARATELY IN DATABASE. TYPICAL OPERATION DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 924 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. DURING PRE-SEALIFT PERIOD AND | Particulate Matter (PM) | P | GOOD OPERATIONS PRACTICES. | 0.05 | GR/DSCF | AV OVER 3 H | [7 empty] | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATER (DIESEL), UNIT 208, 209 | 13.22 | DIESEL | 3.5 | MMBTU/H | PERMIT LISTS UNIT 208 AND 209 AS BURNING DIESEL FUEL AND NATURAL GAS. THESE ARE LISTED SEPARATELY IN DATABASE. DURING PRE-SEALIFT PERIOD AND COMMISSIONING PERIOD, UNITS MAY BE OPERATED WITH NATURAL GAS OR DIESEL FOR THE SAME AMOUNT OF TIME. DURING LONG-TE | Particulate Matter (PM) | P | GOOD OPERATIONS PRACTICE | 0.05 | GR/DSCF | AV OVER 3 H | [7 empty] | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATER (DIESEL), UNIT 210 | 13.22 | DIESEL | 4.2 | MMBTU/H | DURING PRE-SEALIFT PERIOD AND COMMISSIONING PERIOD, UNITS MAY BE OPERATED WITH NATURAL GAS OR DIESEL FOR THE SAME AMOUNT OF TIME. DURING LONG-TERM OPERATIONS, UNIT MAY BE RUN FULL-TIME ON NATURAL GAS, WITH DIESEL USE FOR 18 H/D AND UP TO 1,000 H/YR AS A B | Particulate Matter (PM) | P | GOOD OPERATIONS PRACTICES. | 0.05 | GR/DSCF | AV OVER 3 H | [7 empty] | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATERS, 4.0 MMBTU/H | 13.22 | DIESEL | 4 | MMBTU/H | TYPICAL OPERATION BEFORE AND DURING COMMISSIONING PERIOD, 3672 H. TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 0 H/YR. | Particulate Matter (PM) | P | GOOD OPERATIONS PRACTICES. | 0.05 | GR/DSCF | AV OVER 3 H | [7 empty] | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATERS, 35.0 MMBTU/H | 13.22 | DIESEL | 35 | MMBTU/H | TYPICAL OPERATION BEFORE AND DURING COMMISSIONING PERIOD, 2976 H; TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 0 H/YR. | Particulate Matter (PM) | P | GOOD OPERATIONS PRACTICES | 0.05 | GR/DSCF | AV OVER 3 H | [7 empty] | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATERS, 2.0 MMBTU/H | 13.22 | DIESEL | 2 | MMBTU/H | TYPICAL OPERATION BEFORE AND DURING COMMISSIONING PERIOD, 1128 H. TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 0 H/YR. | Particulate Matter (PM) | P | GOOD OPERATIONS PRACTICES. | 0.05 | GR/DSCF | AV OVER 3 H | [7 empty] | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATERS, 20.0 MMBTU/H | 13.22 | DIESEL | 20 | MMBTU/H | TYPICAL OPERATION BEFORE AND DURING COMMISSIONING PERIOD, 2190 H. TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 0 H/YR. | Particulate Matter (PM) | P | GOOD OPERATIONS PRACTICES. | 0.05 | GR/DSCF | AV OVER 3 H | [7 empty] | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
ME-0017 | MCCAINE FOOD INC | MCCAINE FOOD INC | ME | MAINE DEPARTMENT OF ENV PROTECTION | 1999-03-12 |  | BOILER, STEAM | 13.21 | RESIDUAL OIL | 656.7 | GAL/H | INSTALLATION OF A NEW STEAM BOILER AT 81000 LB/H. THROUGHPUT CAPACITY IS AT STANDARD OPERATING CONDITIONS. | Particulate Matter (PM) | P | 0.5 % SULFUR FUEL OIL. | 0.08 | LB/MMBTU |  | 0 | 7.9 | LB/H |  | 0.08 | LB/MMBTU
ID-0009 | ID NAT'L ENGINEERING AND ENVT'L LAB/NUCLEAR TECH | DEPARTMENT OF ENERGY | ID | IDAHO, OTHER | 2000-06-26 | NUCLEAR AND ENVIRONMENTAL RESEARCH AND DEVELOPMENT. | (4) CPP-606 BOILERS AND (1) INTEC PORTABLE BOILER | 13.22 | DISTILLATE | 29976 | GAL/D | FOUR CPP-606 BOILERS AND 1 INTEC PORTABLE BOILER ARE INCLUDED IN THIS ENTRY. | Particulate Matter (PM) | N | NONE INDICATED | 0.05 | GR/DSCF @ 3% O2 | [7 empty] | NOT AVAILABLE
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | BOILERS (ID NOS. 9-10) | 13.29 | LIQUID FUEL | 400 | BHP, EACH | THIS ENTRY INCLUDES 2 JOHNSTON PFTA-400-3LX-150S BOILERS. FOR PURPOSES OF DEFINING THE SCC AND PROCESS CODES, IT WAS ASSUMED THAT BHP MEANS BOILER HORSE POWER. THE PERMITTEE MAY BURN A USED OIL FUEL BLEND SUBJECT TO THE FOLLOWING CONDITIONS; PERMITTEE SHA | Particulate Matter (PM) | P | GOOD AIR POLLUTION CONTROL PRACTICES ACCORDING TO NSPS. | 0.05 | GR/DSCF | EACH | [6 empty] | NOT AVAILABLE
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | BOILER (ID NO. 11) | 13.29 | LIQUID FUEL | 400 | BHP | ONE JOHNSTON PFTA-400-3LX-150S BOILER IS INCLUDED IN THIS ENTRY. THE INSTALLATION DATE WAS 1986. THE PERMITTEE MAY BURN A USED OIL FUEL BLEND SUBJECT TO THE FOLLOWING CONDITIONS; PERMITTEE SHALL NOT BURN USED OIL WHILE MANUFACTURING POLLOCK SURIMI, THE FU | Particulate Matter (PM) | N |  | 0.05 | GR/DSCF | 3 H AV | [6 empty] | NOT AVAILABLE | NEED EMISSION LIMIT IN STANDARDIZED UNITS.
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | BOILER (ID NOS. 12-13) | 13.29 | LIQUID FUEL | 200 | BHP, EACH | FOR PURPOSES OF DEFINING THE SCC AND PROCESS TYPE CODES, IT WAS ASSUMED THAT BHP MEANS BOILER HORSEPOWER. THE PERMITTEE MAY BLEND FISH OIL WITH DIESEL FUEL AND MAY ADD FISH OIL TO A USED OIL BLEND UNDER THE FOLLOWING CONDITIONS; PERMITTEE SHALL NOT BURN U | Particulate Matter (PM) | N |  | 0.05 | GR/DSCF | 3 H AV, EACH | [6 empty] | NOT AVAILABLE
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | HOT AIR DRYER (ID NOS. 14-15) | 13.29 |  | 24.1 | MMBTU/H, EACH | TWO STORD INT'L SIDJ-4.5 DRYERS WITH RAY ROTARY BGE-700 BURNERS ARE INCLUDED IN THIS ENTRY. THE DRYERS WERE INSTALLED IN 1990. THE PERMITTEE MAY BLEND FISH OIL WITH DIESEL FUEL AND MAY ADD FISH OIL TO A USED OIL BLEND UNDER THE FOLLOWING CONDITIONS; PERMI | Particulate Matter (PM) | N |  | 0.05 | GR/DSCF | 3 H AV, EACH | [7 empty] | NEED EMISSION LIMIT IN STANDARDIZED UNITS.
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | HOT AIR DRYER (ID NO. 16) | 13.29 |  | 6.3 | MMBTU/H | ONE ALFA-LAVAL KIX K4 (FME A/S) DRYER WITH MAXON OVENPAK 500-SP BURNER IS INCLUDED IN THIS ENTRY. THE INSTALLATION DATE WAS 1997. THE PERMITTEE MAY BLEND FISH OIL WITH DIESEL FUEL AND MAY ADD FISH OIL TO A USED OIL BLEND UNDER THE FOLLOWING CONDITIONS; PE | Particulate Matter (PM) | N |  | 0.05 | GR/DSCF | 3 H AV
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | ELECTRICITY GENERATION | AUXILIARY BOILER- DISTILLATE OIL | 13.22 | DISTILLATE FUEL OIL | 99 | MMBTU/H | DISTILLATE OIL USED AS BACK-UP FUEL- SEE NOTES FOR NATURAL GAS IN AUX. BOILER | Particulate Matter (PM) | P | LIMITED USE | 3.96 | LB/H |  |  | 1.426 | T/YR |  | 0.04 | LB/MMBTU
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | ELECTRICITY GENERATION | AUXILIARY BOILER- DISTILLATE OIL | 13.22 | DISTILLATE FUEL OIL | 99 | MMBTU/H | DISTILLATE OIL USED AS BACK-UP FUEL- SEE NOTES FOR NATURAL GAS IN AUX. BOILER | Particulate Matter (PM) | P | LIMITED USE | 3.96 | LB/H |  |  | 1.426 | T/YR |  | 0.04 | LB/MMBTU
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | SOYBEAN EXTRACTION PLANT | BOILER, NO 2 FUEL OIL | 13.22 | NO 2 FUEL OIL | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. Fuel oil is backup fuel. There is a separate entry for this boiler when firing natural gas. | Particulate Matter (PM) | N |  | 0.47 | LB/H |  |  | 2.06 | T/YR |  | 0.0054 | LB/MMBTU |  | USING NATURAL GAS WITH BACKUP NO. 2 FUEL OIL. EMISSIONS BASED ON MFG. TESTED RATE FOR NATURAL GAS 0.005 LB/MMBTU AND 0.0054 LB/MMBTU WHEN BURNING #2 OIL.
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | SOYBEAN EXTRACTION PLANT | BOILER, NO 2 FUEL OIL | 13.22 | NO 2 FUEL OIL | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. Fuel oil is backup fuel. There is a separate entry for this boiler when firing natural gas. | Particulate Matter (PM) | N |  | 0.47 | LB/H |  |  | 2.06 | T/YR |  | 0.0054 | LB/MMBTU |  | USING NATURAL GAS WITH BACKUP NO. 2 FUEL OIL. EMISSIONS BASED ON MFG. TESTED RATE FOR NATURAL GAS 0.005 LB/MMBTU AND 0.0054 LB/MMBTU WHEN BURNING #2 OIL.
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 |  | BOILER NO.2 | 13.22 | DISTILLATE FUEL OIL | 43.2 | MMBTU | One of two units | Particulate Matter (PM) | P | GOOD COMBUSTION PRACTICES | 0.62 | LB/H | each unit | [6 empty] | NOT AVAILABLE | one of two units
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 |  | BOILER NO.2 | 13.22 | DISTILLATE FUEL OIL | 43.2 | MMBTU | One of two units | Particulate Matter (PM) | P | GOOD COMBUSTION PRACTICES | 0.62 | LB/H | each unit | [6 empty] | NOT AVAILABLE | one of two units
WA-0313 | HANFORD | UNITED STATES DEPARTMENT OF ENERGY | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2003-11-13 | RADIOACTIVE WASTE TREATMENT PLANT | BOILERS, STEAM PLANT, (6) | 13.21 | #2 FUEL OIL | 50.2 | MMBTU/H | SIX HORIZONTAL-PACKAGED FIRE TUBE BOILERS. THREE ARE PERMITTED TO OPERATE 8760 H/YR EACH, AND THREE ARE PERMITTED TO OPERATE 3679 H/YR TOTAL. | Particulate Matter (PM) | P | REDUCED HOURS OF OPERATION, ULTRA LOW SULFUR FUEL, AND GOOD COMBUSTION PRACTICE | 0.02 | LB/MMBTU |  |  | 1 | LB/H |  | 0.02 | LB/MMBTU
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, DISTILLATE OIL (1) | 13.22 | #2 FUEL OIL | 40 | MMBTU/H | AUXILIARY BOILER. | Particulate Matter (PM) | P | CLEAN FUEL AND GOOD COMBUSTION. | 0.024 | LB/MMBTU | 3 HOUR AVERAGE |  |  |  |  | 0.024 | LB/MMBTU
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, DISTILLATE OIL (1) | 13.22 | #2 FUEL OIL | 40 | MMBTU/H | AUXILIARY BOILER. | Particulate Matter (PM) | P | CLEAN FUEL AND GOOD COMBUSTION. | 0.024 | LB/MMBTU | 3 HOUR AVERAGE |  |  |  |  | 0.024 | LB/MMBTU
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NO. 2 FUEL OIL | 13.22 | FUEL OIL #2 | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. USING NATURAL GAS WITH #2 OIL BACKUP. TWO SET OF LIMITS, THIS ONE FOR #2 OIL. EACH BOILER IS RESTRICTED TO 250,000 GALLONS OF FUEL OIL PER ROLLING 12-MONTHS. | Particulate Matter (PM) | N |  | 0.31 | LB/H |  |  | 0.27 | T/YR |  | 0.015 | LB/MMBTU |  | LIMIT IS FOR EACH BOILER.
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NO. 2 FUEL OIL | 13.22 | FUEL OIL #2 | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. USING NATURAL GAS WITH #2 OIL BACKUP. TWO SET OF LIMITS, THIS ONE FOR #2 OIL. EACH BOILER IS RESTRICTED TO 250,000 GALLONS OF FUEL OIL PER ROLLING 12-MONTHS. | Particulate Matter (PM) | N |  | 0.31 | LB/H |  |  | 0.27 | T/YR |  | 0.015 | LB/MMBTU |  | LIMIT IS FOR EACH BOILER.
MO-0051 | PROCTOR & GAMBLE PAPER PRODUCTS | Proctor & Gamble Paper Products | MO | MISSOURI DNR, AIR POLL CONTROL PROGRAM | 1998-01-01 | SANITARY TISSUE & TOWEL BUSINESS, EXPANSION TO EXISTING DIAPER MANUFACTURING PLANT | BOILERS, #2 FUEL OIL, (3) | 13.22 | #2 FUEL OIL | 265.7 | KGAL/YR | ADDITIONAL THROUGHPUT INFORMATION: 50 MMBTU/H EACH. # 2 FUEL OIL AS BACK-UP, LIMITED TO HEAT INPUT OF 50 MMBTU/H WHEN USED, MAX OF 744 H/YR, AND OIL MAX SULFUR CONTENT OF 0.34% | Particulate Matter < 10 μ (PM10) | P | LOW NOX BURNERS, W/O FLUE GAS RECIRC., GOOD COMBUSTION | 0.05 | LB/MMBTU | [5 empty] | 0.05 | LB/MMBTU
VT-0016 | OMYA / VERPOL | OMYA, INC. / Vermont Marble Power Division | VT | VERMONT AIR POLLUTION CONTROL DIVISION | 1999-10-26 | PRODUCTION OF FINELY GROUND CALCIUM CARBONATE MATERIALS | BOILER, FIRE TUBE | 13.22 | # 2 FUEL OIL | 24 | MMBTU/H | fire tube boiler, 600 hp, 20,700 lb steam/h. fuel: < 0.3% S | Particulate Matter < 10 μ (PM10) | P | LOW SULFUR FUEL, GOOD OPERATING PRACTICE. | 0.35 | LB/MMBTU |  |  | 8.4 | LB/H |  | 0.35 | LB/MMBTU |  | regulatory basis: MSER - most stringent emission rate
VT-0018 | AGRIMARK/ CABOT INC. (AMC) | AGRIMARK/ CABOT INC. (AMC) | VT | VERMONT AIR POLLUTION CONTROL DIVISION | 2000-01-03 | CHEESE MANUFACTURER | BOILER, (2) | 13.21 | #6 FUEL OIL | 27 | MMBTU/H | Throughput for each boiler. ACCORDING TO THE PERMIT, SO2 EMISSIONS DO NOT VIOLATE AAQS - NO OTHER POLLUTANTS BESIDES PM LISTED. | Particulate Matter < 10 μ (PM10) | P | FUEL S <= 1.5% BY WT | 0.31 | LB/MMBTU |  |  | 8.5 | LB/H | each | 0.31 | LB/MMBTU
AK-0058 | NORTHSTAR DEVELOPMENT FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-08-16 | OIL AND GAS EXPLORATION FACILITY | HEATERS | 13.22 | DIESEL | 10 | MMBTU/H | SOURCE ID: 210B, 215, 216, 217, AND 218. | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICE |  |  | see note | [7 empty] | GOOD COMBUSTION PRACTICES. VISIBLE EMISSION LIMIT AS SURROGATE FOR PARTICULATE MATTER EMISSION LIMIT.
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 |  | BOILER NO.2 | 13.22 | DISTILLATE FUEL OIL | 43.2 | MMBTU | One of two units | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES | 0.32 | LB/H | each unit | [6 empty] | NOT AVAILABLE | one of two units
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 |  | BOILER NO.2 | 13.22 | DISTILLATE FUEL OIL | 43.2 | MMBTU | One of two units | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES | 0.32 | LB/H | each unit | [6 empty] | NOT AVAILABLE | one of two units
AK-0060 | DUTCH HARBOR SEAFOOD PROCESSING FACILITY | WESTWARD SEAFOODS, INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2003-10-10 | FISH PROCESSING PLANT | BOILER, FUEL OIL, (2) | 13.29 | DISTILLATE OIL | 29.3 | MMBTU/H | Throughput for each. Cleaver-Brooks firetube boiler, Model No. NCB-100-700-200. Boilers use a mixture of distillate fuel oil, fish oil, used oil. | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION MANAGEMENT, OPACITY LIMIT |  |  | see note | [7 empty] | Limit is opacity limit of 20% opacity, 6 min avg. Vendor specifications for these boilers are: 0.025 lb/mmbtu and 0.015 gr/dscf.
WA-0313 | HANFORD | UNITED STATES DEPARTMENT OF ENERGY | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2003-11-13 | RADIOACTIVE WASTE TREATMENT PLANT | BOILERS, STEAM PLANT, (6) | 13.21 | #2 FUEL OIL | 50.2 | MMBTU/H | SIX HORIZONTAL-PACKAGED FIRE TUBE BOILERS. THREE ARE PERMITTED TO OPERATE 8760 H/YR EACH, AND THREE ARE PERMITTED TO OPERATE 3679 H/YR TOTAL. | Particulate Matter < 10 μ (PM10) | P | REDUCED HOURS OF OPERATION, ULTRA LOW SULFUR FUEL, AND GOOD COMBUSTION PRACTICE | 0.02 | LB/MMBTU |  |  | 1 | LB/H |  | 0.02 | LB/MMBTU
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NO. 2 FUEL OIL | 13.22 | FUEL OIL #2 | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. USING NATURAL GAS WITH #2 OIL BACKUP. TWO SET OF LIMITS, THIS ONE FOR #2 OIL. EACH BOILER IS RESTRICTED TO 250,000 GALLONS OF FUEL OIL PER ROLLING 12-MONTHS. | Particulate Matter < 10 μ (PM10) | N |  | 0.5 | LB/H |  |  | 0.78 | T/YR |  | 0.024 | LB/MMBTU |  | LIMIT IS FOR EACH BOILER.
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NO. 2 FUEL OIL | 13.22 | FUEL OIL #2 | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. USING NATURAL GAS WITH #2 OIL BACKUP. TWO SET OF LIMITS, THIS ONE FOR #2 OIL. EACH BOILER IS RESTRICTED TO 250,000 GALLONS OF FUEL OIL PER ROLLING 12-MONTHS. | Particulate Matter < 10 μ (PM10) | N |  | 0.5 | LB/H |  |  | 0.78 | T/YR |  | 0.024 | LB/MMBTU |  | LIMIT IS FOR EACH BOILER.
NJ-0045 | MERCK - RAHWAY PLANT | MERCK | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-01-14 | CHEMICAL MANUFACTURING | BOILERS - NO. 2 OIL (2) | 13.22 | NO. 2 OIL | 99.5 | MMBTU/H | NO. 2 FUEL OIL USE SHALL NOT EXCEED 3,987,183 GAL/YR BASED ON AN AVERAGE HEATING VALUE OF 138,500 BTU/GAL OF OIL | Sulfur Dioxide (SO2) | N | NONE | 5.1 | LB/H | [5 empty] | 0.051 | LB/MMBTU
KY-0068 | TOYOTA MOTOR MANUFACTURING, USA, INC | TOYOTA MOTOR MANUFACTURING, USA, INC | KY | KENTUCKY DEP, DIV FOR AIR QUALITY | 1997-05-29 | MODIFICATION OF AN AUTOMOBILE ASSEMBLY PLANT (THIRD REVISION OF PERMIT) | BOILER (FUEL OIL) | 13.22 | NO.2 FUEL OIL | 96 | MMBTU/H | A SEPARATELY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING NATURAL GAS (PRIMARY FUEL). WHEN FIRING NO.2 FUEL OIL, ANNUAL OPERATING HOURS SHALL NOT EXCEED 2628 H/YR, 685.97 GAL/YR, AND 1.803 MMGAL/YR. THE ANNUAL HOURS OF OPERATION LIMIT AND THE ANNUAL F | Sulfur Dioxide (SO2) | P | THE SULFUR CONTENT OF NO.2 FUEL SHALL NOT EXCEED 0.3%. | 0.3 | LB/MMBTU |  |  | 40 | T/YR |  | 0.3 | LB/MMBTU
TN-0054 | PROCTOR AND GAMBLE MANUFACTURING COMPANY | PROCTOR AND GAMBLE MANUFACTURING COMPANY | TN | TENNESSEE DIV OF AIR POLLUTION CONTROL | 1998-03-19 |  | BOILER | 13.22 | NO. 2 FUEL OIL | 0 |  | STACK TEST TO BE CONDUCTED PRIOR TO OBTAINING AN OPERATING PERMIT. | Sulfur Dioxide (SO2) | N |  | 37.96 | LB/H |  | 0 | 46.64 | LB/H |  | 0
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, KEWAUNEE | 13.22 | NO. 2 FUEL OIL | 13 | MMBTU/H |  | Sulfur Dioxide (SO2) | N |  | 4 | LB/H | [5 empty] | 0.31 | LB/MMBTU
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | GLYCOL SKID HEATER (DIESEL), UNIT NO. 14 | 13.22 | DIESEL | 1.05 | LB/MMBTU | GLYCOL SKID HEATER ALSO USES NATURAL GAS AS FUEL, LISTED SEPARATELY. MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 1000 H/YR. | Sulfur Dioxide (SO2) | P | SULFUR CONTENT OF FUEL OIL SHALL NOT EXCEED 0.15% BY WEIGHT. | 500 | PPM | AVERAGED OVER A PERIOD OF 3 H |  |  |  |  | 2.71 | LB/MMBTU | CALCULATED FROM 500 PPM | BACT: FUEL SULFUR LIMIT STATE: EMISSION LIMIT 1
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | PORTABLE HEATER, UNIT NO. 105-107 | 13.22 | DIESEL | 1 | MMBTU/H | TYPICAL OPERATION DURING COMMISSIONING PERIOD; 1848 H, TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 8760 H/YR. PORTABLE HEATER AND BLOWER ENGINE ON PORTABLE HEATER ARE LISTED SEPARATELY FOR DATABASE. | Sulfur Dioxide (SO2) | P | ENSURE THE EMISSION LIMIT IS MET BY USING FUEL OIL WITH A SULFUR CONTENT NOT TO EXCEED 0.15% BY WEIGHT. | 500 | PPM | AVERAGED OVER 3 H |  |  |  |  | 2.71 | LB/MMBTU | CALCULATED FROM 500 PPM
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | MISCELLANEOUS HEATERS | 13.22 | DIESEL | 13 | MMBTU/H | EQUIPMENT PART OF CONSTRUCTION RESERVE POOL. TYPICAL OPERATION, 1440 H/YR. | Sulfur Dioxide (SO2) | P | TO ENSURE COMPLIANCE WITH THE EMISSION LIMIT, THE SULFUR CONTENT OF THE FUEL OIL SHALL NOT EXCEED 0.15% BY WEIGHT. | 500 | PPM | AVERAGED OVER 3 H |  |  |  |  | 2.71 | LB/MMBTU | CALCULATED FROM 500 PPM
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | RIG BOILER, DIESEL, UNIT 206, 207 | 13.22 | DIESEL | 6.3 | MMBTU/H | PERMIT LISTS UNIT 6 AND 7 AS BOTH BURNING NATURAL GAS AND DIESEL-- LISTED SEPARATELY IN DATABASE. TYPICAL OPERATION DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 924 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. DURING PRE-SEALIFT PERIOD AND | Sulfur Dioxide (SO2) | P | SULFUR CONTENT OF FUEL OIL SHALL NOT EXCEED 0.15% BY WEIGHT. | 500 | PPM | AV OVER 3 H |  |  |  |  | 2.71 | LB/MMBTU | CALCULATED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMIT STATE: EMISSION LIMIT 1 AND FUEL RESTRICTION
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATER (DIESEL), UNIT 208, 209 | 13.22 | DIESEL | 3.5 | MMBTU/H | PERMIT LISTS UNIT 208 AND 209 AS BURNING DIESEL FUEL AND NATURAL GAS. THESE ARE LISTED SEPARATELY IN DATABASE. DURING PRE-SEALIFT PERIOD AND COMMISSIONING PERIOD, UNITS MAY BE OPERATED WITH NATURAL GAS OR DIESEL FOR THE SAME AMOUNT OF TIME. DURING LONG-TE | Sulfur Dioxide (SO2) | P | SULFUR CONTENT OF FUEL OIL SHALL NOT EXCEED 0.15% BY WEIGHT | 500 | PPM | AV OVER 3 H |  |  |  |  | 2.71 | LB/MMBTU | CALCULATED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMIT STATE: EMISSION LIMIT 1 AND SULFUR RESTRICTION TO FUEL
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATER (DIESEL), UNIT 210 | 13.22 | DIESEL | 4.2 | MMBTU/H | DURING PRE-SEALIFT PERIOD AND COMMISSIONING PERIOD, UNITS MAY BE OPERATED WITH NATURAL GAS OR DIESEL FOR THE SAME AMOUNT OF TIME. DURING LONG-TERM OPERATIONS, UNIT MAY BE RUN FULL-TIME ON NATURAL GAS, WITH DIESEL USE FOR 18 H/D AND UP TO 1,000 H/YR AS A B | Sulfur Dioxide (SO2) | P | SULFUR CONTENT OF FUEL OIL SHALL NOT EXCEED 0.15% BY WEIGHT. | 500 | PPM | AV OVER 3 H |  |  |  |  | 2.71 | LB/MMBTU | CALCULATED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMITS STATE: EMISSION LIMIT 1 AND SULFUR CONTENT LIMIT TO FUEL
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATERS, 4.0 MMBTU/H | 13.22 | DIESEL | 4 | MMBTU/H | TYPICAL OPERATION BEFORE AND DURING COMMISSIONING PERIOD, 3672 H. TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 0 H/YR. | Sulfur Dioxide (SO2) | P | SULFUR CONTENT OF FUEL OIL SHALL NOT EXCEED 0.15% BY WEIGHT. | 500 | PPM | AV OVER 3 H |  |  |  |  | 2.71 | LB/MMBTU | CONVERTED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMIT STATE: EMISSION LIMIT 1 AND SULFUR CONTENT RESTRICTION TO THE FUEL
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATERS, 35.0 MMBTU/H | 13.22 | DIESEL | 35 | MMBTU/H | TYPICAL OPERATION BEFORE AND DURING COMMISSIONING PERIOD, 2976 H; TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 0 H/YR. | Sulfur Dioxide (SO2) | P | SULFUR CONTENT OF FUEL OIL SHALL NOT EXCEED 0.15% BY WEIGHT. | 500 | PPM | AVERAGED OVER 3 H |  |  |  |  | 2.71 | LB/MMBTU | CALCULATED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMIT STATE: EMISSION LIMIT 1 AND SULFUR CONTENT RESTRICTION TO THE FUEL.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATERS, 2.0 MMBTU/H | 13.22 | DIESEL | 2 | MMBTU/H | TYPICAL OPERATION BEFORE AND DURING COMMISSIONING PERIOD, 1128 H. TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 0 H/YR. | Sulfur Dioxide (SO2) | P | SULFUR CONTENT OF FUEL OIL SHALL NOT EXCEED 0.15% BY WEIGHT. | 500 | PPM | AV OVER 3 H |  |  |  |  | 2.71 | LB/MMBTU | CALCULATED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMITS STATE: EMISSION LIMIT 1 AND SULFUR CONTENT RESTRICTION TO THE FUEL.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATERS, 20.0 MMBTU/H | 13.22 | DIESEL | 20 | MMBTU/H | TYPICAL OPERATION BEFORE AND DURING COMMISSIONING PERIOD, 2190 H. TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 0 H/YR. | Sulfur Dioxide (SO2) | P | SULFUR CONTENT OF FUEL OIL SHALL NOT EXCEED 0.15% BY WEIGHT. | 500 | PPM | AV OVER 3 H |  |  |  |  | 2.71 | LB/MMBTU | CALCULATED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMIT STATE: EMISSION LIMIT 1 AND SULFUR CONTENT RESTRICTION TO THE FUEL.
ME-0017 | MCCAINE FOOD INC | MCCAINE FOOD INC | ME | MAINE DEPARTMENT OF ENV PROTECTION | 1999-03-12 |  | BOILER, STEAM | 13.21 | RESIDUAL OIL | 656.7 | GAL/H | INSTALLATION OF A NEW STEAM BOILER AT 81000 LB/H. THROUGHPUT CAPACITY IS AT STANDARD OPERATING CONDITIONS. | Sulfur Dioxide (SO2) | P | 0.5 % SULFUR FUEL OIL. | 0.52 | LB/MMBTU |  | 0 | 51.2 | LB/H |  | 0
ID-0009 | ID NAT'L ENGINEERING AND ENVT'L LAB/NUCLEAR TECH | DEPARTMENT OF ENERGY | ID | IDAHO, OTHER | 2000-06-26 | NUCLEAR AND ENVIRONMENTAL RESEARCH AND DEVELOPMENT. | (4) CPP-606 BOILERS AND (1) INTEC PORTABLE BOILER | 13.22 | DISTILLATE | 29976 | GAL/D | FOUR CPP-606 BOILERS AND 1 INTEC PORTABLE BOILER ARE INCLUDED IN THIS ENTRY. | Sulfur Dioxide (SO2) | P | FUEL CONTENT NO GREATER THAN 0.3 WEIGHT PERCENT SULFUR | 1295 | LB/D | COMBINED |  | 213 | T/YR | COMBINED | 0.31 | LB/MMBTU | COMBINED | ACCORDING TO NSPS THESE PROCESS UNITS SHALL NOT COMBUST DISTILLATE OIL THAT CONTAINS GREATER THAN 0.5 WEIGHT PERCENT FUEL IN THE CPP-606 BOILERS. ACCORDING TO THIS PERMIT, THE CPP-606 AND INTEC PORTABLE BOILERS SHALL NOT COMBUST FUEL WITH GREATER THAN 0.3
ID-0013 | IDAHO NUCLEAR TECHNOLOGY & ENGINEERING CENTER | NATIONAL ENGINEERING & ENVIRONMENTAL LABORATORY | ID | IDAHO DEPT OF ENVIRONMENTAL QUALITY | 2000-06-26 | NUCLEAR AND ENVIRONMENTAL RESEARCH AND DEVELOPMENT | BOILERS, STATIONARY FIRETUBE, (4) | 13.22 | DISTILLATE FUEL OIL | 36.4 | MMBTU/H | TOTAL FUEL COMBUSTED FOR ALL BOILERS, INCLUDING THE PORTABLE BOILER, IS LIMITED TO 29,976 GAL/DAY. | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL 0.3% SULFUR BY WEIGHT | 1295 | LB/D |  |  | 213 | T/YR |  | 1.5 | LB/MMBTU
ID-0013 | IDAHO NUCLEAR TECHNOLOGY & ENGINEERING CENTER | NATIONAL ENGINEERING & ENVIRONMENTAL LABORATORY | ID | IDAHO DEPT OF ENVIRONMENTAL QUALITY | 2000-06-26 | NUCLEAR AND ENVIRONMENTAL RESEARCH AND DEVELOPMENT | BOILER, PORTABLE FIRETUBE, (1) | 13.22 | DISTILLATE FUEL OIL | 29.3 | MMBTU/H | TOTAL FUEL COMBUSTED FOR ALL BOILERS, INCLUDING THE PORTABLE BOILER, IS LIMITED TO 29,976 GAL/DAY. | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL, 0.3% SULFUR BY WEIGHT | 1295 | LB/D |  |  | 213 | T/YR |  | 1.8 | LB/MMBTU
AK-0058 | NORTHSTAR DEVELOPMENT FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-08-16 | OIL AND GAS EXPLORATION FACILITY | HEATERS | 13.22 | DIESEL | 10 | MMBTU/H | SOURCE ID: 210B, 215, 216, 217, AND 218. | Sulfur Dioxide (SO2) | P | FUEL SULFUR LIMITS: USED OIL BLENDS LIMITED TO 0.5% SULFUR BY WEIGHT |  |  | see note | [7 empty] | No emission rate limit -- fuel sulfer limit is BACT. APPLICABLE TO SOURCES ID NO. 217 AND 218 WHICH ARE CAPABLE OF OPERATING ON USED OIL OR FUEL BLENDED WITH USED OIL.
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | BOILERS (ID NOS. 9-10) | 13.29 | LIQUID FUEL | 400 | BHP, EACH | THIS ENTRY INCLUDES 2 JOHNSTON PFTA-400-3LX-150S BOILERS. FOR PURPOSES OF DEFINING THE SCC AND PROCESS CODES, IT WAS ASSUMED THAT BHP MEANS BOILER HORSE POWER. THE PERMITTEE MAY BURN A USED OIL FUEL BLEND SUBJECT TO THE FOLLOWING CONDITIONS; PERMITTEE SHA | Sulfur Dioxide (SO2) | P | ACCORDING TO SIP AND NSPS, USE LIQUID FUEL WITH A SULFUR CONTENT NO GREATER THAN 0.075% BY WEIGHT EXCEPT AS DESCRIBED UNDER THE PROCESS NOTES. GOOD AIR POLLUTION CONTROL PRACTICES ACCORDING TO NSPS. | 500 | PPM | 3 H AV, EACH |  |  |  |  | 2.7 | LB/MMBTU | CALCULATED, EACH
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | BOILER (ID NO. 11) | 13.29 | LIQUID FUEL | 400 | BHP | ONE JOHNSTON PFTA-400-3LX-150S BOILER IS INCLUDED IN THIS ENTRY. THE INSTALLATION DATE WAS 1986. THE PERMITTEE MAY BURN A USED OIL FUEL BLEND SUBJECT TO THE FOLLOWING CONDITIONS; PERMITTEE SHALL NOT BURN USED OIL WHILE MANUFACTURING POLLOCK SURIMI, THE FU | Sulfur Dioxide (SO2) | P | USE DIESEL FUEL WITH A SULFUR CONTENT NO GREATER THAN 0.075% BY WEIGHT EXCEPT AS DESCRIBED UNDER THE PROCESS NOTES. | 500 | PPM | 3 H AV |  |  |  |  | 2.7 | LB/MMBTU | CALCULATED
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | BOILER (ID NOS. 12-13) | 13.29 | LIQUID FUEL | 200 | BHP, EACH | FOR PURPOSES OF DEFINING THE SCC AND PROCESS TYPE CODES, IT WAS ASSUMED THAT BHP MEANS BOILER HORSEPOWER. THE PERMITTEE MAY BLEND FISH OIL WITH DIESEL FUEL AND MAY ADD FISH OIL TO A USED OIL BLEND UNDER THE FOLLOWING CONDITIONS; PERMITTEE SHALL NOT BURN U | Sulfur Dioxide (SO2) | P | USE DIESEL FUEL WITH A SULFUR CONTENT NO GREATER THAN 0.075% BY WEIGHT EXCEPT AS DESCRIBED UNDER THE PROCESS NOTES. | 500 | PPM | 3 H AV, EACH |  |  |  |  | 2.7 | LB/MMBTU | CALCULATED, EACH
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | HOT AIR DRYER (ID NOS. 14-15) | 13.29 |  | 24.1 | MMBTU/H, EACH | TWO STORD INT'L SIDJ-4.5 DRYERS WITH RAY ROTARY BGE-700 BURNERS ARE INCLUDED IN THIS ENTRY. THE DRYERS WERE INSTALLED IN 1990. THE PERMITTEE MAY BLEND FISH OIL WITH DIESEL FUEL AND MAY ADD FISH OIL TO A USED OIL BLEND UNDER THE FOLLOWING CONDITIONS; PERMI | Sulfur Dioxide (SO2) | P | USE DIESEL FUEL WITH A SULFUR CONTENT NO GREATER THAN 0.075% BY WEIGHT EXCEPT AS DESCRIBED UNDER THE PROCESS NOTES. | 500 | PPM | 3 H AV, EACH |  |  |  |  | 2.7 | LB/MMBTU | CALCULATED, EACH
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | HOT AIR DRYER (ID NO. 16) | 13.29 |  | 6.3 | MMBTU/H | ONE ALFA-LAVAL KIX K4 (FME A/S) DRYER WITH MAXON OVENPAK 500-SP BURNER IS INCLUDED IN THIS ENTRY. THE INSTALLATION DATE WAS 1997. THE PERMITTEE MAY BLEND FISH OIL WITH DIESEL FUEL AND MAY ADD FISH OIL TO A USED OIL BLEND UNDER THE FOLLOWING CONDITIONS; PE | Sulfur Dioxide (SO2) | P | USE DIESEL FUEL WITH A SULFUR CONTENT NO GREATER THAN 0.075% BY WEIGHT EXCEPT AS DESCRIBED UNDER THE PROCESS NOTES. | 500 | PPM | 3 H AV |  |  |  |  | 2.7 | LB/MMBTU | CALCULATED
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | ELECTRICITY GENERATION | AUXILIARY BOILER- DISTILLATE OIL | 13.22 | DISTILLATE FUEL OIL | 99 | MMBTU/H | DISTILLATE OIL USED AS BACK-UP FUEL- SEE NOTES FOR NATURAL GAS IN AUX. BOILER | Sulfur Dioxide (SO2) | P | LOW SULFUR OIL (NO PERCENTAGES GIVEN) | 5.021 | LB/H |  |  | 1.807 | T/YR |  | 0.0507 | LB/MMBTU
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | ELECTRICITY GENERATION | AUXILIARY BOILER- DISTILLATE OIL | 13.22 | DISTILLATE FUEL OIL | 99 | MMBTU/H | DISTILLATE OIL USED AS BACK-UP FUEL- SEE NOTES FOR NATURAL GAS IN AUX. BOILER | Sulfur Dioxide (SO2) | P | LOW SULFUR OIL (NO PERCENTAGES GIVEN) | 5.021 | LB/H |  |  | 1.807 | T/YR |  | 0.0507 | LB/MMBTU
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | SOYBEAN EXTRACTION PLANT | BOILER, NO 2 FUEL OIL | 13.22 | NO 2 FUEL OIL | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. Fuel oil is backup fuel. There is a separate entry for this boiler when firing natural gas. | Sulfur Dioxide (SO2) | N |  | 18.2 | LB/H |  |  | 26.2 | T/YR |  | 0.21 | LB/MMBTU | calculated | Using AP-42 emission factor of 0.6 lb/million cubic feet and manufacturer's data 0.21 lb SO2/mmBtu on #2 fuel oil or may opt for burning oil with no greater than 0.5 weight % sulfur. For each shipment of oil, the supplier shall provide the sulfur content
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | SOYBEAN EXTRACTION PLANT | BOILER, NO 2 FUEL OIL | 13.22 | NO 2 FUEL OIL | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. Fuel oil is backup fuel. There is a separate entry for this boiler when firing natural gas. | Sulfur Dioxide (SO2) | N |  | 18.2 | LB/H |  |  | 26.2 | T/YR |  | 0.21 | LB/MMBTU | calculated | Using AP-42 emission factor of 0.6 lb/million cubic feet and manufacturer's data 0.21 lb SO2/mmBtu on #2 fuel oil or may opt for burning oil with no greater than 0.5 weight % sulfur. For each shipment of oil, the supplier shall provide the sulfur content
LA-0137 | NORTH BEND CARBON BLACK PLANT | COLUMBIAN CHEMICALS COMPANY | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-05-22 | CARBON BLACK PLANT THAT PRODUCES RUBBER GRADE CARBON BLACK IN 3 UNITS AND INDUSTRIAL GRADE CARBON BLACK IN 5 UNITS AND THE HIGH FINENESS AREA. CARBON BLACK IS PRODUCED FROM FUEL OIL IN REACTORS AND COLLECTED IN BAGHOUSES. VENTS FROM THE BAGHOUSES ARE BURN | STEAM BOILER | 13.29 | FEEDSTOCK OIL | 15 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | SULFUR CONTENT OF FEEDSTOCK TO 3 RUBBER GRADE UNITS <= 3% BY WEIGHT; SULFUR CONTENT OF FEEDSTOCK TO 5 INDUSTRIAL GRADE UNITS <= 1.5% BY WEIGHT. | 166.17 | LB/H | HOURLY MAXIMUM |  |  |  |  | 11.1 | LB/MMBTU | CALCULATED BY CATC | *AS IMPOSED BY PSD-LA-580(M-4), ISSUED JULY 11, 2005. ANNUAL SO2 LIMIT FOR THE DRYER STACK (59), STEAM BOILER (62), MAIN COMBUSTION STACK (81), DRYER STACK (84), AND NEW TAIL GAS FLARE (123) ESTABLISHED AT 15,095.70 TPY (ANNUAL MAXIMUM). PSD-LA-580(M-3) S
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 |  | BOILER NO.2 | 13.22 | DISTILLATE FUEL OIL | 43.2 | MMBTU | One of two units | Sulfur Dioxide (SO2) | P | GOOD COMBUSTION PRACTICES AND CONTINUOUS EMISSION MONITORING SYSTEM. | 2.19 | LB/H | each unit | [6 empty] | NOT AVAILABLE | One of two units
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 |  | BOILER NO.2 | 13.22 | DISTILLATE FUEL OIL | 43.2 | MMBTU | One of two units | Sulfur Dioxide (SO2) | P | GOOD COMBUSTION PRACTICES AND CONTINUOUS EMISSION MONITORING SYSTEM. | 2.19 | LB/H | each unit | [6 empty] | NOT AVAILABLE | One of two units
AK-0059 | USAF EARECKSON AIR STATION | USAF EARECKSON AIR STATION | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2003-09-29 |  | BOILERS, DIESEL, (5) | 13.22 | DIESEL |  |  | Boiler units numbers 78-82. Throughputs range from 2.01- 2.79 mmBtu/h. Boiler 78 fires a blend of diesel and reclaimed oil, 2:1 ratio. | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL: < 0.3 % S BY WT |  |  | see note | [7 empty] | BACT is the use of low sulfur fuel. No emission rate limits.
AK-0060 | DUTCH HARBOR SEAFOOD PROCESSING FACILITY | WESTWARD SEAFOODS, INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2003-10-10 | FISH PROCESSING PLANT | BOILER, FUEL OIL, (2) | 13.29 | DISTILLATE OIL | 29.3 | MMBTU/H | Throughput for each. Cleaver-Brooks firetube boiler, Model No. NCB-100-700-200. Boilers use a mixture of distillate fuel oil, fish oil, used oil. | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL: SULFUR RESTRICTION OF .24% S BY WT FOR A JET A AND DIESEL NO. 2 FUEL BLEND. |  |  | see note | [7 empty] | BACT is fuel sulfur limit. Mass balance calculations result in an estimated 122 ppmv.
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, DISTILLATE OIL (1) | 13.22 | #2 FUEL OIL | 40 | MMBTU/H | AUXILIARY BOILER. | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL. | 0.051 | LB/MMBTU | [5 empty] | 0.051 | LB/MMBTU |  | EMISSION LIMIT 1 EQUALS TO 0.05% S BY WEIGHT.
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, DISTILLATE OIL (1) | 13.22 | #2 FUEL OIL | 40 | MMBTU/H | AUXILIARY BOILER. | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL. | 0.051 | LB/MMBTU | [5 empty] | 0.051 | LB/MMBTU |  | EMISSION LIMIT 1 EQUALS TO 0.05% S BY WEIGHT.
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NO. 2 FUEL OIL | 13.22 | FUEL OIL #2 | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. USING NATURAL GAS WITH #2 OIL BACKUP. TWO SET OF LIMITS, THIS ONE FOR #2 OIL. EACH BOILER IS RESTRICTED TO 250,000 GALLONS OF FUEL OIL PER ROLLING 12-MONTHS. | Sulfur Dioxide (SO2) | N |  | 10.4 | LB/H |  |  | 3.64 | T/YR |  | 0.51 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NO. 2 FUEL OIL | 13.22 | FUEL OIL #2 | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. USING NATURAL GAS WITH #2 OIL BACKUP. TWO SET OF LIMITS, THIS ONE FOR #2 OIL. EACH BOILER IS RESTRICTED TO 250,000 GALLONS OF FUEL OIL PER ROLLING 12-MONTHS. | Sulfur Dioxide (SO2) | N |  | 10.4 | LB/H |  |  | 3.64 | T/YR |  | 0.51 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
NJ-0045 | MERCK - RAHWAY PLANT | MERCK | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-01-14 | CHEMICAL MANUFACTURING | BOILERS - NO. 2 OIL (2) | 13.22 | NO. 2 OIL | 99.5 | MMBTU/H | NO. 2 FUEL OIL USE SHALL NOT EXCEED 3,987,183 GAL/YR BASED ON AN AVERAGE HEATING VALUE OF 138,500 BTU/GAL OF OIL | Total Suspended Particulates | N | NONE | 1.4 | LB/H |  |  | 0.14 | LB/MMBTU |  | 0.14 | LB/MMBTU
KY-0068 | TOYOTA MOTOR MANUFACTURING, USA, INC | TOYOTA MOTOR MANUFACTURING, USA, INC | KY | KENTUCKY DEP, DIV FOR AIR QUALITY | 1997-05-29 | MODIFICATION OF AN AUTOMOBILE ASSEMBLY PLANT (THIRD REVISION OF PERMIT) | BOILER (FUEL OIL) | 13.22 | NO.2 FUEL OIL | 96 | MMBTU/H | A SEPARATELY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING NATURAL GAS (PRIMARY FUEL). WHEN FIRING NO.2 FUEL OIL, ANNUAL OPERATING HOURS SHALL NOT EXCEED 2628 H/YR, 685.97 GAL/YR, AND 1.803 MMGAL/YR. THE ANNUAL HOURS OF OPERATION LIMIT AND THE ANNUAL F | Visible Emissions (VE) | N | N/A | 20 | % OPACITY | [5 empty] | 20 | % OPACITY
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, KEWAUNEE | 13.22 | NO. 2 FUEL OIL | 13 | MMBTU/H |  | Visible Emissions (VE) | N |  | 20 | % OPACITY | [5 empty] | 20 | % OPACITY
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | VEGETABLE OIL PLANT | BOILER, NEBRASKA, BACKUP OIL | 13.22 | NATURAL GAS | 28 | MMBTU/H | This process reflects the requirements for the backup fuel (No. 2 oil). See separate process for primary fuel (natural gas) requirements. | Visible Emissions (VE) | N |  | 20 | % OPACITY | [5 empty] | 20 | % OPACITY
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | GLYCOL SKID HEATER (DIESEL), UNIT NO. 14 | 13.22 | DIESEL | 1.05 | LB/MMBTU | GLYCOL SKID HEATER ALSO USES NATURAL GAS AS FUEL, LISTED SEPARATELY. MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 1000 H/YR. | Visible Emissions (VE) | N | NONE INDICATED | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H |  |  |  |  | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | PORTABLE HEATER, UNIT NO. 105-107 | 13.22 | DIESEL | 1 | MMBTU/H | TYPICAL OPERATION DURING COMMISSIONING PERIOD; 1848 H, TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 8760 H/YR. PORTABLE HEATER AND BLOWER ENGINE ON PORTABLE HEATER ARE LISTED SEPARATELY FOR DATABASE. | Visible Emissions (VE) | P | GOOD OPERATIONS PRACTICES. | [7 empty] | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | MISCELLANEOUS HEATERS | 13.22 | DIESEL | 13 | MMBTU/H | EQUIPMENT PART OF CONSTRUCTION RESERVE POOL. TYPICAL OPERATION, 1440 H/YR. | Visible Emissions (VE) | P | GOOD OPERATIONS PRACTICES | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H |  |  |  |  | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | RIG BOILER, DIESEL, UNIT 206, 207 | 13.22 | DIESEL | 6.3 | MMBTU/H | PERMIT LISTS UNIT 6 AND 7 AS BOTH BURNING NATURAL GAS AND DIESEL-- LISTED SEPARATELY IN DATABASE. TYPICAL OPERATION DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 924 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. DURING PRE-SEALIFT PERIOD AND | Visible Emissions (VE) | P | GOOD OPERATIONS PRACTICES. | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H |  |  |  |  | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATER (DIESEL), UNIT 208, 209 | 13.22 | DIESEL | 3.5 | MMBTU/H | PERMIT LISTS UNIT 208 AND 209 AS BURNING DIESEL FUEL AND NATURAL GAS. THESE ARE LISTED SEPARATELY IN DATABASE. DURING PRE-SEALIFT PERIOD AND COMMISSIONING PERIOD, UNITS MAY BE OPERATED WITH NATURAL GAS OR DIESEL FOR THE SAME AMOUNT OF TIME. DURING LONG-TE | Visible Emissions (VE) | P | GOOD OPERATIONS PRACTICES | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H |  |  |  |  | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATER (DIESEL), UNIT 210 | 13.22 | DIESEL | 4.2 | MMBTU/H | DURING PRE-SEALIFT PERIOD AND COMMISSIONING PERIOD, UNITS MAY BE OPERATED WITH NATURAL GAS OR DIESEL FOR THE SAME AMOUNT OF TIME. DURING LONG-TERM OPERATIONS, UNIT MAY BE RUN FULL-TIME ON NATURAL GAS, WITH DIESEL USE FOR 18 H/D AND UP TO 1,000 H/YR AS A B | Visible Emissions (VE) | P | GOOD OPERATIONS PRACTICES | 20 | % OPACITY | FOR >3 MIN IN ANY 1 H |  |  |  |  | 20 | % OPACITY | FOR >3 MIN IN ANY 1 H | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATERS, 4.0 MMBTU/H | 13.22 | DIESEL | 4 | MMBTU/H | TYPICAL OPERATION BEFORE AND DURING COMMISSIONING PERIOD, 3672 H. TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 0 H/YR. | Visible Emissions (VE) | P | GOOD OPERATIONS PRACTICES. | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H |  |  |  |  | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATERS, 35.0 MMBTU/H | 13.22 | DIESEL | 35 | MMBTU/H | TYPICAL OPERATION BEFORE AND DURING COMMISSIONING PERIOD, 2976 H; TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 0 H/YR. | Visible Emissions (VE) | P | GOOD OPERATIONS PRACTICES | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H |  |  |  |  | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATERS, 2.0 MMBTU/H | 13.22 | DIESEL | 2 | MMBTU/H | TYPICAL OPERATION BEFORE AND DURING COMMISSIONING PERIOD, 1128 H. TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 0 H/YR. | Visible Emissions (VE) | P | GOOD OPERATIONS STANDARDS. | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H |  |  |  |  | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H | TYPICAL OPERATION BEFORE AND DURING COMMISSIONING PERIOD, 2190 H. TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 0 H/YR.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATERS, 20.0 MMBTU/H | 13.22 | DIESEL | 20 | MMBTU/H | TYPICAL OPERATION BEFORE AND DURING COMMISSIONING PERIOD, 2190 H. TYPICAL OPERATION AFTER COMMISSIONING PERIOD, 0 H/YR. | Visible Emissions (VE) | P | GOOD OPERATIONS PRACTICES. | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H |  |  |  |  | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0033 | COMINCO RED DOG MINE | COMINCO ALASKA, INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-12-10 |  | HEATERS, SMALL, 45 UNITS | 13.22 | DIESEL |  |  | THESE SMALL HEATERS HAVE CAPACITIES FROM 0.1 MMBTU/HR TO 0.67 MMBTU/HR. PERMIT IMPOSES ONLY A VE LIMIT FOR THESE SOURCES. | Visible Emissions (VE) | N |  | 20 | % OPACITY | [5 empty] | 20 | % OPACITY
AK-0033 | COMINCO RED DOG MINE | COMINCO ALASKA, INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-12-10 |  | HEATERS, ABCO, 3 UNITS | 13.22 | ARCTIC DIESEL | 13.4 | MMBTU/H | 3 ABCO HEATERS OF 13.4 MMBTU/HR EACH. ONLY NOX AND VE FOR THIS PROCESS. | Visible Emissions (VE) | P | LOW NOX BURNERS | 20 | % OPACITY | [5 empty] | 20 | % OPACITY
ID-0009 | ID NAT'L ENGINEERING AND ENVT'L LAB/NUCLEAR TECH | DEPARTMENT OF ENERGY | ID | IDAHO, OTHER | 2000-06-26 | NUCLEAR AND ENVIRONMENTAL RESEARCH AND DEVELOPMENT. | (4) CPP-606 BOILERS AND (1) INTEC PORTABLE BOILER | 13.22 | DISTILLATE | 29976 | GAL/D | FOUR CPP-606 BOILERS AND 1 INTEC PORTABLE BOILER ARE INCLUDED IN THIS ENTRY. | Visible Emissions (VE) | N |  | 20 | % OPACITY | 6 MIN AV |  | 27 | % OPACITY | FOR 1 6 MIN PERIOD /H | 20 | % OPACITY | 6 MIN AV
AK-0058 | NORTHSTAR DEVELOPMENT FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-08-16 | OIL AND GAS EXPLORATION FACILITY | HEATERS | 13.22 | DIESEL | 10 | MMBTU/H | SOURCE ID: 210B, 215, 216, 217, AND 218. | Visible Emissions (VE) | P | GOOD COMBUSTION PRACTICE | 20 | % OPACITY | [5 empty] | 20 | % OPACITY |  | VE used as surrogate for PM10 emissions
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | BOILERS (ID NOS. 9-10) | 13.29 | LIQUID FUEL | 400 | BHP, EACH | THIS ENTRY INCLUDES 2 JOHNSTON PFTA-400-3LX-150S BOILERS. FOR PURPOSES OF DEFINING THE SCC AND PROCESS CODES, IT WAS ASSUMED THAT BHP MEANS BOILER HORSE POWER. THE PERMITTEE MAY BURN A USED OIL FUEL BLEND SUBJECT TO THE FOLLOWING CONDITIONS; PERMITTEE SHA | Visible Emissions (VE) | P | GOOD AIR POLLUTION CONTROL PRACTICES ACCORDING TO NSPS. | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H, EACH |  |  |  |  | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H, EACH
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | BOILER (ID NO. 11) | 13.29 | LIQUID FUEL | 400 | BHP | ONE JOHNSTON PFTA-400-3LX-150S BOILER IS INCLUDED IN THIS ENTRY. THE INSTALLATION DATE WAS 1986. THE PERMITTEE MAY BURN A USED OIL FUEL BLEND SUBJECT TO THE FOLLOWING CONDITIONS; PERMITTEE SHALL NOT BURN USED OIL WHILE MANUFACTURING POLLOCK SURIMI, THE FU | Visible Emissions (VE) | N |  | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H |  |  |  |  | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | BOILER (ID NOS. 12-13) | 13.29 | LIQUID FUEL | 200 | BHP, EACH | FOR PURPOSES OF DEFINING THE SCC AND PROCESS TYPE CODES, IT WAS ASSUMED THAT BHP MEANS BOILER HORSEPOWER. THE PERMITTEE MAY BLEND FISH OIL WITH DIESEL FUEL AND MAY ADD FISH OIL TO A USED OIL BLEND UNDER THE FOLLOWING CONDITIONS; PERMITTEE SHALL NOT BURN U | Visible Emissions (VE) | N |  | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H, EACH |  |  |  |  | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H, EACH
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | HOT AIR DRYER (ID NOS. 14-15) | 13.29 |  | 24.1 | MMBTU/H, EACH | TWO STORD INT'L SIDJ-4.5 DRYERS WITH RAY ROTARY BGE-700 BURNERS ARE INCLUDED IN THIS ENTRY. THE DRYERS WERE INSTALLED IN 1990. THE PERMITTEE MAY BLEND FISH OIL WITH DIESEL FUEL AND MAY ADD FISH OIL TO A USED OIL BLEND UNDER THE FOLLOWING CONDITIONS; PERMI | Visible Emissions (VE) | N |  | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H, EACH |  |  |  |  | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H, EACH
AK-0050 | DUTCH HARBOR PLANT | UNISEA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-03-28 | THE DUTCH HARBOR PLANT IS A SEAFOOD PROCESSING FACILITY THAT PROCESSES FISH AND CRABS INTO EDIBLE PRODUCTS FOR HUMAN CONSUMPTION. BYPRODUCTS AND WASTE MATERIAL FROM THE OPERATION ARE PROCESSED INTO FISH MEAL. | HOT AIR DRYER (ID NO. 16) | 13.29 |  | 6.3 | MMBTU/H | ONE ALFA-LAVAL KIX K4 (FME A/S) DRYER WITH MAXON OVENPAK 500-SP BURNER IS INCLUDED IN THIS ENTRY. THE INSTALLATION DATE WAS 1997. THE PERMITTEE MAY BLEND FISH OIL WITH DIESEL FUEL AND MAY ADD FISH OIL TO A USED OIL BLEND UNDER THE FOLLOWING CONDITIONS; PE | Visible Emissions (VE) | N |  | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H |  |  |  |  | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | SOYBEAN EXTRACTION PLANT | BOILER, NO 2 FUEL OIL | 13.22 | NO 2 FUEL OIL | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. Fuel oil is backup fuel. There is a separate entry for this boiler when firing natural gas. | Visible Emissions (VE) | N |  | 20 | % OPACITY | 6-minute average |  |  |  |  | 20 | % OPACITY | 6-minute average
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | SOYBEAN EXTRACTION PLANT | BOILER, NO 2 FUEL OIL | 13.22 | NO 2 FUEL OIL | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. Fuel oil is backup fuel. There is a separate entry for this boiler when firing natural gas. | Visible Emissions (VE) | N |  | 20 | % OPACITY | 6-minute average |  |  |  |  | 20 | % OPACITY | 6-minute average
AK-0060 | DUTCH HARBOR SEAFOOD PROCESSING FACILITY | WESTWARD SEAFOODS, INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2003-10-10 | FISH PROCESSING PLANT | BOILER, FUEL OIL, (2) | 13.29 | DISTILLATE OIL | 29.3 | MMBTU/H | Throughput for each. Cleaver-Brooks firetube boiler, Model No. NCB-100-700-200. Boilers use a mixture of distillate fuel oil, fish oil, used oil. | Visible Emissions (VE) | P | GOOD COMBUSTION, CLEAN FUEL | 20 | % OPACITY | 6 min avg |  |  |  |  | 20 | % OPACITY |  | Basis is state rule, opacity used as limit for PM10 BACT.
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NO. 2 FUEL OIL | 13.22 | FUEL OIL #2 | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. USING NATURAL GAS WITH #2 OIL BACKUP. TWO SET OF LIMITS, THIS ONE FOR #2 OIL. EACH BOILER IS RESTRICTED TO 250,000 GALLONS OF FUEL OIL PER ROLLING 12-MONTHS. | Visible Emissions (VE) | N |  | 5 | % OPACITY | AS A 6-MINUTE AVERAGE |  |  |  |  | 5 | % OPACITY | AS A 6-MINUTE AVERAGE | OPACITY AT ANY STACK FROM EITHER BOILER.
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NO. 2 FUEL OIL | 13.22 | FUEL OIL #2 | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. USING NATURAL GAS WITH #2 OIL BACKUP. TWO SET OF LIMITS, THIS ONE FOR #2 OIL. EACH BOILER IS RESTRICTED TO 250,000 GALLONS OF FUEL OIL PER ROLLING 12-MONTHS. | Visible Emissions (VE) | N |  | 5 | % OPACITY | AS A 6-MINUTE AVERAGE |  |  |  |  | 5 | % OPACITY | AS A 6-MINUTE AVERAGE | OPACITY AT ANY STACK FROM EITHER BOILER.
NJ-0045 | MERCK - RAHWAY PLANT | MERCK | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-01-14 | CHEMICAL MANUFACTURING | BOILERS - NO. 2 OIL (2) | 13.22 | NO. 2 OIL | 99.5 | MMBTU/H | NO. 2 FUEL OIL USE SHALL NOT EXCEED 3,987,183 GAL/YR BASED ON AN AVERAGE HEATING VALUE OF 138,500 BTU/GAL OF OIL | Volatile Organic Compounds (VOC) | N | NONE | 0.36 | LB/H |  |  | 0.0036 | LB/MMBTU |  | 0.0036 | LB/MMBTU |  | ADDITIONAL VOC LIMIT IS 50 PPMVD @ 7% O2.
MO-0051 | PROCTOR & GAMBLE PAPER PRODUCTS | Proctor & Gamble Paper Products | MO | MISSOURI DNR, AIR POLL CONTROL PROGRAM | 1998-01-01 | SANITARY TISSUE & TOWEL BUSINESS, EXPANSION TO EXISTING DIAPER MANUFACTURING PLANT | BOILERS, #2 FUEL OIL, (3) | 13.22 | #2 FUEL OIL | 265.7 | KGAL/YR | ADDITIONAL THROUGHPUT INFORMATION: 50 MMBTU/H EACH. # 2 FUEL OIL AS BACK-UP, LIMITED TO HEAT INPUT OF 50 MMBTU/H WHEN USED, MAX OF 744 H/YR, AND OIL MAX SULFUR CONTENT OF 0.34% | Volatile Organic Compounds (VOC) | P | LOW NOX BURNERS, W/O FLUE GAS RECIRC., GOOD COMBUSTION | 0.052 | LB/MMBTU | [5 empty] | 0.052 | LB/MMBTU
TN-0054 | PROCTOR AND GAMBLE MANUFACTURING COMPANY | PROCTOR AND GAMBLE MANUFACTURING COMPANY | TN | TENNESSEE DIV OF AIR POLLUTION CONTROL | 1998-03-19 |  | BOILER | 13.22 | NO. 2 FUEL OIL | 0 |  | STACK TEST TO BE CONDUCTED PRIOR TO OBTAINING AN OPERATING PERMIT. | Volatile Organic Compounds (VOC) | N |  | 4.4 | LB/H |  | 0 | 5.4 | LB/H |  | 0
ME-0017 | MCCAINE FOOD INC | MCCAINE FOOD INC | ME | MAINE DEPARTMENT OF ENV PROTECTION | 1999-03-12 |  | BOILER, STEAM | 13.21 | RESIDUAL OIL | 656.7 | GAL/H | INSTALLATION OF A NEW STEAM BOILER AT 81000 LB/H. THROUGHPUT CAPACITY IS AT STANDARD OPERATING CONDITIONS. | Volatile Organic Compounds (VOC) | N |  | 0.84 | LB/H |  | 0 | 0 |  |  | 0
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | ELECTRICITY GENERATION | AUXILIARY BOILER- DISTILLATE OIL | 13.22 | DISTILLATE FUEL OIL | 99 | MMBTU/H | DISTILLATE OIL USED AS BACK-UP FUEL- SEE NOTES FOR NATURAL GAS IN AUX. BOILER | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.495 | LB/H |  |  | 0.178 | T/YR |  |  |  |  | ADDITIONAL EMISSION LIMIT: 0.005 LB/MMBTU.
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | ELECTRICITY GENERATION | AUXILIARY BOILER- DISTILLATE OIL | 13.22 | DISTILLATE FUEL OIL | 99 | MMBTU/H | DISTILLATE OIL USED AS BACK-UP FUEL- SEE NOTES FOR NATURAL GAS IN AUX. BOILER | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.495 | LB/H |  |  | 0.178 | T/YR |  |  |  |  | ADDITIONAL EMISSION LIMIT: 0.005 LB/MMBTU.
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | SOYBEAN EXTRACTION PLANT | BOILER, NO 2 FUEL OIL | 13.22 | NO 2 FUEL OIL | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. Fuel oil is backup fuel. There is a separate entry for this boiler when firing natural gas. | Volatile Organic Compounds (VOC) | N |  | 1.18 | LB/H |  |  | 5.17 | T/YR |  | 0.014 | LB/MMBTU |  | Using manufacturers test data factors: 8 lb VOC/1,000,000 lb air for natural gas, and 15 lb VOC/1,000,000 lb air for fuel oil.
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | SOYBEAN EXTRACTION PLANT | BOILER, NO 2 FUEL OIL | 13.22 | NO 2 FUEL OIL | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. Fuel oil is backup fuel. There is a separate entry for this boiler when firing natural gas. | Volatile Organic Compounds (VOC) | N |  | 1.18 | LB/H |  |  | 5.17 | T/YR |  | 0.014 | LB/MMBTU |  | Using manufacturers test data factors: 8 lb VOC/1,000,000 lb air for natural gas, and 15 lb VOC/1,000,000 lb air for fuel oil.
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 |  | BOILER NO.2 | 13.22 | DISTILLATE FUEL OIL | 43.2 | MMBTU | One of two units | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.23 | LB/H | each unit | [7 empty] | One of two units
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 |  | BOILER NO.2 | 13.22 | DISTILLATE FUEL OIL | 43.2 | MMBTU | One of two units | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.23 | LB/H | each unit | [7 empty] | One of two units
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, DISTILLATE OIL (1) | 13.22 | #2 FUEL OIL | 40 | MMBTU/H | AUXILIARY BOILER. | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION. | 0.003 | LB/MMBTU
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, DISTILLATE OIL (1) | 13.22 | #2 FUEL OIL | 40 | MMBTU/H | AUXILIARY BOILER. | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION. | 0.003 | LB/MMBTU
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NO. 2 FUEL OIL | 13.22 | FUEL OIL #2 | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. USING NATURAL GAS WITH #2 OIL BACKUP. TWO SET OF LIMITS, THIS ONE FOR #2 OIL. EACH BOILER IS RESTRICTED TO 250,000 GALLONS OF FUEL OIL PER ROLLING 12-MONTHS. | Volatile Organic Compounds (VOC) | N |  | 0.03 | LB/H |  |  | 0.5 | T/YR |  | 0.0015 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NO. 2 FUEL OIL | 13.22 | FUEL OIL #2 | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. USING NATURAL GAS WITH #2 OIL BACKUP. TWO SET OF LIMITS, THIS ONE FOR #2 OIL. EACH BOILER IS RESTRICTED TO 250,000 GALLONS OF FUEL OIL PER ROLLING 12-MONTHS. | Volatile Organic Compounds (VOC) | N |  | 0.03 | LB/H |  |  | 0.5 | T/YR |  | 0.0015 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.

## Data <100 MMBTU - Gaseous Fuel
RBLCID | FACILITYNAME | CORPORATEORCOMPANYNAME | FACILITYSTATE | AGENCYNAME | PERMITDATE | YEAR | FACILITYDESCRIPTION | PROCESSNAME | PROCTYPE | FUEL | THRUPUT | THRUPUTUNIT | PROCESSNOTES | POLLUTANT | CONTROLCOD | CTRLDESC | EMISLIMIT1 | EMISLIMIT1UNIT | EMISLIMIT1AVGTIMECONDITION | EMISLIMIT2 | EMISLIMIT2UNIT | EMISLIMIT2AVGTIMECONDITION | STDEMISSLIMIT | STDUNITLIMIT | STDLIMITAVGTIMECONDITION | POLLUTANTCOMPLIANCENOTES
TX-0309 | FORMOSA PLASTICS TEXAS | FORMOSA PLASTICS CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-02-10 | 2000 | THIS PERMIT AUTHORIZES THE OPERATION OF THE FORMOSA ETHYLENE GLYCOL PLANT & A PRODUCTION INCREASE, EQUIPMENT UPGRADES & CHANGES, ADDITIONAL FUGITIVE EMISSIONS, & AN ADDITIONAL COOLING TOWER CELL. THE APPLICANT WISHES TO CONSOLIDATE ALL FUGITIVE EMISSION P | WASTE HEAT BOILER, 70Z401 | 13.31 | NAT GAS |  |  | SHALL BE MAINTAINED AT A MINIMUM COMBUSTION CHAMBER TEMP OF 1450 F. | Acrylonitrile | N | NONE INDICATED | 0.12 | LB/H |  | 0.52 | T/YR
MA-0029 | SITHE MYSTIC DEVELOPMENT LLC | SITHE MYSTIC DEVELOPMENT LLC | MA | MASSACHUSETTS DIV OF AIR QUAL CONTROL | 1999-09-29 | 1999 | COMBINED CYCLE ELECTRIC GENERATING FACILITY | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 96 | MMBTU/H |  | Ammonia (NH3) | A | VAPOR TREATMENT SYSTEM. NO EMISSION RATE LIMITS PROVIDED.
CA-0919 | COCA COLA | COCA COLA | CA | SOUTH COAST AQMD, CA | 1999-11-23 | 1999 |  | BOILER, FIRE TUBE | 13.31 | NATURAL GAS | 31.5 | MMBTU/H | ARB RECORD # A310-947-00 SCOTCH MARINE CUSTOM FIRE-TUBE BOILER USED TO PROVIDE STEAM FOR SANITATION. BACT LIMITS ARE APPLIED TO NOX AND CO LEVELS. NO BACT LIMITS WERE APPLIED TO PM, ROG, AND SOX. DEFAULT EMISSION FACTORS ARE THE BASIS OF THE PM, ROG AND S | Ammonia (NH3) | N | NO CONTROL | 5 | PPMVD @ 3% O2
CA-0938 | CHILDREN'S HOSPITAL LOS ANGELES | CHILDREN'S HOSPITAL LOS ANGELES | CA | SOUTH COAST AQMD, CA | 1999-12-02 | 1999 | BOILERS USED TO PRODUCE STEAM. | BOILER, (3) | 13.31 | NATURAL GAS | 33.9 | MMBTU/H | 3 boilers, one 33.9 MMBtu/h and two 24.2 MMBtu/h each. Limits and controls for each boiler are the same. BACT review for CO and NOx, NH3 also included. | Ammonia (NH3) | P | SCR STOICHIOMETRY | 5 | PPMVD | at 3% O2 | [6 empty] | Limit is dry, averaged over 15 minutes and corrected to 3% O2.
CA-1021 | DAMAPONG TEXTILES | DAMAPONG TEXTILES | CA | SOUTH COAST AQMD, CA | 1999-12-07 | 1999 |  | BOILER: 16.5 MMBTU/H | 13.31 | NATURAL GAS | 16.5 | MMBTU/H | EQUIP: NATURAL GAS FIRED-TUBE BOILER, MFR: SELLERS ENGINEERING, MODEL: 105E-395 HP, FUNC EQUIP: TO PROVIDE STEAM FOR A DYE TANK, SCHEDULE: VARIABLE, | Ammonia (NH3) | N |  | 5 | NH3PPMVD @ 3% O2 | 15-MIN
TX-0309 | FORMOSA PLASTICS TEXAS | FORMOSA PLASTICS CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-02-10 | 2000 | THIS PERMIT AUTHORIZES THE OPERATION OF THE FORMOSA ETHYLENE GLYCOL PLANT & A PRODUCTION INCREASE, EQUIPMENT UPGRADES & CHANGES, ADDITIONAL FUGITIVE EMISSIONS, & AN ADDITIONAL COOLING TOWER CELL. THE APPLICANT WISHES TO CONSOLIDATE ALL FUGITIVE EMISSION P | WASTE HEAT BOILER, 70Z401 | 13.31 | NAT GAS |  |  | SHALL BE MAINTAINED AT A MINIMUM COMBUSTION CHAMBER TEMP OF 1450 F. | Ammonia (NH3) | N | NONE INDICATED | 5.1 | LB/H |  | 22.34 | T/YR
CA-0946 | LACORR PACKAGING | LACORR PACKAGING | CA | SOUTH COAST AQMD, CA | 2000-07-12 | 2000 | PROVIDE STEAM FOR CARDBOARD MANUFACTURING | BOILER | 13.31 | NATURAL GAS | 21 | MMBTU/H | CLEAVER BROOKS MODEL CB-LE 500 BOILER | Ammonia (NH3) | P | SCR STOICHIOMETRY | 5 | PPMVD | Corrected to 3% O2 | [6 empty] | NH3 15 MIN @ 3% O2
AR-0076 | U.S. ARMY, PINE BLUFF ARSENAL | U.S. ARMY, PINE BLUFF ARSENAL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-02-17 | 2004 | PINE BLUFF ARSENAL IS THE ARMY'S ONLY CHEMICAL ARSENAL AND THE ONLY INSTALLATION WITH BOTH MANUFACTURING AND DEPOT FUNCTIONS. OPERATIONAL FUNCTIONS INCLUDE: AMMUNITION OPERATIONS; CHEMICAL AND BIOLOGICAL DEFENSE OPERATIONS; PRODUCT AND PROCESS DEVELOPMENT | BOILER, PROCESS STEAM, (2) SN-PBCDF-03, -04 | 13.31 | NATURAL GAS | 0.03 | MMDSCF/H | THROUGH PUT FOR EACH. ADDITIONAL THROUGHPUT: 28.4 MMBTU/H (EACH). PROCESS STEAM BOILER SERVES BRINE REDUCTION AREA EQUIPMENT. | Beryllium / Beryllium Compounds | P | NATURAL GAS ONLY. | 3.41 | E-7 LB/H | EACH | [6 empty] | BACT FOR PM WILL BE CONSIDERED AS BACT FOR BE.
AR-0076 | U.S. ARMY, PINE BLUFF ARSENAL | U.S. ARMY, PINE BLUFF ARSENAL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-02-17 | 2004 | PINE BLUFF ARSENAL IS THE ARMY'S ONLY CHEMICAL ARSENAL AND THE ONLY INSTALLATION WITH BOTH MANUFACTURING AND DEPOT FUNCTIONS. OPERATIONAL FUNCTIONS INCLUDE: AMMUNITION OPERATIONS; CHEMICAL AND BIOLOGICAL DEFENSE OPERATIONS; PRODUCT AND PROCESS DEVELOPMENT | BOILER, HOT WATER, (2) SN-PBCDF-05, -06 | 13.31 | NATURAL GAS | 0.01 | MMDSCF/H | ADDITIONAL THROUGHPUT: 11.7 MMBTU/H, THROUGHPUT FOR EACH. | Beryllium / Beryllium Compounds | P | NATURAL GAS ONLY. | 1.4 | E-7 LB/H
*AL-0231 | NUCOR DECATUR LLC | NUCOR CORPORATION | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-06-12 | 2007 | THE FACILITY PRODUCES STEEL COILS PRIMARILY FROM STEEL SCRAP USING THE ELECTRIC ARC FURNACE (EAF) PROCESS. | VACUUM DEGASSER BOILER | 13.31 | NATURAL GAS | 95 | MMBTU/H |  | Carbon Dioxide | N |  | 0.061 | LB/MMBTU |  | 5.8 | LB/H
*NE-0043 | NATUREWORKS, LLC |  | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2007-10-01 | 2007 | POLYMER PRODUCTION FACILITY | HOT OIL HEATER | 13.31 |  |  |  |  | Carbon Dioxide | P | GOOD COMBUSTION PRACTICES
NJ-0045 | MERCK - RAHWAY PLANT | MERCK | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-01-14 | 1997 | CHEMICAL MANUFACTURING | BOILERS - NAT GAS (3) | 13.31 | NATURAL GAS | 99.5 | MMBTU/H |  | Carbon Monoxide | N | NONE | 3.6 | LB/H |  | 0.036 | LB/MMBTU |  | 0.036 | LB/MMBTU |  | ADDITIONAL CO LIMIT IS 50 PPMVD @ 7% O2.
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 8 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 50 | MMBTU/H | THE NUMBER 8 PAPER MACHINE CONSISTS OF THREE SOURCES: THE NATURAL GAS FIRED BURNERS, THE PAPER MACHINE, AND THE DUST SYSTEM. STACK TESTING FOR CO AND NOX. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 0.1139 | LB/MMBTU |  | 0 |  |  | 0.1139 | LB/MMBTU
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 5 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 21 | MMBTU/H | THE BURNERS FOR THE NUMBER 5 PAPER MACHINE HAVE BEEN UPGRADED. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.2142 | LB/MMBTU |  | 0 |  |  | 0.2142 | LB/MMBTU
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 6 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 58.4 | MMBTU/H | THE BURNERS FOR THE NUMBER 6 PAPER MACHINE HAVE BEEN UPGRADED. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 0.1139 | LB/MMBTU |  | 0 |  |  | 0.1139 | LB/MMBTU
AR-0019 | QUINCY SOYBEAN COMPANY OF ARKANSAS | QUINCY SOYBEAN COMPANY OF ARKANSAS | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-03-04 | 1997 |  | BOILER, COGENERATION/WASTE HEAT RECOVERY | 13.31 | NATURAL GAS | 68 | MMBTU/H | TURBINE AND WASTE HEAT RECOVERY BOILER BOTH EXHAUST THROUGH SN-65 THROUGHPUT: 68 MMBTU/H AND 79 MMBTU/H | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 10.6 | LB/H |  | 0 |  |  | 0.15588 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HIGH PRESSURE BOILER #2-R2 | 13.31 | FUEL OIL | 0.3 | MMBTU/H | PERMIT NO: 97-A-416 FUEL OIL < 10,674,202 GALLONS/Y PER WHOLE FACILITY SULFUR CONTENT OF FUEL OIL < 0.05 % BY WEIGHT | Carbon Monoxide | P | LOW NOX/FGR | 1.3 | LB/H |  | 5.7 | T/YR |  | 4.3 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #3 B3 | 13.31 | NATURAL GAS | 2.3 | MMBTU/HR | BOILER BURNS NATURAL GAS OR FUEL OIL. PERMIT NO: 97-A-408 20% OPACITY PER NSPS SUBPART DC SO2 SET AT 9.46 TPY TO STAY UNDER PSD SIGNIFICANCE | Carbon Monoxide | P | LOW NOX BURNER, FLUE GAS RECIRC. | 9.9 | LB/H |  | 43.36 | T/YR |  | 4.3 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #2 B2 | 13.31 | NATURAL GAS | 2.3 | MMBTU/H | 20% OPACITY BY NSPS SUBPART DC SO2 - 9.46 TPY TO STAY UNDER PSD SIGNIFICANCE | Carbon Monoxide | P | LOW NOX BURNER , FLUE GAS RECIRC. | 9.9 | LB/H |  | 43.36 | T/YR |  | 4.3 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #1 | 13.31 | NATURAL GAS | 2.3 | MMBTU/H | FUEL IS NATURAL GAS AND FUEL OIL ONLY. PERMIT NUMBER: 97-A-377. 20 % OPACITY NSPS SUBPART BC SO2 - 9.46 TPY, SET TO STAY UNDER PSD SIGNIFICANCE LEVELS | Carbon Monoxide | P | LOW NOX BURNER, FLEE GAS RECIRC. | 9.9 | LB/H |  | 43.36 | T/YR |  | 4.3 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HYDROGEN PLANT BURNER R9 | 13.31 |  |  |  | PERMIT NUMBER: 97-A-391 20% OPACITY - 1A 23.3(2)D. THIS PROCESS GENERATES HYDROGEN FROM NATURAL GAS. THE HYDROGEN IS USED FOR THE HYDROGENATION OF THE SOYBEAN OIL. | Carbon Monoxide | N |  | 0.53 | LB/H |  | 2.3 | T/YR |  | 0.034 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HIGH PRESSURE BOILER #1 | 13.31 | NATURAL GAS | 0.3 | MMBTU/H | FUELS ARE NATURAL GAS AND #2FUEL OIL. PERMIT NUMBER 97-A-390 20% OPACITY BY NSPS SUBPART DC SO2 LIMIT 1.26 TPY TO STAY UNDER PSD SIGNIFICANCE | Carbon Monoxide | N |  | 1.3 | LB/H |  | 5.7 | T/YR |  | 4.3 | LB/MMBTU
WI-0188 | GOLDEN BOOKS PUBLISHING COMPANY INC. | GOLDEN BOOKS PUBLISHING COMPANY INC. | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 1997-06-24 | 1997 | PRINTING FACILITY | SPACE HEAT & COMBUSTION SOURCES, (P01 S01) | 13.31 | NATURAL GAS | 93 | MMBTU/H | SECOND FUEL: PROPANE | Carbon Monoxide | N | REGULATORY BASIS: STATE REGULATION. | 3.19 | LB/H |  |  |  |  | 0.034 | LB/MMBTU
LA-0115 | GEISMAR PLANT | SHELL CHEMICAL COMPANY | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1997-11-03 | 1997 | PERMIT FOR A NEW POLYMER PRODUCTION COMPLEX AT AN EXISTING SOCMI FACILITY | HEATER, HOT OIL | 13.31 | NATURAL GAS | 54.9 | MMBTU/H |  | Carbon Monoxide | P | PROPER OPERATING TECHNIQUES WITH AUTOMATIC COMBUSTION CONTROL, 2% EXCESS O2 | 2.09 | LB/H |  | 8.24 | T/YR |  | 0.038069 |  | NOT AVAILABLE
PA-0149 | BUCKNELL UNIVERSITY | BUCKNELL UNIVERSITY | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 1997-11-26 | 1997 |  | HEAT RECOVERY BOILER | 13.31 | NG SUPPLEMENT | 24000 | LB/HR STEAM | COMPLIANCE WILL BE VERIFIED BY STACK TESTS. ENERGY RECOVERY INTERNATIONAL HSRG RATED AT 70,000 LB STEAM/HR WHEN SUPPLEMENTAL FUEL IS FIRED. EMISSION LIMITATIONS APPLY WHEN TURBINE IS IN OPERATION. | Carbon Monoxide | N |  | 0.1 | LB/MMBTU |  | 5.03 | LB/HR |  | 0.1 | LB/MMBTU
LA-0113 | BASF CORPORATION | BASF CORPORATION | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1997-12-30 | 1997 |  | DUCT BURNER, COGEN UNIT NO. 2 | 13.31 | NATURAL GAS | 0.4 | MMLB/H STEAM |  | Carbon Monoxide | P | GOOD DESIGN, PROPER OPERATING PRACTICES, 2% EXCESS O2 | 83.93 | LB/H |  |  |  |  | 0.4 | MMLB/H STEAM | NOT AVAILABLE
LA-0112 | GEISMAR FACILITY | AIR LIQUIDE AMERICA CORP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1998-02-13 | 1998 | AIR SEPARATION TO PRODUCE NITROGEN AND OXYGEN IN LIQUIDIZED GAS FORMS - ALSO TRANSPORT. PROJECT: NEW COGEN UNIT, NATURAL GAS FIRED FRAME 7 GE TURBINE WITH DUCT BURNER. | BOILER NO. 1 | 13.31 | NATURAL GAS | 95 | MMBTU/H |  | Carbon Monoxide | P | GOOD DESIGN, PROPER OPERATING PRACTICES AND 2% EXCESS O2 | 5.7 | LB/H | HOURLY MAXIMUM | 24.97 | T/YR | ANNUAL MAXIMUM | 0.06 | LB/MMBTU | THREE ONE-HOUR TEST AVERAGE
LA-0112 | GEISMAR FACILITY | AIR LIQUIDE AMERICA CORP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1998-02-13 | 1998 | AIR SEPARATION TO PRODUCE NITROGEN AND OXYGEN IN LIQUIDIZED GAS FORMS - ALSO TRANSPORT. PROJECT: NEW COGEN UNIT, NATURAL GAS FIRED FRAME 7 GE TURBINE WITH DUCT BURNER. | REACTIVATION HEATERS (2) | 13.31 |  | 9 | MMBTU/H | THROUGHPUT FOR EACH UNIT | Carbon Monoxide | N |  | 0.4 | LB/H | HOURLY MAXIMUM | 1.75 | T/YR | ANNUAL MAXIMUM | 0.044 | LB/MMBTU | CALCULATED
MI-0283 | WESTERN MICHIGAN UNIVERSITY | WESTERN MICHIGAN UNIVERSITY | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 1998-04-27 | 1998 | POWER PLANT | DUCT BURNER, 2 EACH | 13.31 | NATURAL GAS | 85 | MMBTU/H | THROUGHPUT FOR EACH. BY STACK TESTING IT WAS FOUND THAT WHEN OPERATED WITHOUT THE UPSTREAM TURBINE (IN THE FRESH AIR FIRING MODE), THE DUCT BURNERS PERFORMED NO BETTER THAN 0.17 LB/MMBTU. ONLY CO AND NOX WERE ADDRESSED IN THIS DETERMINATION. | Carbon Monoxide | N |  | 6.8 | LB/H |  | 29.9 | T/YR, FRESH AIR MODE |  | 0.08 | LB/MMBTU |  | THESE LIMITS APPLY TO DUCT BURNERS OPERATING IN THE FRESH AIR MODE.
WY-0051 | UNION PACIFIC RESOURCES - PATRICK DRAW GAS PLANT | UNION PACIFIC RESOURCES - PATRICK DRAW GAS PLANT | WY | WYOMING AIR QUAL DIV, DEPT OF ENV QUAL | 1998-05-18 | 1998 |  | HEATER, 2 EA | 13.31 | NATURAL GAS | 45 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE. | 0.04 | LB/MMBTU |  | 0 |  |  | 0.04 | LB/MMBTU
WY-0052 | UNION PACIFIC RESOURCES - PATRICK DRAW GAS PLANT | UNION PACIFIC RESOURCES - PATRICK DRAW GAS PLANT | WY | WYOMING AIR QUAL DIV, DEPT OF ENV QUAL | 1998-05-18 | 1998 |  | HEATER, 2 EA | 13.31 | NATURAL GAS | 45 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE. | 0.04 | LB/MMBTU |  | 0 |  |  | 0.04 | LB/MMBTU
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | 1998 | VEGETABLE OIL PLANT | BOILER, NEBRASKA, NAT GAS | 13.31 | NATURAL GAS | 28 | MMBTU/H | See separate process for backup fuel (No. 2 oil) requirements. | Carbon Monoxide | N |  | 1 | LB/H |  |  |  |  | 0.036 | LB/MMBTU
IN-0104 | CON AGRA SOYBEAN PROCESSING CO. | CON AGRA SOYBEAN PROCESSING CO. | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1998-08-14 | 1998 | SOYBEAN PROCESSING | BOILERS, REFINERY & HYDROGEN PLANT REFORMER | 13.31 | NATURAL GAS | 10 | MMBTU/H | 2 refinery boilers: 10 mmBtu/h each; 1 hydrogen plant reformer boiler: 20 mmBtu/h | Carbon Monoxide | P | COMBUSTION CONTROL | 0.074 | MMBTU/H |  |  |  |  | 0.074 | MMBTU/H
TX-0300 | SALT CREEK GAS PLANT | MOBIL EXPLORATION & PRODUCING US INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-10-13 | 1998 | MOBIL EXPLORATION & PRODUCING US INC HAS REQUESTED AN AMENDMENT TO PERMIT NO 20660 AND A MODIFICATION TO PSD-TX-795 TO (1) INCREASE THE CO AND VOC ALLOWABLES ON THEIR COOPER-BESSEMER GMVH-12C2 ENGINES TO ALLOW THEM TO BETTER CONTROL NOX TO THE 2 G/HP-H LE | HOT OIL HEATER, EPN 26 | 13.31 | NAT GAS | 32.2 | MMBTU/H |  | Carbon Monoxide | N | NONE INDICATED | 35 | LB/MMSCF |  | 0.42 | LB/H |  | 0.013 | LB/MMBTU | CALCULATED USING THROUGHPUT | ADDITIONAL EMISSION LIMITS: 1.84 T/YR
OH-0245 | REPUBLIC TECHNOLOGIES INTERNATIONAL | REPUBLIC TECHNOLOGIES INTERNATIONAL/CANTON | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 1999-01-27 | 1999 | STEEL MILL. THIS PLANT IS PSD FOR PM, SO2, NOX, CO, AND VOC. THIS MODIFICATION IS A SIGNIFICANT INCREASE FOR NOX. | ECCENTRIC BOTTOM TAPPING LADLE PREHEATER FURNACE | 13.31 | NATURAL GAS | 14 | MMBTU/H |  | Carbon Monoxide | N |  | 1.2 | LB/H |  | 5.3 | T/YR |  | 0.086 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 1 (NATURAL GAS) | 13.31 | NATURAL GAS | 84.4 | MMBTU/H | MFR. IS COMBUSTION ENGINEERING. ONLY NATURAL GAS, A MIXTURE OF NO. 2 OIL AND LASALOCID OIL, AND NO. 2 OIL SHALL BE FIRED IN BOILER 1. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. AFTER APRIL 3 | Carbon Monoxide | N | NONE LISTED | 3 | LB/H |  | 37 | PPMVD @ 7% O2 |  | 0.036 | LB/MMBTU
CO-0040 | AMERICAN SODA, LLP, PARACHUTE FACILITY |  | CO | COLORADO DEPT OF HEALTH - AIR POLL CTRL | 1999-05-06 | 1999 |  | INDUSTRIAL BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 80.8 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION MANAGEMENT. CAPITAL AND ANNUALIZED COSTS ARE INCLUDED IN OPERATION AND MAINTENANCE | 0.09 | LB/MMBTU |  |  |  |  | 0.09 | LB/MMBTU
CO-0041 | AMERICAN SODA, LLP, PINEANCE FACILITY |  | CO | COLORADO DEPT OF HEALTH - AIR POLL CTRL | 1999-05-06 | 1999 |  | BOILER NO.2, TEST MINE HOT WATER (1) | 13.31 | NATURAL GAS | 51.08 | MMBTU | NATURAL GAS FIRED HOT WATER BOILER PRODUCES HIGH PRESSURE HOT WATER FOR INJECTION INTO THE WELLS. ONLY NOX, CO AND PM EMISSION LIMITS HAVE BEEN PROVIDED FOR THIS PROCESS. | Carbon Monoxide | P | GOOD COMBUSTION | 0.09 | LB/MMBTU |  | 0.2 | T/YR |  | 0.09 | LB/MMBTU
CA-0917 | SOUTHERN CALIFORNIA GAS COMPANY | SOUTHERN CALIFORNIA GAS COMPANY | CA | SOUTH COAST AQMD, CA | 1999-08-17 | 1999 |  | HOT OIL HEATER, AMERICAN HEATER COMPANY | 13.31 | NATURAL GAS | 6.5 | MMBTU/H | ARB RECORD # A310-944-00 AMERICAN HEATER COMPANY MODEL AHE-650 HOT OIL HEATER USED TO REGENERATE LIQUID ABSORBENT (TRIETHYLENE GLYCOL) BY HEATING IT TO APPROXIMATELY 450 DEGREES F. TO REMOVE ABSORBED WATER. PERMIT SETS LIMITS FOR NOX AND CO, NO OTHER POLL | Carbon Monoxide | P | POWER FLAME MODEL C5-G-30B LOW-NOX BURNER. | 50 | PPMVD @ 3% O2 |  |  |  |  | 0.3 | LB/MMBTU
CA-0948 | MARUCHAN, INC. | MARUCHAN, INC. | CA | SOUTH COAST AQMD, CA | 1999-09-09 | 1999 | PASTA AND MACARONI PRODUCTION FACILITY | BOILER, (2) | 13.31 | NATURAL GAS | 8.18 | MMBTU/H | 2 BOILERS, MIURA MODEL LX-200SG | Carbon Monoxide | N |  | 100 | PPMVD | Corrected to 3% O2 |  |  |  | 0.074 | LB/MMBTU | Calculated using F-Factor | CO 15 MIN @ 3% O2
MA-0029 | SITHE MYSTIC DEVELOPMENT LLC | SITHE MYSTIC DEVELOPMENT LLC | MA | MASSACHUSETTS DIV OF AIR QUAL CONTROL | 1999-09-29 | 1999 | COMBINED CYCLE ELECTRIC GENERATING FACILITY | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 96 | MMBTU/H |  | Carbon Monoxide | A | OXIDATION CATALYST | 7.7 | LB/H |  | 100 | PPM @ 15% O2 |  | 0.08 | LB/MMBTU
OK-0051 | GREEN COUNTRY ENERGY PROJECT | COGENTRIX ENERGY INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 1999-10-01 | 1999 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS |  |  |  | Carbon Monoxide | P | BOILER DESIGN & GOOD OPERATING PRACTICES | 0.082 | LB/MMBTU |  |  |  |  | 0.082 | LB/MMBTU
CA-0923 | ARAMARK UNIFORM CLEANERS | ARAMARK UNIFORM CLEANERS | CA | SAN JOAQUIN VALLEY APCD - CENTRAL REGIONAL OFFICE, CA | 1999-10-04 | 1999 | FACILITY PROCESS SOLVENT-LADEN TOWELS AND UNIFORMS. ITEMS ARE COUNTED ON A TABLE SERVED BY AN UNCONTROLLED EXHAUST HOOD AND PLACED INTO INDUSTRIAL WASHERS AND DRYERS (CHALLENGER CPG4-3S3L BURNERS, 2.75 MMBTU/H) | DRYER, NATURAL GAS | 13.31 | NATURAL GAS | 2.75 | MMBTU/H | ARB RECORD # A340-951-00. DRYER PROCESSES SOLVENT LADEN TOWELS, < 950 LB TOWELS/DAY. BACT NOT TRIGGERED FOR PM10 OR SOX | Carbon Monoxide | P | NATURAL GAS-FIRED BURNER | 0.348 | LB/MMBTU |  |  |  |  | 0.348 | LB/MMBTU
CA-0919 | COCA COLA | COCA COLA | CA | SOUTH COAST AQMD, CA | 1999-11-23 | 1999 |  | BOILER, FIRE TUBE | 13.31 | NATURAL GAS | 31.5 | MMBTU/H | ARB RECORD # A310-947-00 SCOTCH MARINE CUSTOM FIRE-TUBE BOILER USED TO PROVIDE STEAM FOR SANITATION. BACT LIMITS ARE APPLIED TO NOX AND CO LEVELS. NO BACT LIMITS WERE APPLIED TO PM, ROG, AND SOX. DEFAULT EMISSION FACTORS ARE THE BASIS OF THE PM, ROG AND S | Carbon Monoxide | P | GOOD COMBUSTION PRATICES. | 50 | PPMVD @ 3% O2 |  |  |  |  | 0.037 | LB/MMBTU
CA-0918 | SCHI SANTA MONICA BEACH HOTEL ASSOCIATES | SCHI SANTA MONICA BEACH HOTEL ASSOCIATES | CA | CALIFORNIA AIR RESOURCES BOARD | 1999-12-02 | 1999 |  | CLAYTON WATER-TUBE BOILER | 13.31 | NATURAL GAS | 4.29 | MMBTU/H | ARB RECORD # A310-945-00 CLAYTON MODEL E6100-LNB WATER TUBE BOILER USED TO SUPPLY HOT WATER BACT LIMITS SET FOR NOX AND CO. NO EMISSIONS LIMITS ON PM, VOC AND SOX. | Carbon Monoxide | P | ULTRA LOW-NOX BURNER SYSTEM | 100 | PPMVD @ 3% O2 |  |  |  |  | 0.075 | LB/MMBTU
CA-0938 | CHILDREN'S HOSPITAL LOS ANGELES | CHILDREN'S HOSPITAL LOS ANGELES | CA | SOUTH COAST AQMD, CA | 1999-12-02 | 1999 | BOILERS USED TO PRODUCE STEAM. | BOILER, (3) | 13.31 | NATURAL GAS | 33.9 | MMBTU/H | 3 boilers, one 33.9 MMBtu/h and two 24.2 MMBtu/h each. Limits and controls for each boiler are the same. BACT review for CO and NOx, NH3 also included. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 50 | PPMVD | at 3% O2 |  |  |  | 0.037 | LB/MMBTU | Calculated using F-Factor
CA-1021 | DAMAPONG TEXTILES | DAMAPONG TEXTILES | CA | SOUTH COAST AQMD, CA | 1999-12-07 | 1999 |  | BOILER: 16.5 MMBTU/H | 13.31 | NATURAL GAS | 16.5 | MMBTU/H | EQUIP: NATURAL GAS FIRED-TUBE BOILER, MFR: SELLERS ENGINEERING, MODEL: 105E-395 HP, FUNC EQUIP: TO PROVIDE STEAM FOR A DYE TANK, SCHEDULE: VARIABLE, | Carbon Monoxide | N |  | 50 | PPMVD @ 3% O2 | 15-MIN AVG | [5 empty] | NOT AVAILABLE
CA-0939 | HI-COUNTRY | HI-COUNTRY FOODS | CA | SOUTH COAST AQMD, CA | 1999-12-16 | 1999 | BOILER USED TO SUPPLY STEAM TO HEAT EVAPORATORS AND PASTEURIZING SYSTEMS. | BOILER | 13.31 | NATURAL GAS | 20.9 | MMBTU/H | Fire tube boiler equipped with low NOx burners. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 10 | PPMVD | Corrected to 3% O2 |  |  |  | 0.074 | LB/MMBTU | Calculated using F-Factor | CO 15 MIN @ 3% O2
CA-1006 | HI-COUNTRY | HI-COUNTRY | CA | SOUTH COAST AQMD, CA | 1999-12-16 | 1999 |  | BOILER, 20.9 MMBTU/H | 13.31 | NATURAL GAS | 20.9 | MMBTU/H | EQUIP: ALZETA, ULTRA LOW NOX BURNER, MFR: CLEAVER BROOKS, TYPE: FIRE TUBE, MODEL: CB 700, FUNC EQUIP: SUPPLY STEAM TO HEAT EVAPORATOR/PASTEURIZING SYS., FUEL_TYPE: , SCHEDULE: CONTINUOUS, H/D: 24, D/W: 7, W/Y: 52, NOTES: SOURCE TEST RESULTS: AVG. NOX (PPM | Carbon Monoxide | N |  | 100 | PPMVD @ 3% O2 | 15 MIN AVG |  |  |  | 0.07 | LB/MMBTU | CALCULATED
OK-0050 | ONETA GENERATING STA | CALPINE CORP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2000-01-21 | 2000 | ELECTRIC GENERATION PLANT | DUCT BURNERS (4) | 13.31 | NATURAL GAS | 328 | MMBTU/H | The emission limits indicted are for the duct burners only. Emission limits for the turbines associated with these duct burners are provided under the process Combustion Turbines | Carbon Monoxide | P | COMBUSTION CONTROL | 0.1 | LB/MMBTU |  |  |  |  | 0.1 | LB/MMBTU
CA-0941 | SANTA MONICA - UCLA MEDICAL CENTER | SANTA MONICA - UCLA MEDICAL CENTER | CA | SOUTH COAST AQMD, CA | 2000-01-28 | 2000 | BOILER USED TO PRODUCE HOT WATER AND STEAM | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 16.3 | MMBTU/H | CLEAVER BROOKS MODEL CE (LE) 200-400 FIRE-TUBE BOILER | Carbon Monoxide | P | FLUE GAS RECIRCULATION | 50 | PPMVD | Corrected to 3% O2 |  |  |  | 0.037 | LB/MMBTU | Calculated using F-Factor | CO 15 MIN @ 3% O2
TX-0309 | FORMOSA PLASTICS TEXAS | FORMOSA PLASTICS CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-02-10 | 2000 | THIS PERMIT AUTHORIZES THE OPERATION OF THE FORMOSA ETHYLENE GLYCOL PLANT & A PRODUCTION INCREASE, EQUIPMENT UPGRADES & CHANGES, ADDITIONAL FUGITIVE EMISSIONS, & AN ADDITIONAL COOLING TOWER CELL. THE APPLICANT WISHES TO CONSOLIDATE ALL FUGITIVE EMISSION P | WASTE HEAT BOILER, 70Z401 | 13.31 | NAT GAS |  |  | SHALL BE MAINTAINED AT A MINIMUM COMBUSTION CHAMBER TEMP OF 1450 F. | Carbon Monoxide | N | NONE INDICATED | 81 | LB/H |  | 247 | T/YR |  |  |  | NOT AVAILABLE | ADDITIONAL EMISSION LIMITS: 100 PPM @ 7% O2 24 H AV. THE CO EMISSION LIMITS APPLY WHENEVER HAZARDOUS WASTE IS BEING BURNED IN THE BOILER. HAZARDOUS WASTE MAY NOT BE BURNED IN THE WASTE HEAT BOILER UNTIL AND UNLESS APPROPRIATE AUTHORITY IS OBTAINED UNDER R
CA-0942 | SAN BERNARDINO COUNTY MEDICAL CENTER | SAN BERNARDINO COUNTY MEDICAL CENTER | CA | SOUTH COAST AQMD, CA | 2000-02-15 | 2000 | BOILER USED TO PRODUCE STEAM TO HEAT BUILDING. | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 6 | MMBTU/H | CLEAVER BROOKS MODEL FLX-700-600 | Carbon Monoxide | N |  | 50 | PPMVD | Corrected to 3% O2 |  |  |  | 0.037 | LB/MMBTU | Calculated using F-Factor | CO 15 MIN @ 3% O2
CA-0942 | SAN BERNARDINO COUNTY MEDICAL CENTER | SAN BERNARDINO COUNTY MEDICAL CENTER | CA | SOUTH COAST AQMD, CA | 2000-02-15 | 2000 | BOILER USED TO PRODUCE STEAM TO HEAT BUILDING. | BOILER, LPG | 13.31 | LPG | 6 | MMBTU/H | CLEAVER BROOKS MODEL FLX-700-600. LPG USED AS EMERGENCY FUEL | Carbon Monoxide | N |  | 400 | PPMVD | Corrected to 3% O2 |  |  |  | 0.3 | LB/MMBTU | Calculated using F-Factor
PA-0165 | PROCTER & GAMBLE PAPER PRODUCTS COMPANY | PROCTER & GAMBLE PAPER PRODUCTS COMPANY | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2000-02-24 | 2000 | THIS LATEST MODIFICATION UPDATES CHANGES TO PLANT WHICH INCLUDES GENERATION OF ERCS FROM THE SHUT DOWN OF SOURCES AS APPROVED BY RACT PERMIT. | BOILERS, (3) | 13.31 | NATURAL GAS | 90 | MMBTU/H | INSTALLATION OF LOW NOX BURNERS TO 3 BOILERS | Carbon Monoxide | P | LOW NOX BURNERS | 0.173 | LB/MMBTU |  |  |  |  | 0.173 | LB/MMBTU
CA-0944 | BUMBLE BEE SEAFOODS, INC. | BUMBLE BEE SEAFOODS, INC. | CA | SOUTH COAST AQMD, CA | 2000-03-10 | 2000 | BOILER PRODUCES STEAM FOR FACILITY | BOILER | 13.31 | NATURAL GAS | 16.3 | MMBTU/H | SUPERIOR MOHAWK MODEL 4X-2007-S150 FIRE TUBE BOILER | Carbon Monoxide | N |  | 100 | PPMVD | Corrected to 3% O2 |  |  |  | 0.074 | LB/MMBTU | Calculated using F-Factor | CO 15 MIN @ 3% O2
CA-0940 | NATION WIDE BOILER | NATION WIDE BOILER | CA | SOUTH COAST AQMD, CA | 2000-03-15 | 2000 | EMERGENCY RENTAL BOILER TO PRODUCE HOT WATER AND STEAM | BOILER, PORTABLE | 13.31 | NATURAL GAS | 28.8 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 50 | PPMVD | Corrected to 3% O2 |  |  |  | 0.037 | LB/MMBTU | Calculated using F-Factor | CO 15 MIN @ 3% O2
CA-0947 | RRR REAL ESTATE | RRR REAL ESTATE | CA | SOUTH COAST AQMD, CA | 2000-03-15 | 2000 | BOILER USED TO PRODUCE HOT WATER AND HEAT | BOILER | 13.31 | NATURAL GAS | 7.5 | MMBTU/H | CLEAVER BROOKS CB-200 | Carbon Monoxide | N |  | 100 | PPMVD | Corrected to 3% O2 |  |  |  | 0.074 | LB/MMBTU | Calculated using F-Factor | CO 15 MIN @ 3% O2
CA-1005 | COLLEGE OF THE DESERT | COLLEGE OF THE DESERT | CA | SOUTH COAST AQMD, CA | 2000-03-16 | 2000 |  | BOILER, 5.05 MMBTU/H | 13.31 | NATURAL GAS | 5.05 | MMBTU/H | EQUIP MFR: TRANE, TYPE: DIRECT FIRED, MODEL: ABDA 0440, FUNC EQUIP: PROVIDE COOLING, SCHEDULE: CONTINUOUS | Carbon Monoxide | N |  | 50 | PPMV @ 3% O2 | 15 MIN AVG |  |  |  | 0.06 | LB/MMBTU | CALCULATED
CA-0945 | LIBERTY CONTAINER CO | LIBERTY CONTAINER CO, KEY CONTAINER | CA | SOUTH COAST AQMD, CA | 2000-03-17 | 2000 | MANUFACTURER OF CONTAINERS | BOILER | 13.31 | NATURAL GAS | 16.3 | MMBTU/H | CLEAVER BROOKS CB (LE) 700-400 | Carbon Monoxide | N |  | 50 | PPM @ 3% O2 | 15 MINUTE AVERAGE | 322 | LB/MO |  | 0.037 | LB/MMBTU | CALCULATED USING F-FACTOR | CO 15 MIN @ 3% O2
AK-0053 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFI | CRUDE HEATER, CF-H-31003A | 13.31 | FUEL GAS | 65.6 | MMBTU/H | PERMIT INFORMATION LISTS FUEL TYPE AS FUEL GAS" BUT TECHNICAL DOCUMENTS INDICATE THAT FUEL IS NATURAL GAS. SCC AND PROCESS CODES WERE CHOSEN FOR NATURAL GAS." | Carbon Monoxide | P | GOOD OPERATIONAL PRACTICES. | 0.07 | LB/MMBTU |  |  |  |  | 0.07 | LB/MMBTU
AK-0053 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFI | CRUDE HEATER, CF-H-31003B | 13.31 | FUEL GAS | 65.6 | MMBTU/H | PERMIT INFORMATION INDICATES FUEL TYPE IS FUEL GAS" BUT TECHNICAL INFORMATION INDICATES FUEL GAS IS NATURAL GAS. SCC AND PROCESS CODES WERE CHOSEN FOR NATURAL GAS. UNIT IS DESCRIBED AS BORN." | Carbon Monoxide | P | GOOD OPERATIONAL PRACTICES | 0.07 | LB/MMBTU |  |  |  |  | 0.07 | LB/MMBTU
TX-0274 | SOLAR GAS TURBINE COGEN. | AMERIPOL SYNPOL CORP. | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-04-03 | 2000 | AMERIPOL PROPOSES TO CONSTRUCT A COGENERATION FACILITY, TURBINE WITH DUCT BURNER FIRED HEAT RECOVERY STEAM GENERATOR (HRSG) AND AN AUXILLIARY BOILER. THE TURBINE IS A 4.4 MW (DESIGN CAPACITY AT ISO CONDITIONS, BASE LOAD) NATURAL GAS FIRED SOLAR TURBINE, M | AUXILIARY BOILER | 13.31 | NATURAL GAS | 54.01 | MMBTU/H | WILL BE OPERATED 175 H/YR ONLY DURING PERIODS OF CTG DOWNTIME. | Carbon Monoxide | N | NONE INDICATED | 4.45 | LB/H |  | 0.39 | T/YR |  | 0.08 | LB/MMBTU | CONVERTED USING THROUGHPUT | ADDITIONAL CO LIMIT OF 100 PPMVD WHEN CORRECTED TO 3 % O2 (ONE-HOUR AVERAGE).
CA-0943 | L & N UNIFORM SUPPLY CO INC. | L & N UNIFORM SUPPLY CO INC. | CA | SOUTH COAST AQMD, CA | 2000-04-06 | 2000 | BOILER USED TO GENERATE STEAM FOR LAUNDRY | BOILER | 13.31 | NATURAL GAS | 6.3 | MMBTU/H | SUPERIOR BOILER MODEL 5-ACT-625-150M. | Carbon Monoxide | N |  | 100 | PPMVD | Corrected to 3% O2 |  |  |  | 0.074 | LB/MMBTU | Calculated using F-Factor | CO 15 MIN @ 3% O2
MA-0027 | CABOT POWER CORPORATION | CABOT POWER CORPORATION | MA | MASSACHUSETTS DIV OF AIR QUAL CONTROL | 2000-05-07 | 2000 | COMBINED CYCLE ELECTRIC GENERATING FACILITY. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 26.6 | MMBTU/H | PROCESS RESTRICTED TO 500 HOURS PER YEAR (12,881,000 SCF NATURAL GAS) | Carbon Monoxide | A | OXIDATION CATALYST | 4 | LB/H |  |  |  |  | 0.15 | LB/MMBTU
LA-0146 | SHELL CHEMICAL COMPANY - GEISMAR PLANT | SHELL CHEMICAL COMPANY - GEISMAR PLANT | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2000-05-10 | 2000 | SHELL CHEMICAL PROPOSES TO INSTALL AN IDENTICAL SHOP 3 UNIT AND AN OLEFINS FEED PROCESSING UNIT (OFP). THE OFP UNIT WILL UTILIZE INTERNAL OLEFINS (C15/16) FROM SHOP 1, 2, AND 3. THIS UNIT WILL ALSO CONVERT THE INTERNAL OLEFINS INTO HIGH SOLUBILITY OLEFINS | C15/C16 COLUMN REBOILER FURNACE | 13.31 | NATURAL GAS | 20.75 | MMBTU/H (LHV) | EMISSION POINT 120-99 | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES AND ENGINEERING DESIGN, CLEAN BURNING FUEL | 1.66 | LB/H |  | 5.82 | T/YR |  | 0.08 | LB/MMBTU
CA-0946 | LACORR PACKAGING | LACORR PACKAGING | CA | SOUTH COAST AQMD, CA | 2000-07-12 | 2000 | PROVIDE STEAM FOR CARDBOARD MANUFACTURING | BOILER | 13.31 | NATURAL GAS | 21 | MMBTU/H | CLEAVER BROOKS MODEL CB-LE 500 BOILER | Carbon Monoxide | N |  | 50 | PPMVD | Corrected to 3% O2 |  |  |  | 0.037 | LB/MMBTU | Calculated using F-Factor | CO 15 MIN @ 3% O2
CA-1100 | LACORR PACKAGING | LACORR PACKAGING | CA | SOUTH COAST AQMD, CA | 2000-07-12 | 2000 |  | BOILER: 5 TO < 33.5 MMBTU/HR | 13.31 | NATURAL GAS | 21 | MMBTU/H | EQUIP: , MFR: CLEAVER BROOKS, TYPE: FIRE-TUBE, MODEL: CB-LE 500, FUNC EQUIP: PROVIDE STEAM FOR CARDBOARD MANUFACTURING, FUEL_TYPE: , SCHEDULE: CONTINUOUS, H/D: 24, D/W: 5, W/Y: 52, NOTES: BACT NH3: 5 PPMD CORRECTED TO 3% O2, 15 CONSECUTIVE MINUTES SOURCE | Carbon Monoxide | A | SCR | 50 | PPMVD@3% O2 | 15 MIN | [5 empty] | NOT AVAILABLE
WY-0056 | LA LAND & EXPLORATION CO. - LOST CABIN GAS PLANT | LOUISIANA LAND & EXPLORATION CO. - LOST CABIN GAS | WY | WYOMING AIR QUAL DIV, DEPT OF ENV QUAL | 2000-07-25 | 2000 | NATURAL GAS TREATMENT - SOUR GAS SWEETENING (H2S REMOVAL) | BOILER (AUXILLARY), TRAIN III | 13.31 | NATURAL GAS | 76.7 | MMBTU/H | ONLY USED FOR START UP / SHUT DOWN, IDLES OTHERWISE, EMISSIONS BASED ON AN-42 EMISSION FACTORS (EXCEPT FOR NOX), ASSUMING 15% LOAD 7884 H/YR AND 100% LOAD 876 H/YR. LIMITS FOR NOX AND CO ONLY. | Carbon Monoxide | N |  | 13.4 | T/YR |  | 13 | LB/H |  | 0.17 | LB/MMBTU
WI-0181 | CHARTER STEEL | CHARTER STEEL | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2000-08-02 | 2000 | STEEL MILL | BOILER | 13.31 | NATURAL GAS | 10 | MMBTU/H | THIS BOILER IS SUBJECT TO NSPS | Carbon Monoxide | P | BACT FOR CO IS DETERMINED TO BE GOOD COMBUSTION CONTROL AND THE USE OF NATURAL GAS TO FUEL THE BOILER. NO EMISSION RATE LIMIT.
WI-0181 | CHARTER STEEL | CHARTER STEEL | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2000-08-02 | 2000 | STEEL MILL | SPACE HEATERS | 13.31 |  | 5 | MMBTU/H | SPACE HEATERS' THROUGHPUT IS NO MORE THAN 5 MMBTU/H EACH. | Carbon Monoxide | P | BACT FOR CO IS DETERMINED TO BE GOOD COMBUSTION CONTROL AND THE USE OF NATURAL GAS TO FUEL THE SPACE HEATERS AND SIMILAR COMBUSTION APPLIANCES. NO EMISSION RATE LIMIT.
CA-1061 | NELCO PRODUCTS. INC, | NELCO PRODUCTS. INC, | CA | SOUTH COAST AQMD, CA | 2000-08-04 | 2000 |  | HEATER: REFINERY PROCESS, FORCED DRAFT < 50 MMBTU/HR | 13.31 | NATURAL GAS | 19 | MMBTU/H | EQUIP: , MFR: AMERICAN HYDROTHERM, TYPE: FORCED CIRCULATION, MODEL: 1200-4D-90, FUNC EQUIP: HEATS RECIRCULATING OIL USED IN LAMINATING PRESSES, FUEL_TYPE: , SCHEDULE: VARIABLE, H/D: 24, D/W: 7, W/Y: 52, NOTES: THE APPLICANT PROPOSED TO USE THE ALZETA ULNB | Carbon Monoxide | N |  | 50 | PPMVD 3% O2
TX-0363 | SAINT-GOBAIN VETROTEX AMERICA | VETROTEX AMERICA | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-11-13 | 2000 | VETROTEX AMERICA (VETROTEX) OPERATES A FIBER GLASS MANUFACTURING PLANT. THE VETROTEX PLANT PRODUCES FIBERGLASS REINFORCEMENT PRODUCTS AND IS COMPRISED OF FIVE GLASS MANUFACTURING FURNACES AND ASSOCIATED EQUIPMENT. THESE REFINFORCEMENT PRODUCTS ARE USED IN | BOILER NO 3 | 13.31 | NAT GAS |  |  |  | Carbon Monoxide | N | NONE INDICATED | 0.57 | LB/H |  | 2.5 | T/YR |  |  |  | NOT AVAILABLE
SC-0065 | BROAD RIVER INVESTORS - GAFFNEY | BROAD RIVER INVESTORS, LLC | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 2000-12-21 | 2000 | ELECTRIC GENERATION FACILITY | HOT WATER HEATERS, NAT. GAS (2) | 13.31 | NATURAL GAS | 11 | MMBTU/H (EACH) |  | Carbon Monoxide | P | GOOD COMBUSTION CONTROL | 1.04 | LB/H | EACH
AR-0040 | DUKE ENERGY HOT SPRINGS | DUKE ENERGY HOT SPRINGS | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2000-12-29 | 2000 | NATURAL GAS FIRED POWER PLANT | BOILERS, AUXILIARY 2 | 13.31 | NATURAL GAS | 44.1 | MMBTU/H | THROUGHPUT FOR EACH | Carbon Monoxide | P | PROPER COMBUSTION PROCEDURES. LB/HR LIMIT FOR EACH BOILER. | 0.15 | LB/MMBTU |  | 6.7 | LB/H |  | 0.15 | LB/MMBTU
NM-0042 | DEMING ENERGY FACILITY | DUKE ENERGY LUNA | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2000-12-29 | 2000 | THIS FACILITY WILL GENERATE APPROXIMATELY 640 MW (NOMINAL). IT WILL BE A COMBINED CYCLE FACILITY CONSISTING OF 2 GENERAL ELECTRIC PG7241 (FA) COMBUSTION TURBINES, 2 DUCT BURNERS, AN AUXILIARY BOILER, AND A COOLING TOWER. THE NOX FROM THE COMBUSTION TURBIN | AUX-1 AUXILARY BOILER | 13.31 | NATURAL GAS | 44.1 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION CONTROL, NATURAL GAS COMBUSTION | 6.6 | LB/H |  |  |  |  | 0.022 | LB/MMBTU | CALCULATED
AR-0044 | ARKANSAS STEEL ASSOCIATES | ARKANSAS STEEL ASSOCIATES | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-01-05 | 2001 | STEEL MILL. | PREHEATERS, LADLE, (3) | 13.31 | NATURAL GAS | 4 | MMBTU/H |  | Carbon Monoxide | P | NATURAL GAS COMBUSTION/GOOD COMBUSTION PRACTICES. | 0.3 | LB/H | combined | 1.2 | T/YR | combined | 0.075
AL-0168 | GENPOWER KELLEY LLC | GENPOWER KELLEY LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-01-12 | 2001 | ELECTRIC GENERATION | BOILER | 13.31 | NATURAL GAS | 83 | MMBTU/H | BOILER OPERATION LIMITED TO 1000 HR/YR | Carbon Monoxide | P | EFFICIENT COMBUSTION | 0.085 | LB/MMBTU |  | 7.02 | LB/H |  | 0.085 | LB/MMBTU
IN-0090 | NUCOR STEEL | NUCOR STEEL | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-01-19 | 2001 |  | LADLE PREHEATERS | 13.31 | NATURAL GAS | 15 | MMBTU/HR EACH | TUNDISH PREHEATERS 6 MMBTU/H EACH, TUNDISH NOZZLE PREHEATERS 1 MMBTU/H EACH, TUNDISH DRYERS 9 MMBTU/H, TRANSITION PIECE PREHEATERS 15 MMBTU/H | Carbon Monoxide | P | PERMIT LIMITATION IS NATURAL GAS OR PROPANE USAGE
IN-0090 | NUCOR STEEL | NUCOR STEEL | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-01-19 | 2001 |  | TUNDISH PREHEATERS (2) | 13.31 |  | 6 | MMBTU/H | THROUGHPUT FOR EACH | Carbon Monoxide | P | PERMIT LIMITATION IS USE OF NATURAL GAS.
AL-0169 | BLOUNT MEGAWATT FACILITY | BLOUNT COUNTY ENERGY LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-02-05 | 2001 | ELECTRIC GENERATING FACILITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 40 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.08 | LB/MMBTU |  | 3.2 | LB/H |  | 0.08 | LB/MMBTU
OH-0258 | PRO TEC COATING COMPANY | USS GALVANIZING, INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-02-15 | 2001 | STEEL FINISHING MILL: METAL COATING WITH 2 NON-INSIGNIFICANT ANNEALING FURNACES AND 4 BOILERS | BOILERS (4) | 13.31 | NATURAL GAS | 20.9 | MMBTU/H | This permit is a modification to only 2 of the 4 boilers at this facility. Permit limits the same for each of the boilers being modified. | Carbon Monoxide | N |  | 0.23 | LB/H | each | 1.01 | T/YR | each | 0.011 | LB/MMBTU |  | Limit is for each unit. Only 2 of the 4 boilers modified in this permit.
OH-0255 | PSEG WATERFORD ENERGY LLC | PSEG WATERFORD ENERGY LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-03-29 | 2001 | THREE 170 MW NATURAL GAS-FIRED COMBUSTION TURBINES; STAGE I SIMPLE CYCLE TO STAGE II COMBINED CYCLE | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 85.2 | MMBTU/H |  | Carbon Monoxide | N |  | 6.3 | LB/H |  | 27.6 | T/YR |  | 0.074 | LB/MMBTU
OK-0074 | KIAMICHI ENERGY FACILITY | KIOWA POWER PARTNERS LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-05-01 | 2001 | ENERGY PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 27.5 | MMBTU/H |  | Carbon Monoxide | P | GOOD OPERATING PRACTICES AND DESIGN | 0.084 | LB/MMBTU |  |  |  |  | 0.084 | LB/MMBTU
IN-0086 | MIRANT SUGAR CREEK, LLC | MIRANT SUGAR CREEK, LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-05-09 | 2001 |  | AUXILARY BOILER, NATURAL GAS (2) | 13.31 | NATURAL GAS | 35 | MMBTU/H | AUXILARY BOILERS ARE LIMITED TO 5,000 H/YR OF OPERATION. THROUGH PUT IS FOR EACH BOILER. | Carbon Monoxide | P | GOOD COMBUSTION. LB/H LIMIT IS FOR EACH BOILER. | 0.824 | LB/MMBTU |  | 2.88 | LB/H |  | 0.824 | LB/MMBTU
NV-0039 | CHUCK LENZIE GENERATING STATION | NEVADA POWER COMPANY | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2001-06-01 | 2001 | A NEW ELECTRIC POWER PLANT CONSISTING OF FOUR COMBUSTION TURBINE GENERATORS, FOUR HEAT RECOVERY STEAM GENERATORS EACH WITH DUCT FIRING, AND TWO STEAM TURBINE GENERATORS FOR A TOTAL NOMINAL OUTPUT OF 1170 MW. THE FACILITY IS LOCATED AT 11405 U.S. HIGHWAY 9 | AUXILIARY BOILERS | 13.31 | NATURAL GAS | 44.1 | MMBTU/H | THESE (TWO) BOILERS WILL EACH BE OPERATED A MAXIMUM OF 6,000 HOURS PER YEAR ACCORDING TO THE APPLICATION FOR ATC. | Carbon Monoxide | P | GOOD COMBUSTION CONTROL | 100 | PPMVD@3% O2 | 1-HOUR AVERAGE | 1.6 | LB/H |  | 0.036 | LB/MMBTU |  | EMISSION LIMITS 1 & 2 TAKE EFFECT ON JANUARY 1, 2006, PER SECTION 49 OF THE AIR QUALITY REGULATIONS. EMISSION LIMIT 2 APPLIES TO EACH AUXILIARY BOILER.
IN-0087 | DUKE ENERGY, VIGO LLC | DUKE ENERGY, VIGO LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-06-06 | 2001 |  | AUXILARY BOILER, NATURAL GAS (2) | 13.31 | NATURAL GAS | 46 | MMBTU/H | NATURAL GAS FIRED BOILERS (THROUGHPUT FOR EACH) LIMITED TO 500 H/YR OPERATION | Carbon Monoxide | P | GOOD COMBUSTION. LIMIT IS FOR EACH BOILER. | 0.082 | LB/MMBTU |  | 3.8 | LB/H |  | 0.082 | LB/MMBTU
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-5302A AND H-5302B | 13.31 | NATURAL GAS | 35 | MMBTU/H EA | 35 MMBTU/H MAXIMUM RATE/CAPACITY EA, 30 MMBTU/H NOMINAL CAPACITY EA. | Carbon Monoxide | P | LIMIT EXTENDED FROM PREVIOUS PERMIT TO AVOID PSD REVIEW. FOLLOW PREVENTATIVE MAINTENANCE PROCEDURES. | 0.2 | LB/MMBTU | FIRING NAT GAS |  |  |  | 0.2 | LB/MMBTU | FIRING NAT GAS
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-4510A AND H-4510B | 13.31 | NAT GAS | 14.4 | MMBTU/H EACH |  | Carbon Monoxide | P | LIMIT EXTENDED FROM PREVIOUS PERMIT TO AVOID PSD REVIEW. FOLLOW PREVENTATIVE MAINTENANCE PROCEDURES. | 0.02 | LB/MMBTU | FIRING NAT GAS |  |  |  | 0.02 | LB/MMBTU | FIRING NAT GAS
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-5701A AND H-5701B | 13.31 | NAT GAS | 29 | MMBTU/H EACH | 29 MMBTU/H MAXIMUM RATE/CAPACITY EA, 22.7 MMBTU/H NOMINAL CAPACITY EA. HEATERS BURN BOTH NATURAL GAS AND DIESEL FUELS. OPERATING RESTRICTION OF NO MORE THAN 200 H DURING ANY 12 CONSECUTIVE MOS, COMBINED, WHILE FIRING FUEL OIL. OPERATING RESTRICTION OF COM | Carbon Monoxide | P | FOLLOW PREVENTATIVE MAINTENANCE PROCEDURES | 5 | LB/1000 GAL | EA, FIRING DIESEL |  |  |  | 0.2 | LB/MMBTU | FIRING NATURAL GAS
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-2001A AND H-2001B | 13.31 | NAT GAS | 17.5 | MMBTU/H EACH | 17.5 MMBTU/H MAXIMUM RATE/CAPACITY EA, 13.1 MMBTU/H NOMINAL CAPACITY EA. | Carbon Monoxide | P | BACT LIMIT EXTENDED FROM PREVIOUS PERMIT TO AVOID PSD REVIEW. FOLLOW PREVENTATIVE MAINTENANCE PROCEDURES. | 0.2 | LB/MMBTU | FIRING NAT GAS |  |  |  | 0.2 | LB/MMBTU | FIRING NAT GAS
AL-0190 | GE PLASTICS | GE PLASTICS | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-07-13 | 2001 | SYNTHETIC ORGANIC CHEMICAL MANUFACTURER THAT PRODUCES POLYCARBONATE RESIN PELLETS | FURNACE, HOT OIL, 10 MMBTU/H | 13.31 | NATURAL GAS | 10 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.8 | LB/H |  | 0.08 | LB/MMBTU |  | 0.08 | LB/MMBTU
AL-0190 | GE PLASTICS | GE PLASTICS | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-07-13 | 2001 | SYNTHETIC ORGANIC CHEMICAL MANUFACTURER THAT PRODUCES POLYCARBONATE RESIN PELLETS | FURNACE, HOT OIL, 20 MMBTU/H | 13.31 | NATURAL GAS | 20 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.6 | LB/H |  | 0.03 | LB/MMBTU |  | 0.03 | LB/MMBTU
OH-0263 | FREMONT ENERGY CENTER, LLC | CALPINE CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-08-09 | 2001 | TWO 180 MW COMBINED CYCLE TURBINES (2 HRSGS),USING SELECTIVE CATALYTIC REDUCTION (SCR) AND OXIDATION CATALYST | AUXILIARY BOILER | 13.31 | NATURAL GAS | 80 | MMBTU/H | Auxiliary boiler, natural gas-fired, 80 mmBtu/hr | Carbon Monoxide | N |  | 7.84 | LB/H |  | 34.3 | T/YR |  | 0.098 | LB/MMBTU | Calculated
OK-0044 | SMITH POCOLA ENERGY PROJECT | SMITH COGENERATION OK INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-16 | 2001 | ELEC. POWER GENERATION | AUXILIARY BOILERS, (2) | 13.31 | NATURAL GAS | 48 | MMBTU/H | THROUGHPUT FOR EACH | Carbon Monoxide | P | COMBUSTION CONTROL | 7.91 | LB/H | combined | 34.64 | T/YR | combined | 0.084 | LB/MMBTU
OK-0054 | QUAD GRAPHICS OKC FACILITY | QUAD GRAPHICS INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-21 | 2001 | PRINT SHOP | BOILERS | 13.31 | NATURAL GAS | 62.77 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION/MAINTENANCE | 10.81 | T/YR |  | 4.39 | LB/H |  | 0.069938 | LB/MMBTU | Not Available | Standard Emissions for CO not available
OK-0054 | QUAD GRAPHICS OKC FACILITY | QUAD GRAPHICS INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-21 | 2001 | PRINT SHOP | HEATERS/OXIDIZERS | 13.31 | NATURAL GAS | 16 | MMBTU/H | THESE UNITS INCLUDE HEATERS FOR INK DRYING AND OXIDIZERS ASSOCIATED WITH CONTROLLING EMISSIONS. EMISSION LIMITS ARE FOR PRODUCTS OF COMBUSTION. | Carbon Monoxide | P | FUEL LIMITS AND MAINTENANCE PER MANUFACTURERS SPECS | 1.32 | LB/H/UNIT |  | 4.33 | T/YR |  | 0.27063 | LB/MMBTU | Not Available
CA-1099 | COSMETIC LABORATORIES | COSMETIC LABORATORIES | CA | SOUTH COAST AQMD, CA | 2001-09-04 | 2001 |  | BOILER: 5 TO < 33.5 MMBTU/HR | 13.31 | NATURAL GAS | 21.46 | MMBTU/H | EQUIP: , MFR: CLAYTON INDUSTRIES, TYPE: WATER-TUBE, MODEL: EG504-1-FMB, FUNC EQUIP: PROCESS STEAM FOR MANUFACTURING PROCESSES, FUEL_TYPE: , SCHEDULE: CONTINUOUS, H/D: 24, D/W: 5, W/Y: 52, NOTES: AQMD UNANNOUNCED EMISSIONS TEST 6/28/2002 USING PORTABLE ANA | Carbon Monoxide | A | ULTRA LOW-NOX BURNER | 100 | PPMD @ 3% O2 | 15-MIN | [5 empty] | NOT AVAILABLE
CA-0903 | DISNEYLAND RESORT | DISNEYLAND RESORT | CA | SOUTH COAST AQMD, CA | 2001-09-27 | 2001 |  | BOILER, CLEAVER BROOKS WATER-TUBE | 13.31 | NATURAL GAS | 8.5 | MMBTU/H | ARB RECORD # A310-946-00; AUTHORITY TO CONSTRUCT # 360389 (12/21/99) CLEAVER BROOKS MODEL FLX WATER-TUBE BOILER USED TO SUPPLY HOT WATER. BACT DETERMINATION FOR NOX AND CO ONLY, THIS PROCESS DOES NOT HAVE EMISSION LIMITS SET FOR SOX, VOC, OR PM. | Carbon Monoxide | P | ALZETA ULTRA LOW-NOX BURNER, GOOD COMBUSTION | 50 | PPMVD @ 3% O2 |  |  |  |  | 0.0375 | LB/MMBTU
MD-0033 | KELSON RIDGE | FREE STATE ELECTRIC, LLC | MD | MARYLAND, OTHER | 2001-09-27 | 2001 | FACILITY WAS LICENSED; PROJECT WAS THEN CANCELLED BY APPLICANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 40 | MMBTU/H | EMISSIONS LIMITS APPLY TO EACH BOILER | Carbon Monoxide | B | EXCLUSIVE USE OF NATURAL GAS, ADVANCED DRY LOW-NOX BURNERS; GOOD COMBUSTION CONTROLS HEAT INPUT TO THE AUXILIARY BOILERS (2) SHALL BE LIMITED TO 210,240 MMBTU FOR ANY CONSECUTIVE 12-MONTH PERIOD |  |  | SEE NOTE | [6 empty] | HEAT INPUT TO THE AUXILIARY BOILERS (2) SHALL BE LIMITED TO 210,240 MMBTU FOR ANY CONSECUTIVE 12-MONTH PERIOD
AL-0179 | TENASKA TALLADEGA GENERATING STATION | TENASKA ALABAMA IV PARTNERS, LP | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-10-03 | 2001 | NATURAL GAS/DISTILLATE OIL FIRED COMBINED CYCLE ELECTRIC GENERATING FACILITY. | 30 MMBTU/HR AUXILIARY BOILER | 13.31 | NATURAL GAS | 30 | MMBTU/H | Operation limited to 1000 h/yr. | Carbon Monoxide | P | EFFICIENT COMBUSTION | 0.073 | LB/MMBTU |  | 2.2 | LB/H |  | 0.073 | LB/MMBTU
IN-0110 | COGENTRIX LAWRENCE CO., LLC | COGENTRIX LAWRENCE CO., LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-10-05 | 2001 | POWER PLANT | BOILER, AUXILIARY, NATURAL GAS | 13.31 | NATURAL GAS | 35 | MMBTU/H |  | Carbon Monoxide | P | CLEAN FUEL, GOOD COMBUSTION PRACTICE | 0.082 | LB/MMBTU |  | 2.87 | LB/H |  | 0.082 | LB/MMBTU
OH-0265 | DRESDEN ENERGY LLC | Dresden Energy | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-10-16 | 2001 | TWO 171.7 MW NATURAL GAS AND FUEL OIL- FIRED COMBUSTION TURBINES, COMBINED CYCLE; 49 MMBTU/HR NATURAL GAS FIRED BOILER; 2,250,000 GALLON FIXED ROOF STORAGE TANK FOR #2 FUEL OIL. | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 49 | MMBTU/H | Boiler is restricted to 800 hour of operation per a rolling 12 months. | Carbon Monoxide | N |  | 4.12 | LB/H |  | 1.65 | T/YR |  | 0.084 | LB/MMBTU |  | Boiler is restricted to 800 hours or operation per a rolling 12 months.
OK-0043 | WEBERS FALLS ENERGY FACILITY | ENERGETIX | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-10-22 | 2001 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 30 | MMBTU/H | BOILER OPERATIONS LIMITED TO 3,000 HOURS/YEAR. | Carbon Monoxide | P | BOILER DESIGN & GOOD OPERATING PRACTICES | 0.085 | LB/MMBTU |  |  |  |  | 0.085 | LB/MMBTU
AL-0181 | DUKE ENERGY AUTAUGA, LLC | DUKE ENERGY AUTAUGA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-10-23 | 2001 | COMBINED CYCLE ELECTRIC GENERATING PLANT. | 31.4 MMBTU/HR NATURAL GAS FIRED BOILER | 13.31 | NATURAL GAS | 31.4 | MMBTU/H | Operation limited to 2500 hrs/yr. | Carbon Monoxide | P | EFFICIENT COMBUSTION. | 0.135 | LB/MMBTU |  | 4.71 | LB/H
*WA-0292 | SATSOP COMBUSTION TURBINE PROJECT | GRAYS HARBOR ENERGY LLC | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2001-10-23 | 2001 | GE F7 TURBINE BASED COMBINED CYCLE NATURAL GAS ONLY FUELED COMBUSTION TURBINE INCLUDES COOLING TOWER AND EMERGENCY ICE GENERATOR AND FIRE WATER ENGINES | AUXILIARY BOILER | 13.31 | NAT GAS | 29.3 | MMBTU/H | 29.3 MMBTU/H IS THE DESIGN HEAT INPUT RATE FOR THE BOILER, AS PROVIDED BY THE STATE CONTACT PERSON. | Carbon Monoxide | N |  | 50 | PPM @ 3% O2 | 1-H AV | 1.07 | LB/H |  | 0.037 | LB/MMBTU | CALCULATED
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | 2001 | ELECTRICITY GENERATION | FUEL GAS HEATER | 13.31 | NATURAL GAS | 16 | MMBTU/H | FUEL GAS HEATER PRE-HEATS THE PIPELINE NATURAL GAS FUEL ENTERING THE COMBUSTION TURBINE UNITS AT 70 DEGREES F | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 0.86 | LB/H |  | 3.181 | T/YR |  | 0.0538 | LB/MMBTU
OK-0071 | MCCLAIN ENERGY FACILITY | NRG MCCLAIN LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-10-25 | 2001 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Carbon Monoxide | P | USE OF NATURAL GAS FUEL | 0.37 | LB/MMBTU |  |  |  |  | 0.37 | LB/MMBTU
PR-0007 | COGENERATION PLANT (AES-PRCP) | AES PUERTO RICO | PR | PUERTO RICO ENV QUALITY BOARD, AIR PROGRAM | 2001-10-29 | 2001 | COGENERATION UNIT | LIMESTONE DRYER | 13.31 | PROPANE | 13 | MMBTU/H | LIMESTONE DRYER INCLUDES A CRUSHER. HEATED AIR BOTH CLASSIFIES THE GROUND LIMESTONE AND DRIES THE MATERIAL. UNIT IS LIMITED TO A 505 CAPACITY FACTOR CALCULATED BASED ON 4380 H/CALENDAR YR. COMBUSTION CONTROLS WILL BE USED TO MINIMIZE AIR EMISSIONS. | Carbon Monoxide | P | GOOD COMBUSTION CONTROLS | 0.26 | LB/H |  |  |  |  | 0.02 | LB/MMBTU
CA-1109 | SUPERIOR INDUSTRIES INTERNATIONAL | SUPERIOR INDUSTRIES INTERNATIONAL | CA | SOUTH COAST AQMD, CA | 2001-10-30 | 2001 |  | METAL HEATING FURNACE | 13.31 | NATURAL GAS | 12.6 | MMBTU/H | EQUIP: NO AIR PREHEAT, MFR: THERMAL PROCESS, TYPE: REVERBERATORY, FUNC EQUIP: ALUMINUM MELTING, FUEL_TYPE: PROPANE, SCHEDULE: CONTINUOUS, H/D: 24, D/W: 7, W/Y: 50 NOTES: THIS IS A RECLAIM FACILITY. THE FACILITY REQUESTED PERMIT MODIFICATIONS FOR FOUR ALUM | Carbon Monoxide | N |  | 2000 | PPMVD @ 3% 02 | [6 empty] | NOT AVAILABLE
TX-0378 | LA PORTE POLYPROPYLENE PLANT | ATOFINA PETROCHEMICALS INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-11-05 | 2001 | ATOFINA PROPOSES TO INSTALL A 60 MMBTU/H PACKAGE BOILER TO PROVIDE NEEDED STEAM CAPACITY. THE BURNER WILL MEET ESAD LIMIT OF 0.015 LB NOX/MMBTU FOR HOUSTON/GALVESTON. UPON STARTUP OF EPN ES-206, THE 40 MMBTU/H TEMPORARY BOILER (EPN TEMPBOILER) SHALL BE RE | PACKAGE BOILER BO-4 | 13.31 | NAT GAS | 60 | MMBTU/H |  | Carbon Monoxide | N | NONE INDICATED | 4.84 | LB/H |  | 21.19 | T/YR |  | 0.08 | LB/MMBTU | CALCULATED USING THROUGHPUT | ADDITIONAL EMISSION LIMIT OF 100 PPM @ 15% O2.
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | 2001 | SOYBEAN EXTRACTION PLANT | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. There is a separate process entry for this boiler when firing fuel oil. | Carbon Monoxide | N |  | 12.2 | LB/H |  | 53.4 | LB/H |  | 0.13 | LB/MMBTU | calculated | USING MANUFACTURER'S EMISSION FACTORS OF 150 LBS CO/1,000,000 POUNDS OF AIR for both NG and #2 fuel oil.
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | 2001 | SOYBEAN EXTRACTION PLANT | DRYER, SOY PROTEIN CONCENTRATE - COMBUSTION | 13.31 | NATURAL GAS | 37 | MMBTU/H | Baghouse with 100% capture. Process is in 2 parts - dryer - combustion, and dryer - pm. | Carbon Monoxide | N |  | 1.24 | LB/H |  | 5.43 | T/YR |  | 0.035 | LB/MMBTU |  | Emissions from natural gas combustion, using 0.035 lb CO/mmBtu
IN-0095 | ALLEGHENY ENERGY SUPPLY CO. LLC | ALLEGHENY ENERGY SUPPLY CO. LLC (ACADIA BAY ENERGY | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-12-07 | 2001 | ELECTRIC POWER GENERATING STATION | AUXILLIARY BOILER | 13.31 | NATURAL GAS | 21 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.082 | LB/MMBTU |  |  |  |  | 0.082 | LB/MMBTU
AL-0180 | DUKE ENERGY DALE, LLC | DUKE ENERGY DALE, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-12-11 | 2001 | NATURAL GAS FIRED COMBINED CYCLE ELECTRIC GENERATING PLANT. | 35 MMBTU/HR NAT. GAS FIRED AUXILIARY BOILER | 13.31 | NATURAL GAS | 35 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION | 0.135 | LB/MMBTU |  | 4.71 | LB/H |  | 0.135 | LB/MMBTU
AR-0049 | GEORGIA PACIFIC - CROSSETT PAPER | GEORGIA PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-12-14 | 2001 | KRAFT PAPER MILL. | BURNER EXHAUST A, TAD (SN-85A) | 13.31 | NATURAL GAS | 90 | MMBTU/H | Source has not been installed yet. BACT for PM, VOC, CO and NOx. Initial & 3 yr periodic testing required for CO & NOx. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE IN CONJUNCTION W/NATURAL GAS FUEL. | 0.18 | LB/MMBTU |  |  |  |  | 0.18 | LB/MMBTU |  | Limit for combined Burner A and Burner B: 25.2 lb/h
AR-0049 | GEORGIA PACIFIC - CROSSETT PAPER | GEORGIA PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-12-14 | 2001 | KRAFT PAPER MILL. | BURNER EXHAUST B, TAD | 13.31 | NATURAL GAS | 50 | MMBTU/H | Source not yet installed. BACT for PM, CO, NOx, VOC. Initial & 3 -yr periodic testing is required for NOx & CO. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE IN CONJUNCTION WITH CLEAN FUEL. | 0.18 | LB/MMBTU |  |  |  |  | 0.18 | LB/MMBTU
AR-0049 | GEORGIA PACIFIC - CROSSETT PAPER | GEORGIA PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-12-14 | 2001 | KRAFT PAPER MILL. | BURNER, YANKEE | 13.31 | NATURAL GAS | 21 | MMBTU/H | Source is not installed yet. Initial & 3 year periodic testing required for CO & NOx using methods 10 & 7E respectively. BACT for PM, VOC, CO and NOx. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE. | 0.18 | LB/MMBTU |  | 3.8 | LB/H |  | 0.18 | LB/MMBTU
*PA-0210 | DART CONTAINER CORP OF PA | DART CONTAINER CORP OF PA | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2001-12-14 | 2001 | NEW BOILERS ARE SUBJECT TO 40 CFR, PART 60, SUBPART DC AND BAT AND 25 PA CODE , CHAPTER 123. | BOILER, (2) | 13.31 | NATURAL GAS | 33.5 | MMBTU/H | CLEAVER BROOKS BOILERS. Boilers subject to NSPS/BAT/SIP | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 400 | PPMDV @ 3% O2 |  |  |  |  | 0.3 | LB/MMBTU
OH-0257 | JACKSON COUNTY POWER, LLC | JACKSON COUNTY POWER, LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-12-27 | 2001 | FOUR 305 MW NATURAL-GAS FIRED COMBUSTION TURBINES, COMBINED CYCLE, WITH DLN AND SCR | AUXILIARY BOILER | 13.31 | NATURAL GAS | 76 | MMBTU/H | Limited to 3000 hours of operation per rolling 12 month period. | Carbon Monoxide | N |  | 6.86 | LB/H |  | 10.28 | T/YR |  | 0.082 | LB/MMBTU
NC-0094 | GENPOWER EARLEYS, LLC | GENPOWER EARLEYS, LLC | NC | NORTH CAROLINA DIV OF ENV MGMT | 2002-01-09 | 2002 | POWER GENERATING FACILITY | BOILER, AUXILIARY, NATURAL GAS | 13.31 | NATURAL GAS | 83 | MMBTU/H | Auxiliary boiler supplies steam for start up, and maintain operating temperatures for HSRGs and steam turbine when the CTs are off line. Boiler is allowed to operate < 1000 h/yr. | Carbon Monoxide | P | GOOD C OMBUSTION PRACTICES AND DESIGN | 6.84 | LB/H |  |  |  |  | 0.082 | LB/MMBTU | calculated
LA-0174 | PORT HUDSON OPERATIONS | GEORGIA-PACIFIC CORPORATION | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-01-25 | 2002 | PULP MILL | POWER BOILER NO. 2 | 13.31 | NAT GAS | 65.5 | MMBTU/H | EMISSION POINT NO. 6. | Carbon Monoxide | P | GOOD EQUIPMENT DESIGN AND PROPER COMBUSTION TECHNIQUES | 36.8 | LB/H |  | 24.28 | T/YR |  | 0.56 | LB/MMBTU
OK-0055 | MUSTANG ENERGY PROJECT | MUSTANG POWER LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-02-12 | 2002 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 31 | MMBTU/H |  | Carbon Monoxide | P | COMBUSTION CONTROL | 0.084 | LB/MMBTU |  |  |  |  | 0.084 | LB/MMBTU
OK-0056 | HORSESHOE ENERGY PROJECT | MUSTANG POWER LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-02-12 | 2002 | POWER PLANT | AUXILIARY BOILERS | 13.31 | NATURAL GAS | 0 |  |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES & DESIGN | 0.084 | LB/MMBTU |  |  |  |  | 0.084 | LB/MMBTU
TX-0388 | SAND HILL ENERGY CENTER | AUSTIN ELECTRIC UTILITY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-02-12 | 2002 | ELECTRIC POWER GENERATOR CONSISTING OF NATURAL GAS-FIRED COMBUSTION TURBINE WITH HRSG. | INLET AIR HEATERS (3) | 13.31 |  |  |  |  | Carbon Monoxide | N |  | 0.44 | LB/H |  | 0.22 | T/YR
LA-0120 | GEISMAR PLANT | SHELL CHEMICAL LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-02-26 | 2002 | RE-EVALUATION OF BACT FOR OLEFIN AND ALCOHOL PROJECT. THIS PROJECT WAS APPROVED EARLIER UNDER PSD PERMIT NO. PSD-LA-647 (M-1) DATED JUNE 26, 2001. THE CURRENT PERMIT IS FOR THE MODIFICATION OF REGENERATIVE FURNACE, EMISSION POINT 620-99, TO INCLUDE PREMIX | REGENERATOR FURNACE #620-99 | 13.31 | NATURAL GAS | 3.3 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.26 | LB/H |  | 0.77 | T/YR |  | 0.08 | LB/MMBTU
LA-0120 | GEISMAR PLANT | SHELL CHEMICAL LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-02-26 | 2002 | RE-EVALUATION OF BACT FOR OLEFIN AND ALCOHOL PROJECT. THIS PROJECT WAS APPROVED EARLIER UNDER PSD PERMIT NO. PSD-LA-647 (M-1) DATED JUNE 26, 2001. THE CURRENT PERMIT IS FOR THE MODIFICATION OF REGENERATIVE FURNACE, EMISSION POINT 620-99, TO INCLUDE PREMIX | SYLTHERM FURNACE, #321-99 | 13.31 | NATURAL GAS | 53 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES AND ENGINEERING DESIGN | 4.25 | LB/H |  | 14.89 | T/YR |  | 0.08 | LB/MMBTU
LA-0120 | GEISMAR PLANT | SHELL CHEMICAL LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-02-26 | 2002 | RE-EVALUATION OF BACT FOR OLEFIN AND ALCOHOL PROJECT. THIS PROJECT WAS APPROVED EARLIER UNDER PSD PERMIT NO. PSD-LA-647 (M-1) DATED JUNE 26, 2001. THE CURRENT PERMIT IS FOR THE MODIFICATION OF REGENERATIVE FURNACE, EMISSION POINT 620-99, TO INCLUDE PREMIX | HOT OIL FURNACE, #621-99 | 13.31 | NATURAL GAS | 20 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 1.62 | LB/H |  | 5.68 | T/YR |  | 0.08 | LB/MMBTU
AR-0051 | DUKE ENERGY-JACKSON FACILITY | DUKE ENERGY | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-04-01 | 2002 | 620 MW NATURAL GAS TURBINE ELECTRIC UTILITY PLANT. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Carbon Monoxide | P | GOOD OPERATING PRACTICE | 0.15 | LB/MMBTU |  |  |  |  | 0.15 | LB/MMBTU
TN-0153 | WILLIAMS REFINING & MARKETING, L.L.C. | WILLIAMS REFINING & MARKETING, L.L.C. | TN | MEMPHIS AND SHELBY CO HEALTH DEPT, TN | 2002-04-03 | 2002 | PETROLEUM REFINERY | BOILER, NO. 9 | 13.31 | NATURAL GAS | 95 | MMBTU/H |  | Carbon Monoxide | N |  | 0.09 | LB/MMBTU |  |  |  |  | 0.09 | LB/MMBTU
TN-0153 | WILLIAMS REFINING & MARKETING, L.L.C. | WILLIAMS REFINING & MARKETING, L.L.C. | TN | MEMPHIS AND SHELBY CO HEALTH DEPT, TN | 2002-04-03 | 2002 | PETROLEUM REFINERY | CCR STABILIZATION REBOILER | 13.31 | NATURAL GAS | 54 | MMBTU/H |  | Carbon Monoxide | N |  | 0.1 | LB/MMBTU |  |  |  |  | 0.1 | LB/MMBTU
IA-0058 | GREATER DES MOINES ENERGY CENTER | MIDAMERICAN ENERGY | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-04-10 | 2002 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 68 | MMBTU/H |  | Carbon Monoxide | N |  | 0.084 | LB/MMBTU |  | 25.1 | T/YR |  | 0.084 | LB/MMBTU
OK-0072 | REDBUD POWER PLT | REDBUD ENERGY LP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-05-06 | 2002 | ELECTRICAL GENERATOR | AUXILIARY BOILER | 13.31 | NATURAL GAS | 93 | MMBUT/H |  | Carbon Monoxide | P | BOILER DESIGN AND GOOD OPERATING PRACTICES | 0.07 | LB/MMBTU |  |  |  |  | 0.07 | LB/MMBTU
OH-0264 | NORTON ENERGY STORAGE, LLC | NORTON ENERGY | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-05-23 | 2002 | NINE 300 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE WITH DLN AND SCR; TEN 11.45 MMBTU/H NATURAL GAS-FIRED FUEL SUPPLY HEATERS/BOILERS; SEVEN 12.84 MMBTU/H NATURAL GAS-FIRED RECUPERATOR PRE HEATERS/BOILERS | RECUPERATOR PRE-HEATERS (9) | 13.31 | NATURAL GAS | 12.84 | MMBTU/H | Each boiler is limited to 100 hour of operation per rolling 12 months. | Carbon Monoxide | N |  | 0.514 | LB/H |  | 0.03 | T/YR |  | 0.04 | LB/MMBTU |  | Limits are for each boiler. Each boiler is retricted to 100 hours of operation.
OH-0264 | NORTON ENERGY STORAGE, LLC | NORTON ENERGY | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-05-23 | 2002 | NINE 300 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE WITH DLN AND SCR; TEN 11.45 MMBTU/H NATURAL GAS-FIRED FUEL SUPPLY HEATERS/BOILERS; SEVEN 12.84 MMBTU/H NATURAL GAS-FIRED RECUPERATOR PRE HEATERS/BOILERS | FUEL SUPPLY HEATERS (9) | 13.31 | NATURAL GAS | 11.45 | MMBTU/H | Each fuel supply heater is limited to a maximum annual cumulative fuel heat input of 47,630 mmBtu per rolling 12 months. | Carbon Monoxide | N |  | 0.96 | LB/H |  | 2 | T/YR |  | 0.084 | LB/MMBTU |  | Limits are for each heater.
OK-0070 | GENOVA OK I POWER PROJECT | GENOVA OKLAHOMA LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-06-13 | 2002 | COMBINED CYCLE POWER PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Carbon Monoxide | P | BOILER DESIGN AND GOOD OPERATING PRACTICES | 0.037 | LB/MMBTU |  |  |  |  | 0.037 | LB/MMBTU
NM-0044 | CLOVIS ENERGY FACILITY | DUKE ENERGY CURRY LLC | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2002-06-27 | 2002 | THIS IS A 1,200 MW COMBINED CYCLE MERCHANT POWER PLANT. | AUXILIARY BOILERS (AUX-1 AND AUX-2) | 13.31 | NATURAL GAS | 33 | MMBTU/H | Emission limits are for each (Aux-1 and Aux-2) Auxiliary Boiler. | Carbon Monoxide | P | DRY LOW NOX (DLN) TECHNOLOGY, GOOD COMBUSTION PRACTICES | 4.9 | LB/H |  |  |  |  | 0.07 | LB/MMBTU | (LHV)
AL-0185 | BARTON SHOALS ENERGY | BARTON SHOALS ENERGY, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2002-07-12 | 2002 | ELECTRIC GENERATION - NATURAL GAS FIRED COMBINED CYCLE | TWO (2) 40 MMBTU/H AUXILIARY BOILERS | 13.31 | NATURAL GAS | 40 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.082 | LB/MMBTU |  | 3.3 | LB/H |  | 0.082 | LB/MMBTU
IA-0060 | HAWKEYE GENERATING, LLC | ENTERGY | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-07-23 | 2002 | ENTERGY IS INSTALLING TWO GE 7FA (170MW) NATURAL GAS FIRED TURBINES. THEY ARE REQUIRED TO INSTALL SCR FOR CONTROL OF NOX (3 PPMVD, 3 HOUR AVG. TIME) AND CATALYTIC OXIDATION FOR THE CONTROL OF CO (5 PPMVD, 3 HOUR AVG. TIME) FOR COMBINED CYCLE OPERATION. SI | AUXILIARY BOILER (48.5 MMBTU/H) | 13.31 | NATUAL GAS | 48.69 | MILLION CF/YR |  | Carbon Monoxide | B | GCP | 0.073 | LB/MMBTU |  |  |  |  | 0.073 | LB/MMBTU
AR-0070 | GENOVA ARKANSAS I, LLC | GENOVA ARKANSAS I, LLC | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-08-23 | 2002 | COMBINED CYCLE POWER PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 0.04 | LB/MMBTU |  |  |  |  | 0.04 | LB/MMBTU
VA-0261 | CPV CUNNINGHAM CREEK | COMPETITIVE POWER VENTURE | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-09-06 | 2002 | TURBINES USED TO PRODUCE ELECTRICITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 80 | MMBTU/H | one auxiliary boiler | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES. | 6.42 | LB/H |  | 9.63 | T/YR |  | 0.08 | LB/MMBTU
OH-0248 | LAWRENCE ENERGY | CALPINE CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-09-24 | 2002 | THREE 180 MW GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE, WITH DLN, SCR AND OXIDATION CATALYST | BOILER | 13.31 | NATURAL GAS | 99 | MMBTU/H |  | Carbon Monoxide | N |  | 8.32 | LB/H |  | 0.084 | LB/MMBTU |  | 0.084 | LB/MMBTU |  | Limits are for each boiler.
CA-1023 | LA COUNTY INTERNAL SERVICES DEPT. | LA COUNTY INTERNAL SERVICES DEPT. | CA | SOUTH COAST AQMD, CA | 2002-10-08 | 2002 |  | BOILER, 39 MMBTU/H | 13.31 | NATURAL GAS | 39 | MMBTU/H | MFR: SPRINGFIELD, TYPE: WATER TUBE, MODEL: STIRLING, FUNC EQUIP: BACKS UP COGEN SYSTEM DURING SCHEDULED MAINTENANCE, SCHEDULE: VARIABLE, H/D: 8, D/W: 1, W/Y: 12, NOTES: 90,000 THERMS PER MONTH HEAT INPUT SOURCE TEST RESULTS: TEST DATES MARCH 23-30, 2004 F | Carbon Monoxide | N |  | 100 | PPMVD @ 3% 02 | [6 empty] | NOT AVAILABLE
AL-0192 | HONDA MANUFACTURING OF ALABAMA, LLC | HONDA MANUFACTURING OF ALABAMA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2002-10-18 | 2002 | AUTOMOBILE MANUFACTURING PLANT | BOILERS, NATURAL GAS, (3) | 13.31 | NATURAL GAS | 30 | MMBTU/H | throughput for each boiler. BACT for CO, NOx, PM10, and VE | Carbon Monoxide | P | CLEAN FUEL, GOOD COMBUSTION PRACTICES. | 2.52 | LB/H |  | 0.084 | LB/MMBTU |  | 0.084 | LB/MMBTU
WI-0195 | SENA NIAGARA MILL | STORA ENSO NORTH AMERICA | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2002-10-18 | 2002 |  | PROCESS HEATER, PAPER MACHINE P51 | 13.31 | NATURAL GAS | 34.4 | MMBTU/H | Throughput is total for natural gas IR and flotation dryers. | Carbon Monoxide | P | ANY NEW (REPLACEMENT) IR BURNERS WILL BE LOW NOX BURNERS, FIRING NATURAL GAS | 0.06 | LB/MMBTU |  |  |  |  | 0.06 | LB/MMBTU
NJ-0062 | CONSOLIDATE EDISON DEVELOPMENT (CED) | CONSOLIDATED EDISON DVPMT.- LAKEWOOD GEN. FACILITY | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2002-10-22 | 2002 | POWER GENERATION | FUEL GAS HEATERS (3 UNITS) | 13.31 | NATURAL GAS | 4.62 | MMBTU/H | INSTALLATION OF 3 NEW FUEL GAS HEATERS@ 4.62 MMBTU/HR EACH. FUEL: NATURAL GAS. | Carbon Monoxide | N | GOOD COMBUSTION PRACTICE | 0.69 | LB/H |  | 0.15 | LB/MMBTU |  | 0.15 | LB/MMBTU
GA-0101 | MURRAY ENERGY FACILITY | DUKE ENERGY MURRAY LLC | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2002-10-23 | 2002 | ELECTRIC GENERATING FACILITY | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 31.4 | MMBTU/H | HOURS OF OPERATION NOT TO EXCEED 6,000 H/YR. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 0.037 | LB/MMBTU |  |  |  |  | 0.037 | LB/MMBTU
VA-0255 | VA POWER - POSSUM POINT | Virginia Power | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-11-18 | 2002 | THIE PERMIT WAS AMENDED AND APPROVED ON 11/18/2002 FROM THE PERMIT THAT WAS DATED 10/05/2001. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 99 | MMBTU/H | 2 Auxiliary boilers. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES. | 14.9 | LB/H | EACH UNIT | 74 | T/YR | UNITS COMBINED | 0.15 | LB/MMBTU | EACH UNIT
VA-0260 | HENRY COUNTY POWER | Cogentrix Energy Inc | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-11-21 | 2002 | 4 COMBINED CYCLE TURBINES WITH A TOTAL ELECTRICITY PRODUCTION OF 1,100 MW. | AUXILIARY BOILER, (2) | 13.31 | NATURAL GAS | 40 | MMBTU/H | Two Auxiliary Boilers. BACT for NOx and CO only. | Carbon Monoxide | P | GOOD COMBUSTION AND DESIGN. CLEAN FUEL. | 2.9 | LB/H | each unit | 4.38 | T/YR | each unit | 0.073 | LB/MMBTU | each unit
TX-0408 | INDIAN ROCK GATHERING COMPANY LP | INDIAN ROCK GATHERING COMPANY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-11-22 | 2002 | NATURAL GAS PROCESSING FACILITY | AUXILIARY BOILER, (2) | 13.31 | NATURAL GAS | 6 | MMBTU/H | BOILERS ARE UNCONTROLLED BECAUSE BOILER DUTY IS <40 MMBTU/H. | Carbon Monoxide | N |  | 0.5 | LB/H | EACH | 2.16 | T/YR | EACH | 0.083 | LB/MMBTU |  | UNCONTROLLED BECAUSE BOILER IS LESS THAN 40 MMBTU/H.
VA-0243 | STANLEY FURNITURE |  | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-12-01 | 2002 | WOOD HOUSEHOLD FURNITURE MFG. | BOILER, NAT GAS & OIL | 13.31 | NATURAL GAS | 26.5 | MMBTU/H | KEWANEE NATURAL GAS/DISTILLATE OIL BOILER. THROUGHPUT 26.5 MMBTU/HR - 450,000 GAL #2 OIL. ADDITIONAL SCC, 10200502. FOR ALL POLLUTANTS, NO CONTROLS, EMISSION LIMITS IN T/YR ONLY | Carbon Monoxide | N | EMISSION LIMITS IN T/YR ONLY | 9.4 | T/YR | [6 empty] | NOT AVAILABLE
TX-0392 | LUCITE BEAUMONT | INEOS ACRYLICS, INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-09 | 2002 | SULFURIC ACID REGENERATION FACILITY | NO.1 PRE-HEATER | 13.31 | NATURAL GAS |  |  |  | Carbon Monoxide | N |  | 1.6 | LB/H |  | 6.1 | T/YR
TX-0392 | LUCITE BEAUMONT | INEOS ACRYLICS, INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-09 | 2002 | SULFURIC ACID REGENERATION FACILITY | NO. 2 PRE-HEATER | 13.31 | NATURAL GAS |  |  |  | Carbon Monoxide | N |  | 1.6 | LB/H |  | 6.1 | T/YR
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | HEAT TRANSFER FLUID HEATER, H202 | 13.31 | NATURAL GAS | 31 | MMBTU/H |  | Carbon Monoxide | N | NONE INDICATED | 2.59 | LB/H |  | 11.32 | T/YR |  | 0.08 | LB/MMBTU | CALCULATED USING THROUGHPUT
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | HEAT TRANSFER FLUID HEATER, H2202 | 13.31 | NATURAL GAS | 31 | MMBTU/H |  | Carbon Monoxide | N | NONE INDICATED | 2.59 | LB/H |  | 11.32 | T/YR |  | 0.08 | LB/MMBTU | CALCULATED USING THROUGHPUT
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | (2) STEAM BOILERS, X-426A AND X-426B | 13.31 | NATURAL GAS | 15.8 | MMBTU/H |  | Carbon Monoxide | N | NONE INDICATED | 1.33 | LB/H | EACH | 5.81 | T/YR | EACH | 0.08 | LB/MMBTU | EACH, CALCULATED USING THROUGHPUT
IA-0062 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT (IPL) | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-12-20 | 2002 | PERMITS WERE AMENDED ON 6/26/03. RBLC ID IA-0062 WAS CORRECTED AS MOST OF THE CHANGES WERE MINOR (BASED ON OPERATIONAL & DESIGN CHANGES BEING MADE AS PLANT IS CONSTRUCTED). THE NEW DEW POINT HEATER HAS BEEN GIVEN A NEW RBLC ID. | GAS HEATER, (2) | 13.31 | NATURAL GAS | 16.4 | MMBTU/H | Natural Gas fired Heaters, 16.4 MMBTU/HR capacity for each. Operating hours reduced from 8760 hours to 6000 hours each. | Carbon Monoxide | N |  | 0.082 | LB/MMBTU |  |  |  |  | 0.082 | LB/MMBTU
IA-0062 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT (IPL) | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-12-20 | 2002 | PERMITS WERE AMENDED ON 6/26/03. RBLC ID IA-0062 WAS CORRECTED AS MOST OF THE CHANGES WERE MINOR (BASED ON OPERATIONAL & DESIGN CHANGES BEING MADE AS PLANT IS CONSTRUCTED). THE NEW DEW POINT HEATER HAS BEEN GIVEN A NEW RBLC ID. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 68 | MMBTU/H | Limited to 6000 hours of operation per year. | Carbon Monoxide | A | CATALYTIC OXIDATION | 0.0164 | LB/MMBTU |  |  |  |  | 0.0164 | LB/MMBTU
TX-0389 | BAYTOWN CARBON BLACK PLANT | DEGUSSA ENGINEERED CARBONS, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-31 | 2002 |  | BACK-UP BOILER | 13.31 | NATURAL GAS | 13.4 | MMBUT/H |  | Carbon Monoxide | N |  | 1.11 | LB/H |  | 4.85 | T/YR
WA-0291 | WALLULA POWER PLANT | WALLULA GENERATION, LLC | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2003-01-03 | 2003 | WALLULA GENERATION, LLC, PROPOSES TO CONSTRUCT AND OPERATE A 1,300 MW COMBINED CYCLE ELECTRIC POWER PLANT. THE PROJECT WILL CONSIST OF TWO INDEPENDENT POWER BLOCKS WITH CRITICAL BACK-UP SYSTEMS TO MAINTAIN OVERALL PLANT RELIABILITY AND AVAILABILITY. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 55.3 | MMBTU/H | Operational limit of 4,000 hr per year | Carbon Monoxide | N |  | 111 | PPMDV @ 3% O2 | 3 hr ave | 4.6 | LB/H | 3 hr ave | 0.083 | LB/MMBTU
PA-0216 | J & L SPECIALTY STEEL, INC. | J & L SPECIALTY STEEL, INC. | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2003-01-13 | 2003 | THIS PA/REVIEW MEMO IS VERY LONG AND INVOLVED AND SHOULD BE CONSULTED FOR ANY CLARIFICATION ON ISSUES. | BOILER, DRAP LINE | 13.31 | NATURAL GAS | 33.5 | MMBTU/H | Installation of ultra-low Nox burner on the drap line | Carbon Monoxide | N |  | 2.75 | LB/H |  | 12.08 | T/H |  | 0.08 | LB/MMBTU
OH-0295 | GMC TRUCK AND BUS, MORAINE ASSEMBLY PLANT | GENERAL MOTORS CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-01-14 | 2003 | LIGHT DUTY TRUCKS AND AUTOMOBILE PRODUCTION, ASSEMBLY PLANT | NATURAL GAS USAGE | 13.31 | NATURAL GAS | 1700 | MMCF/rolling 12-mo | THE INCREASE IN NATURAL GAS USAGE CAUSED THIS PERMIT TO BE PSD FOR NOX. COMBINED NATURAL GAS USAGE FOR: ELPO SAND, GUIDE COAT, BODY SAND, BODY WIPE, TOPCOAT SYSTEM, TOPCOAT ABATEMENT, FINAL REPAIR, DEADNER, BUILDING HEAT. | Carbon Monoxide | N |  | 71.4 | T/YR | [6 empty] | NOT AVAILABLE
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HOT OIL HEATER, EPN6 | 13.31 | NAT GAS | 12 | MMBTU/H |  | Carbon Monoxide | N | NONE INDICATED | 1.19 | LB/H |  | 4.33 | T/YR |  | 0.0992 | LB/MMBTU |  | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | GLYCOL REBOILER, EPN11 | 13.31 | NAT GAS | 2.5 | MMBTU/H |  | Carbon Monoxide | N | NONE INDICATED | 0.25 | LB/H |  | 0.9 | T/YR |  | 0.1 | LB/MMBTU | SEE NOTE | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HOT OIL HEATER, EPN26 | 13.31 | NAT GAS | 32.5 | MMBTU/H |  | Carbon Monoxide | N | NONE INDICATED | 3.21 | LB/H |  | 11.73 | T/YR |  | 0.099 | LB/MMBTU | SEE NOTE | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HP TEG FIREBOX, EPN30 | 13.31 | NAT GAS | 3 | MMBTU/H |  | Carbon Monoxide | N | NONE INDICATED | 0.25 | LB/H |  | 1.08 | T/YR |  | 0.0833 | LB/MMBTU | SEE NOTE | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
LA-0193 | STYRENE MONOMER PLANT | COS-MAR COMPANY | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2003-02-11 | 2003 | PLANT PRODUCES STYRENE MONOMER THROUGH THE ALKYLATION OF BENZENE AND ETHYLENE TO ETHYLBENZENE, FOLLOWED BY DEHYDROGENATION OF ETHYLBENZENE TO STYRENE. PROJECT EXPANDS STYRENE MONOMER CAPACITY FROM 1.9 TO 2.55 BILLION POUNDS PER YEAR. | REGENERATION GAS HEATER HS-2102 | 13.31 |  | 14.4 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES - GOOD EQUIPMENT DESIGN, USE OF GASEOUS FUELS FOR GOOD MIXING, AND PROPER COMBUSTION TECHNIQUES | 1.2 | LB/H | HOURLY MAXIMUM |  |  |  | 0.08 | LB/MMBTU | ANNUAL AVERAGE | ANNUAL CO EMISSIONS FROM THE FOLLOWING SOURCES ARE CAPPED AT 953.3 TPY: 145-02-A, 145-02-B, 145-02-C, 145-02-D, 145-02-E, 145-02-F, 145-02-G, 145-02-H, 145-02-I, 145-02-J, 145-02-K, 145-02-L, 145-02-M, 145-02-N, 145-02-O, & 145-02-P.
LA-0193 | STYRENE MONOMER PLANT | COS-MAR COMPANY | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2003-02-11 | 2003 | PLANT PRODUCES STYRENE MONOMER THROUGH THE ALKYLATION OF BENZENE AND ETHYLENE TO ETHYLBENZENE, FOLLOWED BY DEHYDROGENATION OF ETHYLBENZENE TO STYRENE. PROJECT EXPANDS STYRENE MONOMER CAPACITY FROM 1.9 TO 2.55 BILLION POUNDS PER YEAR. | PEB RECOVERY COLUMN HEATER HS-2105 | 13.31 |  | 25.2 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES - GOOD EQUIPMENT DESIGN, USE OF GASEOUS FUELS FOR GOOD MIXING, AND PROPER COMBUSTION TECHNIQUES | 2.1 | LB/H | HOURLY MAXIMUM |  |  |  | 0.08 | LB/MMBTU | ANNUAL AVERAGE | ANNUAL CO EMISSIONS FROM THE FOLLOWING SOURCES ARE CAPPED AT 953.3 TPY: 145-02-A, 145-02-B, 145-02-C, 145-02-D, 145-02-E, 145-02-F, 145-02-G, 145-02-H, 145-02-I, 145-02-J, 145-02-K, 145-02-L, 145-02-M, 145-02-N, 145-02-O, & 145-02-P.
OR-0040 | KLAMATH GENERATION, LLC | KLAMATH GENERATION, LLC | OR | OREGON DEPT OF ENVIRONMENTAL QUALITY | 2003-03-12 | 2003 | POWER GENERATION FACILITY | BOILER, AUXILIARY, NATURAL GAS | 13.31 | NATURAL GAS | 50000 | LB/H | Throughput is lb/h of steam. Boiler provides steam for standby and startup conditions. | Carbon Monoxide | N |  | 0.035 | LB/MMBTU | 3-h avg |  |  |  | 0.035 | LB/MMBTU
OK-0090 | DUKE ENERGY STEPHENS, LLC STEPHENS ENERGY | DUKE ENERGY | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2003-03-21 | 2003 | MERCHANT POWER PLANT - NOMINAL TOTAL OF 620 MW. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Carbon Monoxide | P | BOILER DESIGN AND GOOD OPERATING PRACTICES | 0.085 | LB/MMBTU |  |  |  |  | 0.085 | LB/MMBTU
GA-0098 | RINCON POWER PLANT | GENPOWER RINCON LLC | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2003-03-24 | 2003 | ELECTRIC GENERATING FACILITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 83 | MMBTU/H | THE BOILER IS LIMITED TO 1,000 H/YR OF OPERATION. | Carbon Monoxide | N |  | 0.093 | LB/MMBTU |  |  |  |  | 0.093 | LB/MMBTU
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 | 2003 |  | BOILER NO. 1 | 13.31 | NATURAL GAS | 43.2 | MMBTU/H | One of two boilers | Carbon Monoxide | B | CONTINUOUS EMISSION MONITORING SYSTEM AND GOOD COMBUSTION PRACTICES. | 3.56 | LB/H | each unit |  |  |  | 0.08 | LB/MMBTU |  | one of two units
OH-0276 | CHARTER STEEL | CHARTER MANUFACTURING CO., INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-04-14 | 2003 | NEW MELT SHOP AT EXISTING FACILITY, INCLUDES NEW: ELECTRIC ARC FURNACE; LADLE METALLURGY FURNACE; VACUUM OXYGEN DEGASSER (VOD); VOC BOILER; CONTINUOUS CASTING MACHINES; 3 SILOS; 6 LADLE PREHEATERS; CUT-OFF-TORCH; 3 TUNDISH PREHEATERS; PROCESS SPACE HEATER | BOILER FOR VACUUM OXYGEN DEGASSER VESSEL | 13.31 | NATURAL GAS | 25 | MMBTU/H | VACUUM OXYGEN DEGASSER VESSEL BOILER, WITH LOW NOX BURNER | Carbon Monoxide | N |  | 2.06 | LB/H | FROM NATURAL GAS COMBUSTION | 9.02 | T/YR | FROM NATURAL GAS COMBUSTION |  |  | NOT AVAILABLE
GA-0105 | MCINTOSH COMBINED CYCLE FACILITY | SAVANNAH ELECTRIC AND POWER CO | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2003-04-17 | 2003 | ELECTRIC GENERATING FACILITY | FUEL GAS HEATER | 13.31 | NATURAL GAS | 5 | MMBTU/H |  | Carbon Monoxide | N |  | 37 | PPM @ 15% O2 |  |  |  |  | 0.083 | LB/MMBTU
LA-0184 | TITANIUM DIOXIDE FACILITY | LOUISIANA PIGMENT COMPANY, LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2003-05-13 | 2003 | TITANIUM DIOXIDE (TIO2) PRODUCTION FACILITY RETROACTIVE PSD REVIEW. FACILITY CONSTRUCTED UNDER PSD-LA-533, DATED AUGUST 11, 1989. STACK TEST RESULTS INDICATE THAT WHEN PLANT COMMENCED OPERATIONS, CO EMISSIONS EXCEEDED ITS SIGNIFICANCE LEVEL. | OXYGEN SUPERHEATERS W340-AX & W340-BX (5.61 MM BTU/H EA.) | 13.31 | NATURAL GAS | 5.61 | MMBTU/H |  | Carbon Monoxide | P | GOOD EQUIPMENT DESIGN AND PROPER COMBUSTION TECHNIQUES | 0.508 | LB/H | HOURLY MAXIMUM | 2.03 | T/YR | ANNUAL MAXIMUM | 0.091 | LB/MMBTU | ANNUAL AVERAGE
LA-0184 | TITANIUM DIOXIDE FACILITY | LOUISIANA PIGMENT COMPANY, LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2003-05-13 | 2003 | TITANIUM DIOXIDE (TIO2) PRODUCTION FACILITY RETROACTIVE PSD REVIEW. FACILITY CONSTRUCTED UNDER PSD-LA-533, DATED AUGUST 11, 1989. STACK TEST RESULTS INDICATE THAT WHEN PLANT COMMENCED OPERATIONS, CO EMISSIONS EXCEEDED ITS SIGNIFICANCE LEVEL. | TICL4 SUPERHEATERS W321-AX & W321-BX (10.2 MM BTU/H EA.) | 13.31 | NATURAL GAS | 10.2 | MMBTU/H |  | Carbon Monoxide | P | GOOD EQUIPMENT DESIGN AND PROPER COMBUSTION TECHNIQUES | 0.924 | LB/H | HOURLY MAXIMUM | 3.68 | T/YR | ANNUAL MAXIMUM | 0.091 | LB/MMBTU | ANNUAL AVERAGE
LA-0184 | TITANIUM DIOXIDE FACILITY | LOUISIANA PIGMENT COMPANY, LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2003-05-13 | 2003 | TITANIUM DIOXIDE (TIO2) PRODUCTION FACILITY RETROACTIVE PSD REVIEW. FACILITY CONSTRUCTED UNDER PSD-LA-533, DATED AUGUST 11, 1989. STACK TEST RESULTS INDICATE THAT WHEN PLANT COMMENCED OPERATIONS, CO EMISSIONS EXCEEDED ITS SIGNIFICANCE LEVEL. | SPRAY DRYER DUST COLLECTORS F603-A & F-603-B (BURNERS - 25.5 MM BTU/H EA.) | 13.31 | NATURAL GAS | 13.31 | MMBTU/H |  | Carbon Monoxide | P | GOOD EQUIPMENT DESIGN AND PROPER COMBUSTION TECHNIQUES | 2.31 | LB/H | HOURLY MAXIMUM | 9.198 | T/YR | ANNUAL MAXIMUM | 0.091 | LB/MMBTU | ANNUAL AVERAGE
LA-0184 | TITANIUM DIOXIDE FACILITY | LOUISIANA PIGMENT COMPANY, LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2003-05-13 | 2003 | TITANIUM DIOXIDE (TIO2) PRODUCTION FACILITY RETROACTIVE PSD REVIEW. FACILITY CONSTRUCTED UNDER PSD-LA-533, DATED AUGUST 11, 1989. STACK TEST RESULTS INDICATE THAT WHEN PLANT COMMENCED OPERATIONS, CO EMISSIONS EXCEEDED ITS SIGNIFICANCE LEVEL. | CALCINER OFF-GAS SCRUBBER F476 (BURNER - 12.24 MM BTU/H) | 13.31 | NATURAL GAS | 12.24 | MMBTU/H |  | Carbon Monoxide | P | GOOD EQUIPMENT DESIGN AND PROPER COMBUSTION TECHNIQUES | 1.109 | LB/H | HOURLY MAXIMUM | 4.415 | T/YR | ANNUAL MAXIMUM | 0.091 | LB/MMBTU | ANNUAL AVERAGE
AL-0202 | CORUS TUSCALOOSA | CORUS TUSCALOOSA | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2003-06-03 | 2003 | STEEL MILL | EQUALIZING FURNACE | 13.3 | NATURAL GAS | 1.8 | MMBTU/H |  | Carbon Monoxide | N | NATURAL GAS/GOOD COMBUSTION | 7.2 | LB/H |  | 40 | LB/MMCF |  | 4 | LB/MMBTU
GA-0107 | TALBOT ENERGY FACILITY | OGLETHORPE POWER CORPORATION | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2003-06-09 | 2003 | ELECTRIC GENERATING FACILITY | FUEL GAS PREHEATERS, (3) | 13.31 | NATURAL GAS | 5 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 0.022 | LB/MMBTU |  |  |  |  | 0.022 | LB/MMBTU
IA-0068 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT - EMERY GENERATING STATI | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2003-06-26 | 2003 | IPL CHANGED NAMES FROM THE POWER IOWA ENERGY CENTER (PIEC) TO THE EMERY GENERATING STATION. | GAS HEATER | 13.31 | NATURAL GAS | 9 | MMBTU/H | One natural gas dew point heater is added. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.082 | LB/MMBTU |  | 3.25 | T/YR |  | 0.082 | LB/MMBTU
TX-0458 | JACK COUNTY POWER PLANT | DUKE ENERGY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-07-22 | 2003 | DUKE ENERGY JACK, L.P. IS CONSTRUCTING A 620 MW COMBINED CYCLE POWER PLANT. TWO COMBUSTION TURBINES WILL EACH PROVIDE APPROXIMATELY 170 MW OF ELECTRICITY. A 550 MMBTU/HR DUCT BURNER ON EACH TURBINE EXHAUST STREAM WILL ADD SUPPLEMENTAL HEAT TO THE HEAT REC | AUXILIARY BOILER | 13.31 | NATURAL GAS | 36 | mmbtu/h |  | Carbon Monoxide | N |  | 1.4 | LB/H |  | 4.1 | T/YR |  | 0.038889 | LB/MMBTU
OH-0254 | DUKE ENERGY WASHINGTON COUNTY LLC | DUKE ENERGY NORTH AMERICA | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-08-14 | 2003 | TWO 170 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE | BOILER | 13.31 | NATURAL GAS | 30.6 | MMBTU/H | THE MAXIMUM ANNUAL FUEL HEAT INPUT SHALL NOT EXCEED 128,000 MMBTU/ROLLING 12-MONTHS | Carbon Monoxide | N |  | 3.34 | LB/H |  | 7 | T/ROLLING 12-MONTHS |  | 0.109 | LB/MMBTU
AZ-0049 | LA PAZ GENERATING FACILITY | ALLEGHENY ENERGY SUPPLY LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2003-09-04 | 2003 | NATURAL GAS FIRED, COMBINED CYCLE GENERATING STATION | AUXILIARY BOILER FOR GE TURBINE | 13.31 | NATURAL GAS | 41 | MMBTU/H | THIS BOILER IS TO BE USED IF THE GE TURBINE SETUP IS SELECTED. | Carbon Monoxide | N |  | 0.09 | LB/MMBTU |  |  |  |  | 0.09 | LB/MMBTU
AZ-0049 | LA PAZ GENERATING FACILITY | ALLEGHENY ENERGY SUPPLY LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2003-09-04 | 2003 | NATURAL GAS FIRED, COMBINED CYCLE GENERATING STATION | AUXILIARY BOILER FOR SIEMENS TURBINES | 13.31 | NATURAL GAS | 55.34 | MMBTU/H | THIS BOILER IS FOR USE WHEN THE SIEMENS TURBINE SYSTEM IS SELECTED. | Carbon Monoxide | N |  | 0.14 | LB/MMBTU |  |  |  |  | 0.14 | LB/MMBTU
IN-0108 | NUCOR STEEL | NUCOR STEEL | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2003-11-21 | 2003 | STEEL MINI MILL | BOILER, NATURAL GAS, (2) | 13.31 | NATURAL GAS | 34 | MMBTU/H | Throughput for each. Propane is backup fuel. These boilers supply steam to the entire cold mill area of the plant. Subject to NSPS Subpart Dc | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES, NATURAL GAS | 0.061 | LB/MMBTU |  |  |  |  | 0.061 | LB/MMBTU
MN-0054 | MANKATO ENERGY CENTER |  | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2003-12-04 | 2003 | COMBINED CYCLE GAS TURBINE ELECTRIC POWER PLANT. TWO IDENTICAL GE FRAME F7A GAS TURBINES EACH WITH HRSG W/DUCT BURNERS FEEDING STEAM TO COMMON STEAM TURBINES. PRIMARY FUEL IS NG, NO. 2 VERY LOW SULFUR DISTILLATE OIL FOR BACKUP. ALSO, AUX. BOILER, DIESEL E | BOILER, COMMERCIAL | 13.31 | NATURAL GAS | 70 | MMBTU/H | NATURAL GAS ONLY | Carbon Monoxide | P | GOOD COMBUSTION | 0.06 | LB/MMBTU |  |  |  |  | 0.06 | LB/MMBTU
OR-0039 | COB ENERGY FACILITY, LLC | Peoples Energy Resources | OR | OREGON DEPT OF ENVIRONMENTAL QUALITY | 2003-12-30 | 2003 | POWER GENERATION FACILITY | BOILERS, AUXILIARY, NATURAL GAS, (2) | 13.31 | NATURAL GAS | 80 | MMBTU/H | Throughput for each. Provide auxiliary steam for standby and startup conditions. | Carbon Monoxide | P | GOOD COMBUSTION | 0.037 | LB/MMBTU |  |  |  |  | 0.037 | LB/MMBTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S50/B50, 60 MMBTU/H | 13.31 | NATURAL GAS | 60 | MMBTU/H | NATURAL GAS / PROPANE | Carbon Monoxide | P | NATURAL GAS / PROPANE; GOOD COMBUSTION CONTROL | 0.08 | LB/MMBTU |  |  |  |  | 0.08 | LB/MMBTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S51/B51, 80 MMBTU/H | 13.31 | NATURAL GAS | 80 | MMBTU/H | NAT. GAS / PROPANE | Carbon Monoxide | P | NAT. GAS / PROPANE, GOOD COMBUSTION CONTROL | 0.08 | LB/MMBTU |  |  |  |  | 0.08 | LB/MMBTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S52/B52, 11 MMBTU/H | 13.31 | NATURAL GAS | 11 | MMBTU/H |  | Carbon Monoxide | P | NATURAL GAS / PROPANE ; GOOD COMBUSTION CONTROL | 0.08 | LB/MMBTU |  |  |  |  | 0.08 | LB/MMBTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S53 / B53, 34 MMBTU/H | 13.31 | NATURAL GAS | 34 | MMBTU/H |  | Carbon Monoxide | P | NATURAL GAS / PROPANE; GOOD COMBUSTION CONTROL | 0.08 | LB/MMBTU |  |  |  |  | 0.08 | LB/MMBTU
AL-0191 | HYUNDAI MOTOR MANUFACTURING OF ALABAMA, LLC | HYUNDAI MOTOR MANUFACTURING OF ALABAMA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2004-03-23 | 2004 | AUTOMOBILE MANUFACTURING PLANT | BOILERS, NATURAL GAS, (3) | 13.31 | NATURAL GAS | 50 | MMBTU/H | BACT for NOx, PM, and CO | Carbon Monoxide | P | CLEAN FUEL | 4.5 | LB/H |  | 0.09 | LB/MMBTU |  | 0.09 | LB/MMBTU
NV-0037 | COPPER MOUNTAIN POWER | SEMPRA ENERGY RESOURCES | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2004-05-14 | 2004 | A 600 MW COMBINED CYCLE ELECTRICAL GENERATION FACILITY CONSISTING OF TWO COMBUSTION TURBINE GENERATORS WITH HEAT RECOVERY STEAM GENERATORS, ONE STEAM TURBINE GENERATOR, AND ONE AUXILIARY BOILER. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 60 | MMBTU/H |  | Carbon Monoxide | P | EFFECTIVE COMBUSTION SYSTEM DESIGN, 10:1 TURNDOWN CAPABILITY, AND LNB TECHNOLOGY | 0.08 | LB/MMBTU |  | 4.8 | LB/H |  | 0.08 | LB/MMBTU
WV-0021 | OHIO RIVER PLANT | CABOT CORPORATION | WV | WEST VIRGINIA AIR POLLUTION CONTROL COMM | 2004-06-09 | 2004 | AN EXISTING 3-UNIT, 4-REACTOR CARBON BLACK PRODUCTION FACILITY. TRADITIONALLY, HAS FLARED OR COMBUSTED ALL TAIL GAS. | BOILER, NATURAL GAS, 39.00 MMBTU | 13.31 | NATURAL GAS | 365 | MMSCF/YR | Boiler has MDHI of 39.00 mmbtu and combusts natural gas only. | Carbon Monoxide | N |  | 3.5 | PPH |  | 15.34 | T/YR |  | 0.09 | LB/MMBTU
AR-0086 | NUCOR-YAMATO STEEL COMPANY, BLYTHEVILLE MILL | NUCOR-YAMATO STEEL COMPANY | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-06-11 | 2004 |  | VTD BOILER | 13.31 | NATURAL GAS | 50 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 4.2 | LB/H |  | 18.1 | T/YR |  | 0.0824 | LB/MMBTU
CO-0058 | CHEYENNE STATION | CHEYENNE PLAINS GAS PIPELINE COMPANY | CO | COLORADO DEPT OF HEALTH - AIR POLL CTRL | 2004-06-12 | 2004 | COMPRESSOR STATION | HEATERS | 13.31 | NATURAL GAS | 45 | MMBTU/H | TWO HOT OIL HEATERS RATED AT 45 MMBTU/HR AND ONE UTILITY HEATER RATED AT 16 MMBTU/HR. THE HEATERS ARE INCLUDED IN PERMIT 03WE0913. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 0.037 | LB/MMBTU | 1-HR AVERAGE |  |  |  | 0.037 | LB/MMBTU
WI-0223 | LOUISIANA-PACIFIC HAYWARD | LOUISIANA-PACIFIC CORPORATION | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-06-17 | 2004 | OSB MILL | THERMAL OIL HEATER, GTS ENERGY, S31, B31 | 13.31 | NATURAL GAS | 32 | MMBTU/H | STACK S31; BOILER B31 - GTS ENERGY THERMAL OIL HEATER RATED AT 32.0 MILLION BTU PER HOUR WHEN BURNING NATURAL GAS AND 30.0 MILLION BTU PER HOUR WHEN BURNING DISTILLATE FUEL OIL | Carbon Monoxide | P | USE OF NATURAL GAS / DISTILLATE OIL, W/ RESTRICTION ON OIL USAGE | 2.7 | LB/H |  |  |  |  | 0.084 | LB/MMBTU | CALCULATED, NOT PERMIT LIMIT
WI-0223 | LOUISIANA-PACIFIC HAYWARD | LOUISIANA-PACIFIC CORPORATION | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-06-17 | 2004 | OSB MILL | THERMAL OIL HEATER, GTS ENERGY, S32, B32 | 13.31 | NATURAL GAS | 32 | MMBTU/H | STACK S32; BOILER B32 - GTS ENERGY THERMAL OIL HEATER RATED AT 32.0 MILLION BTU PER HOUR WHEN BURNING NATURAL GAS AND 30.0 MILLION BTU PER HOUR WHEN BURNING DISTILLATE FUEL OIL. | Carbon Monoxide | P | USE OF NATURAL GAS / DISTILLATE OIL, W/ RESTRICTION ON OIL USAGE | 2.7 | LB/H |  |  |  |  | 0.084 | LB/MMBTU | CALCULATED, NOT PERMIT LIMIT
NE-0026 | NUCOR STEEL DIVISION | NUCOR STEEL CORP. | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2004-06-22 | 2004 |  | NNII REHEAT FURNACE | 13.31 | NATURAL GAS | 143 | MMBTU/H |  | Carbon Monoxide | N |  | 0.066 | LB/MMBTU |  |  |  |  | 0.066 | LB/MMBTU
NE-0026 | NUCOR STEEL DIVISION | NUCOR STEEL CORP. | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2004-06-22 | 2004 |  | NNII BILET POST-HEATER | 13.31 | NATURAL GAS | 6.8 | MMBTU/H |  | Carbon Monoxide | N |  | 0.0084 | LB/MMBTU |  |  |  |  | 0.0084 | LB/MMBTU
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | 2004 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, NATURAL GAS (1) | 13.31 | NATURAL GAS | 40 | MMBTU/H | AUXILIARY BOILER. | Carbon Monoxide | P | GOOD COMBUSTION. | 0.084 | LB/MMBTU | 3 HOUR AVERAGE |  |  |  | 0.084 | LB/MMBTU
AR-0077 | BLUEWATER PROJECT | STEELCORR, INC. | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-07-22 | 2004 | THE FACILITY IS A NEW SPECIALTY STEEL MILL PRODUCING VARIOUS HOT ROLLED, COLD ROLLED AND GALVANIZED PRODUCTS FOR VARIOUS END USE MARKETS. AFIN: 47-00541 | BOILERS | 13.31 | NATURAL GAS | 22 | MMBTU/H | ENTRY INCLUDES TWO BOILERS. THE 22 MMBTU/H PICKLE LINE BOILER, 51 MMBTU/H VACUUM DEGASSER BOILERS. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 0.84 | LB/MMBTU |  |  |  |  | 0.84 | LB/MMBTU
WI-0226 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE (WPS) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-08-27 | 2004 | ELECTRIC UTILITY | NATURAL GAS FIRED BOILER | 13.31 | NATURAL GAS | 46.2 | MMBTU/H | NOT PSD | Carbon Monoxide | P | BOILER DESIGN | 1.67 | LB/H |  |  |  |  | 0.036 | LB/MMBTU |  | NATURAL GAS FIRED 46.2 MMBTU/HR BOILER
WI-0227 | PORT WASHINGTON GENERATING STATION | WE ENERGIES (WEPCO) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-13 | 2004 | ELECTRIC GENERATION | NATURAL GAS FIRED AUXILLIARY BOILER | 13.31 | NATURAL GAS | 97.1 | MMBTU/H |  | Carbon Monoxide | P | NATURAL GAS FUEL, GOOD COMBUSTION PRACTICES | 7.77 | LB/H |  |  |  |  | 0.08 | LB/MMBTU | CALCULATED
WI-0227 | PORT WASHINGTON GENERATING STATION | WE ENERGIES (WEPCO) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-13 | 2004 | ELECTRIC GENERATION | GAS HEATER (P06, S06) | 13.31 | NATURAL GAS | 10 | MMBTU/H | GAS CONDITIONING HEATER | Carbon Monoxide | P | NATURAL GAS FUEL | 0.47 | LB/H |  |  |  |  | 0.047 | LB/MMBTU | CALCULATED
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | B63, S63; B64, S64 - NATURAL GAS STATION HEATER 1 AND 2 | 13.31 | NATURAL GAS | 0.75 | MMBTU/H | EMISSION LIMITS ARE THOSE FOR EACH UNIT. | Carbon Monoxide | P | NATURAL GAS | 0.06 | LB/H | [6 empty] | NOT AVAILABLE | (LIMIT IS FOR EACH UNIT)
NV-0042 | CAPITAL CABINET CORPORATION | CAPITAL CABINET CORPORATION | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2004-11-05 | 2004 | A WOOD CABINETS AND COUNTER TOPS MANUFACTURING PLANT | FUEL COMBUSTION | 13.31 | NATURAL GAS | 8.8 | MMBTU/H | THE PROCESS EQUIPMENT CONSISTS OF SIX (6) FUEL COMBUSTION UNITS, THREE ARE MAKE-UP AIR HEATERS, EACH RATED AT 2.592 MMBTU/HR, TWO ARE FURNACES, EACH RATED AT 0.15 MMBTU/HR, ONE IS WATER HEATER RATED AT 0.722 MMBTU/HR. | Carbon Monoxide | P | USE OF NATURAL GAS AS THE ONLY FUEL FOR ALL COMBUSTION UNITS | 0.41 | T/MO | PER CALENDAR MONTH | 3.2 | T/YR | PER ROLLING 12-MONTH PERIOD |  |  |  | THESE ARE FACILITY-WIDE EMISSION LIMITS. FOR COMBUSTION UNITS B03, B04, AND B08, EACH HAS AN ANNUAL EMISSION LIMIT OF 0.94 TONS PER YEAR.
AZ-0047 | WELLTON MOHAWK GENERATING STATION | DOME VALLEY ENERGY PARTNERS | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2004-12-01 | 2004 | COMBINED CYCLE GAS-FIRED ELECTRICITY GENERATING STATION | AUXILIARY BOILER | 13.31 | NATURAL GAS | 38 | MMBTU/H |  | Carbon Monoxide | N |  | 0.08 | LB/MMBTU | BASED ON HIGHER HEATING VALUE OF FUEL |  |  |  | 0.08 | LB/MMBTU
OH-0252 | DUKE ENERGY HANGING ROCK ENERGY FACILITY | DUKE ENERGY HANGING ROCK, LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2004-12-28 | 2004 | FOUR NATURAL GAS (NG) FIRED COMBUSTION TURBINES, WITH DUCT BURNERS; COMBINED CYCLE, EACH 172 MW | BOILERS (2) | 13.31 | NATURAL GAS | 30.6 | MMBTU/H | LIMITS ARE FOR EACH BOILER INDIVIDUALLY. THE MAXIMUM FUEL HEAT INPUT SHALL NOT EXCEED 91,500 MMBTU/ROLLING 12-MONTHS FOR EACH BOILER. | Carbon Monoxide | N |  | 1.13 | LB/H | EACH BOILER | 1.69 | T/ROLLING 12-MONTHS | EACH BOILER | 0.037 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER
WA-0301 | BP CHERRY POINT REFINERY | BRITISH PETROLEUM | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2005-04-20 | 2005 | BRITISH PETROLEUM (BP), FORMERLY KNOWN AS ARCO PRODUCTS COMPANY OPERATES A REFINERY AT CHERRY POINT NEAR BLAINE, WASHINGTON. THE REFINERY IS LOCATED IN A RURAL SETTING NEAR BLAINE AND BIRCH BAY WASHINGTON. THE SURROUNDING LAND USE IS ZONED HEAVY IMPACT IN | PROCESS HEATER, IHT | 13.31 | NATURAL GAS | 13 | MMBTU/H | Isom hydrotreater (IHT) process heater | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 70 | PPM | 7% O2, 24 hr ave | 1.1 | LB/H | 24 hr ave | 0.085 | LB/MMBTU | calculated
LA-0192 | CRESCENT CITY POWER | CRESENT CITY POWER, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-06-06 | 2005 | NEW 600 MW NATURAL GAS-FIRED COMBINED CYCLE POWER PLANT | FUEL GAS HEATERS (3) | 13.31 |  | 19 | MMBTU/H |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 1.52 | LB/H | HOURLY AVERAGE | 0.57 | T/YR | *SEE NOTES. ANNUAL MAXIMUM | 0.08 | LB/MMBTU | ANNUAL AVERAGE | *TPY LIMIT FOR ALL 3 HEATERS. AGGREGATE HEAT INPUT IS LIMITED TO 14,250 MM BTU/YR. ONLY 2 OF THE 3 HEATERS ARE ALLOWED TO OPERATE AT ANY GIVEN TIME.
LA-0203 | OAKDALE OSB PLANT | MARTCO LIMITED PARTNERSHIP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-06-13 | 2005 | PSD FOR A NEW ORIENTED STRAND BOARD (OSB) MANUFACTURING FACILITY CAPABLE OF PRODUCING 900,000 MSF 3/8 INCH OSB PER YEAR. | AUXILIARY THERMAL OIL HEATER | 13.31 | NATURAL GAS | 66.5 | MMBTU/H | OPERATING TIME = 500 HR/YR. | Carbon Monoxide | P | USE OF NATURAL GAS AS FUEL AND GOOD COMBUSTION PRACTICES | 6.57 | LB/H | HOURLY MAXIMUM |  |  |  | 0.099 | LB/MMBTU | CALCULATED BY CATC
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-07-27 | 2005 | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | CRACKING FURNACES A-D | 13.31 |  | 90 | MMBTU/H EA. |  | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES AND USE OF NATURAL GAS AS FUEL | 0.046 | LB/MMBTU |  |  |  |  | 0.046 | LB/MMBTU | THREE ONE-HOUR TEST AVERAGE
MD-0035 | DOMINION | DOMINION COVE POINT LNG, L.P. | MD | MARYLAND DEPARTMENT OF THE ENVIRONMENT | 2005-08-12 | 2005 | LNG FACILITY | VAPORIZATION HEATER | 13.31 | NATURAL GAS |  |  | SEVEN VAPORIZATION HEATERS; RATED HEAT INPUT IS 88.4 MMBTU/H FOR EACH UNIT; EMISSION LIMITS APPLY TO EACH UNIT | Carbon Monoxide | P | EACH VAPORIZATION HEATER SHALL ONLY USE NATURAL GAS FOR FUEL AND SHALL USE GOOD COMBUSTION OPERATING PRACTICES | 0.03 | LB/MMBTU |  |  |  |  | 0.03 | LB/MMBTU
AK-0062 | BADAMI DEVELOPMENT FACILITY | BP EXPLORATION ALASKA | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2005-08-19 | 2005 | OIL AND GAS PROCESSING FACILITY | NATCO PRODUCTION HEATER | 13.31 | NATURAL GAS | 34 | MMBTU/H |  | Carbon Monoxide | P | GOOD OPERATIONAL PRACTICES | 0.1 | LB/MMBTU |  |  |  |  | 0.1 | LB/MMBTU | *SEE NOTES | GOOD OPERATIONAL PRACTICES
AK-0062 | BADAMI DEVELOPMENT FACILITY | BP EXPLORATION ALASKA | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2005-08-19 | 2005 | OIL AND GAS PROCESSING FACILITY | NATCO MISCIBLE INJECTION HEATER | 13.31 | NATURAL GAS | 14.87 | MMBTU/H |  | Carbon Monoxide | P | GOOD OPERATIONAL PRACTICES | 0.12 | LB/MMBTU |  |  |  |  | 0.12 | LB/MMBTU | *SEE NOTES | GOOD OPERATIONAL PRACTICES
AK-0062 | BADAMI DEVELOPMENT FACILITY | BP EXPLORATION ALASKA | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2005-08-19 | 2005 | OIL AND GAS PROCESSING FACILITY | NATCO TEG REBOILER | 13.31 | NATURAL GAS | 1.34 | MMBTU/H |  | Carbon Monoxide | P | GOOD OPERATIONAL PRACTICES | 0.15 | LB/MMBTU |  |  |  |  | 0.15 | LB/MMBTU | SEE NOTES | GOOD OPERATIONAL PRACTICES
CA-1127 | GENENTECH, INC. | GENENTECH, INC. | CA | BAY AREA AQMD, CA | 2005-09-27 | 2005 |  | BOILER: >= 50 MMBTU/H | 13.31 | NATURAL GAS | 97 | MMBTU/H | EQUIP: WATERTUBE, MFR: NEBRASKA BOILER, INC., TYPE: STEAM BOILER, MODEL: NS-E-64-ST-CA-HM-AL, FUNC EQUIP: PROVIDE STEAM AND HOT WATER., FUEL_TYPE: MAY INSTALL DIESEL OIL BACKUP IN FUTURE., SCHEDULE: CONTINUOUS, H/D: 24, D/W: 7, W/Y: 52, NOTES: THREE IDENT | Carbon Monoxide | P | ULTRA LOW NOX BURNERS: NATCOM P-97-LOG-35-2127 | 50 | PPMVD @ 3% O2 | THREE 30-MIN SAMP PERIODS AV
MD-0036 | DOMINION | DOMINION COVE POINT LNG, L.P. | MD | MARYLAND DEPARTMENT OF THE ENVIRONMENT | 2006-03-10 | 2006 | LNG FACILITY | FUEL GAS PROCESS HEATER | 13.31 | NATURAL GAS |  |  | ENGINEERING TECH NO. IDHLE 1.0; 0.93 MMBTU/HR | Carbon Monoxide | P | GOOD COMBUSTION PRACTICES | 143 | PPMVD | [7 empty] | 143 PPMVD (CORRECTED TO 3% O2)
CA-1128 | COTTAGE HEALTH CARE - PUEBLO STREET | COTTAGE HEALTH CARE - PUEBLO STREET | CA | SANTA BARBARA COUNTY APCD, CA | 2006-05-16 | 2006 |  | BOILER: 5 TO < 33.5 MMBTU/H | 13.31 | NATURAL GAS | 25 | MMBTU/H (75 MMBTU/H TOTAL) | EQUIP: THREE 25 MMBTU/H STEAM BOILERS WITH FUEL OIL (AMBER 363) BACKUP, MFR: CLEAVER-BROOKS, TYPE: STEAM BOILER, MODEL: 4WI700-600-150ST, FUNC EQUIP: PROVIDES HEAT TO A NEW HOSPITAL, FUEL_TYPE: BACKUP WITH AMBER 363 (BACT) UP TO 192 HRS/YR, SCHEDULE: CONT | Carbon Monoxide | A | ULTRA-LOW NOX BURNER | 50 | PPMV AT 3% O2 | 6-MIN AV
*NV-0046 | GOODSPRINGS COMPRESSOR STATION | KERN RIVER GAS TRANSMISSION COMPANY | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2006-05-16 | 2006 | THE FACILITY IS A COMPRESSOR STATION ON AN INTER-STATE PIPELINE FOR TRANSPORTING NATURAL GAS. THE FACILITY IS A MAJOR STATIONARY SOURCE FOR NITROGEN OXIDES IN A NON-ATTAINMENT AREA FOR OZONE AIR QUALITY. | COMMERCIAL/INSTITUTIONAL BOILER | 13.31 | NATURAL GAS | 3.85 | MMBTU/H | THE UNIT'S MODEL IDENTIFICATION IS PEERLESS 724 FDA WU. | Carbon Monoxide | P | GOOD COMBUSTION PRACTICE | 0.083 | LB/MMBTU |  | 1.42 | T/YR
NV-0044 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S ENTERTAINMENT | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2007-01-04 | 2007 | THE FACILITY IS A NEW MAJOR STATIONARY SOURCE FOR NITROGEN OXIDES AS A RESULT OF CONSOLIDATING SIX LARGE HOTEL/CASINO RESORTS, WHICH ARE HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. | COMMERCIAL/INSTITUTIONAL-SIZE BOILERS | 13.31 | NATURAL GAS | 35.4 | MMBTU/H | THE BACT DETERMINATIONS REPORTED HERIN ARE SPECIFICALLY FOR THE TWO HURST BOILERS INSTALLED AT CAESAR'S PALACE. EACH OF THEM HAS A RATED HEAT INPUT OF 35.4 MMBTU/HR. THE PERMITTING ACTION ALSO APPROVED THE INSTALLATION OF A NUMBER OF SMALL BOILERS, ALL OF | Carbon Monoxide | P | GOOD COMBUSTION DESIGN | 0.036 | LB/MMBTU |  | 49 | PPMVD | 3% OXYGEN | 0.036 | LB/MMBTU |  | THE DATA PERTAIN TO EITHER ONE OF THE HURST BOILERS, WHICH RATED HEAT INPUT IS 35.4 MMBTU/H.
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | 2007 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NATURAL GAS | 13.31 | NATURAL GAS | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. WITH #2 OIL BACKUP TWO SET OF LIMITS, THIS ONE FOR NATURAL GAS | Carbon Monoxide | N |  | 1.7 | LB/H |  | 7.5 | T/YR |  | 0.083 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
*AL-0231 | NUCOR DECATUR LLC | NUCOR CORPORATION | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-06-12 | 2007 | THE FACILITY PRODUCES STEEL COILS PRIMARILY FROM STEEL SCRAP USING THE ELECTRIC ARC FURNACE (EAF) PROCESS. | GALVANIZING LINE FURNACE | 13.31 | NATURAL GAS | 98.7 | MMBTU/H |  | Carbon Monoxide | N |  | 0.084 | LB/MMBTU |  | 8.3 | LB/H |  | 0.084 | LB/MMBTU
IA-0088 | ADM CORN PROCESSING - CEDAR RAPIDS | ARCHER DANIELS MIDLAND | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-06-29 | 2007 | CONSISTS OF THREE DISTINCT OPERATIONS: CORN WET MILL, CORN DRY MILL AND BOILERHOUSE | INDIRECT-FIRED DDGS DRYER | 13.31 | NATURAL GAS | 93.7 | MMBTU/H | PROJECT INCLUDES THE INSTALLATION OF EIGHT IDENTICAL DDGS DRYERS. PERMITS 07-A-546-P, 547, 548, 549, 550, 557, 558 AND 559. THE COMBUSTION CHAMBER AND THE FEED CHAMBER ARE SEPERATED BY A HEAT EXCHANGER. THE DRYERS CAN FIRE NATURAL GAS, BIOGAS FROM THE WWT | Carbon Monoxide | A | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 0.1 | LB/MMBTU | AVERAGE OF 3 TEST RUNS |  |  |  | 0.1 | LB/MMBTU
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED BATCH ANNEALING FURNACE (535) | 13.31 | NATURAL GAS | 99 | MMBTU/H | THIS PROCESS IS COVERED UNDER 503-0095-X005. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Carbon Monoxide | N |  | 0.09 | LB/MMBTU |  | 8.91 | LB/H |  | 0.09 | LB/MMBTU
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED PASSIVE ANNEALING FURNACE (LO41) | 13.31 | NATURAL GAS | 27.2 | MMBTU/H | THIS PROCESS IS COVERED UNDER 503-0095-X013. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Carbon Monoxide | N |  | 0.09 | LB/MMBTU |  | 2.45 | LB/H |  | 0.09 | LB/MMBTU
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED BATCH ANNEALING FURNACES (LA63, LA64) | 13.31 | NATURAL GAS | 33.4 | MMBTU each | THIS PROCESS IS COVERED UNDER 503-0095-X014. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Carbon Monoxide | N |  | 0.09 | LB/MMBTU |  | 3.01 | LB/H |  | 0.09 | LB/MMBTU
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | 3 NATURAL GAS-FIRED BOILERS WITH ULNB & EGR (537-539) | 13.31 | NATURAL GAS | 64.9 | MMBtu each | THIS PROCESS IS COVERED UNDER 503-0095-X026. | Carbon Monoxide | N |  | 0.04 | LB/MMBTU |  | 2.62 | LB/H |  | 0.04 | LB/MMBTU
MI-0301 | ALCHEM ALUMINUM | ALCHEM ALUMINUM, INC. | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 2000-05-02 | 2000 | SECONDARY ALUMINUM PRODUCTION. | FLUES | 13.31 | NATURAL GAS | 42000 | LB/H | HOLDING CAPACITIES ARE 170,000 AND 250,000 LBS. BURNER CAPACITIES ARE 34,000,000 AND 48,000,000 BTU/HR. | Chlorine / Chlorine Compounds | N | COMBUSTION FLUES DO NOT HAVE ADD-ON CONTROL | 0.03 | LB/H | CHLORINE GAS | 0.12 | T/YR | CHLORINE GAS
MI-0301 | ALCHEM ALUMINUM | ALCHEM ALUMINUM, INC. | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 2000-05-02 | 2000 | SECONDARY ALUMINUM PRODUCTION. | REVERBERATORY FURNACES | 13.31 | NATURAL GAS | 42000 | LB/H | HOLDING CAPACITIES ARE 170,000 AND 250,000 POUNDS. BURNER CAPACITIES ARE 34,000,000 AND 48,000,000 BTU/H. REQ'D TESTS FOR PM, D/F, HCL, HF, CL2, VOC. ALL PERMIT LIMITS ARE BASED ON STACK TESTS OF FURNACES 1,2,7,8 AT CORPORATE'S COLDWATER MI COMPARABLE FAC | Dioxins & Furans | P | DIOXIN AND FURAN EMISSIONS FROM THE FURANCES SHALL NOT EXCEED 0.00021 GRAIN OF D/F TEQ PER TON OF FEED/CHARGE. PER NESHAP-RRR. | 0.0002 | GRAIN/TON
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | B63, S63; B64, S64 - NATURAL GAS STATION HEATER 1 AND 2 | 13.31 | NATURAL GAS | 0.75 | MMBTU/H | EMISSION LIMITS ARE THOSE FOR EACH UNIT. | Fluorine | P | NATURAL GAS | 0.0002 | LB/H | [7 empty] | FLUORIDES (LIMIT IS FOR EACH UNIT)
MI-0301 | ALCHEM ALUMINUM | ALCHEM ALUMINUM, INC. | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 2000-05-02 | 2000 | SECONDARY ALUMINUM PRODUCTION. | REVERBERATORY FURNACES | 13.31 | NATURAL GAS | 42000 | LB/H | HOLDING CAPACITIES ARE 170,000 AND 250,000 POUNDS. BURNER CAPACITIES ARE 34,000,000 AND 48,000,000 BTU/H. REQ'D TESTS FOR PM, D/F, HCL, HF, CL2, VOC. ALL PERMIT LIMITS ARE BASED ON STACK TESTS OF FURNACES 1,2,7,8 AT CORPORATE'S COLDWATER MI COMPARABLE FAC | Hydrochloric Acid | A | LIME INJECTED BAGHOUSE CONTROLS A PORTION OF EMISSIONS (THAT FROM THE SIDEWELLS) | 0.4 | LB/T OF FEED | [7 empty] | LIMIT IS COMBINED, FOR TWO REVERBS, SIDEWELLS AND FLUES.
MI-0301 | ALCHEM ALUMINUM | ALCHEM ALUMINUM, INC. | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 2000-05-02 | 2000 | SECONDARY ALUMINUM PRODUCTION. | FLUES | 13.31 | NATURAL GAS | 42000 | LB/H | HOLDING CAPACITIES ARE 170,000 AND 250,000 LBS. BURNER CAPACITIES ARE 34,000,000 AND 48,000,000 BTU/HR. | Hydrochloric Acid | N | FLUES: DO NOT HAVE ADD-ON CONTROLS. | 0.08 | LB/H |  | 0.35 | T/YR
TX-0309 | FORMOSA PLASTICS TEXAS | FORMOSA PLASTICS CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-02-10 | 2000 | THIS PERMIT AUTHORIZES THE OPERATION OF THE FORMOSA ETHYLENE GLYCOL PLANT & A PRODUCTION INCREASE, EQUIPMENT UPGRADES & CHANGES, ADDITIONAL FUGITIVE EMISSIONS, & AN ADDITIONAL COOLING TOWER CELL. THE APPLICANT WISHES TO CONSOLIDATE ALL FUGITIVE EMISSION P | WASTE HEAT BOILER, 70Z401 | 13.31 | NAT GAS |  |  | SHALL BE MAINTAINED AT A MINIMUM COMBUSTION CHAMBER TEMP OF 1450 F. | Hydrogen Cyanide | N | NONE INDICATED | 1.16 | LB/H |  | 0.51 | T/YR |  |  |  |  | BURNING OF HCN SHALL BE LIMITED TO 12250 LB/H.
MI-0301 | ALCHEM ALUMINUM | ALCHEM ALUMINUM, INC. | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 2000-05-02 | 2000 | SECONDARY ALUMINUM PRODUCTION. | FLUES | 13.31 | NATURAL GAS | 42000 | LB/H | HOLDING CAPACITIES ARE 170,000 AND 250,000 LBS. BURNER CAPACITIES ARE 34,000,000 AND 48,000,000 BTU/HR. | Hydrogen Fluoride | N | COMBUSTION FLUES DO NOT HAVE ADD-ON CONTROLS | 0.37 | LB/H |  | 1.62 | T/YR
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-2001A AND H-2001B | 13.31 | NAT GAS | 17.5 | MMBTU/H EACH | 17.5 MMBTU/H MAXIMUM RATE/CAPACITY EA, 13.1 MMBTU/H NOMINAL CAPACITY EA. | Hydrogen Sulfide | P | FUEL SULFUR CONTENT LIMIT; BURN NATURAL GAS WITH NO GREATER THAN 100 PPM H2S IN ANY OF THE FUEL BURNING EQUIPMENT. |  |  | SEE CONTROL DESCRIPTION
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | B63, S63; B64, S64 - NATURAL GAS STATION HEATER 1 AND 2 | 13.31 | NATURAL GAS | 0.75 | MMBTU/H | EMISSION LIMITS ARE THOSE FOR EACH UNIT. | Lead (Pb) / Lead Compounds | P | NATURAL GAS | 0 | LB/H | [7 empty] | (LIMIT IS FOR EACH UNIT)
WI-0245 | WPSC - WESTON POWER PLANT | WPSC - WESTON POWER PLANT | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2007-06-01 | 2007 |  | PROCESS B64, STACK S64 - NATURAL GAS HEATER STATION 2 | 13.31 | NATURAL GAS |  |  |  | Lead (Pb) / Lead Compounds | P | USE OF NATURAL GAS (BACT) | 0 | LB/H
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | B63, S63; B64, S64 - NATURAL GAS STATION HEATER 1 AND 2 | 13.31 | NATURAL GAS | 0.75 | MMBTU/H | EMISSION LIMITS ARE THOSE FOR EACH UNIT. | Mercury | P | NATURAL GAS | 0 | LB/H | [7 empty] | (LIMIT IS FOR EACH UNIT)
NJ-0045 | MERCK - RAHWAY PLANT | MERCK | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-01-14 | 1997 | CHEMICAL MANUFACTURING | BOILERS - NAT GAS (3) | 13.31 | NATURAL GAS | 99.5 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW-NOX BURNERS | 1.1 | LB/H |  | 0.011 | LB/MMBTU |  | 0.011 | LB/MMBTU |  | BASIS OF LIMIT IS STATE EMISSION OFFSET RULE. NOX LIMIT IS AS NO2""
CA-0775 | CALIFORNIA STATE PRISON, CORCORAN | CALIFORNIA STATE PRISON, CORCORAN | CA | SAN JOAQUIN VALLEY APCD - CENTRAL REGIONAL OFFICE, CA | 1997-01-15 | 1997 |  | CLAYTON INDUSTRIES MODEL SEG-204-2-LNB BOILER | 13.31 | NATURAL GAS | 8.1 | MMBTU/HR | ARB RECORD # A310-792-97 | Nitrogen Oxides (NOx) | P | PREMIXED LEAN BURN COMBUSTION TECHNOLOGY | 0.012 | MMBTU/HR |  | 0 |  |  | 0.012 | MMBTU/HR
CA-0802 | KERN MEDICAL CENTER | KERN MEDICAL CENTER | CA | SAN JOAQUIN VALLEY APCD - CENTRAL REGIONAL OFFICE, CA | 1997-01-27 | 1997 |  | PVI INDUSTRIES MODEL 3500 BOILER | 13.31 | NATURAL GAS | 2.8 | MMBTU/HR | ARB RECORD # A350-775-97 | Nitrogen Oxides (NOx) | P | OPERATION LIMITED TO 80% UTILIZATION. RECORDKEEPING REQUIRED FOR COMPLIANCE VERIFICATION | 0 | NO NUMERIC LIMIT |  | 0 |  |  | 0
IN-0100 | ROCKPORT WORKS | AK STEEL CORPORATION | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1997-02-13 | 1997 | STEEL COIL FINISHING PLANT; ALL POLLUTANTS IN PERMIT ARE LISTED | BOILERS (2), NATURAL GAS FIRED, BH NO. 2 | 13.31 | NATURAL GAS | 76 | MMBTU/H | LOCATED IN BOILER HOUSE #2 | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 6.08 | LB/H | TOTAL |  |  |  | 0.04 | LB/MMBTU
IN-0100 | ROCKPORT WORKS | AK STEEL CORPORATION | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1997-02-13 | 1997 | STEEL COIL FINISHING PLANT; ALL POLLUTANTS IN PERMIT ARE LISTED | ANNEALING FURNACE, SECTION NO. 1 | 13.31 | NATURAL GAS | 72.3 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNER | 1.89 | LB/H |  |  |  |  | 0.04 | LB/MMBTU
IN-0100 | ROCKPORT WORKS | AK STEEL CORPORATION | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1997-02-13 | 1997 | STEEL COIL FINISHING PLANT; ALL POLLUTANTS IN PERMIT ARE LISTED | ANNEALING FURNACE, SECTION NO. 2 | 13.31 | NATURAL GAS | 55.2 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNER | 2.21 | LB/H |  |  |  |  | 0.04 | LB/MMBTU
IN-0100 | ROCKPORT WORKS | AK STEEL CORPORATION | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1997-02-13 | 1997 | STEEL COIL FINISHING PLANT; ALL POLLUTANTS IN PERMIT ARE LISTED | ANNEALING FURNACE, SECTION NO. 3 | 13.31 | NATURAL GAS | 65.7 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNER | 2.63 | LB/H |  |  |  |  | 0.04 | LB/MMBTU
IN-0100 | ROCKPORT WORKS | AK STEEL CORPORATION | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1997-02-13 | 1997 | STEEL COIL FINISHING PLANT; ALL POLLUTANTS IN PERMIT ARE LISTED | HYDROGEN BATCH ANNEALING FURNACES (16) | 13.31 | NATURAL GAS | 6.75 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 9.45 | LB/H |  |  |  |  | 0.1 | LB/MMBTU
IN-0100 | ROCKPORT WORKS | AK STEEL CORPORATION | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1997-02-13 | 1997 | STEEL COIL FINISHING PLANT; ALL POLLUTANTS IN PERMIT ARE LISTED | BOILERS (3), NATURAL GAS FIRED, BH NO. 1 | 13.31 | NATURAL GAS | 76 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 9.12 | LB/H | TOTAL |  |  |  | 0.04 | LB/MMBTU
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 8 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 50 | MMBTU/H | THE NUMBER 8 PAPER MACHINE CONSISTS OF THREE SOURCES: THE NATURAL GAS FIRED BURNERS, THE PAPER MACHINE, AND THE DUST SYSTEM. STACK TESTING FOR CO AND NOX. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.0913 | LB/MMBTU |  | 0 |  |  | 0.0913 | LB/MMBTU
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 5 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 21 | MMBTU/H | THE BURNERS FOR THE NUMBER 5 PAPER MACHINE HAVE BEEN UPGRADED. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.0193 | LB/MMBTU |  | 0 |  |  | 0.0193 | LB/MMBTU
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 6 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 58.4 | MMBTU/H | THE BURNERS FOR THE NUMBER 6 PAPER MACHINE HAVE BEEN UPGRADED. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.0913 | LB/MMBTU |  | 0 |  |  | 0.0913 | LB/MMBTU
AR-0019 | QUINCY SOYBEAN COMPANY OF ARKANSAS | QUINCY SOYBEAN COMPANY OF ARKANSAS | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-03-04 | 1997 |  | BOILER, COGENERATION/WASTE HEAT RECOVERY | 13.31 | NATURAL GAS | 68 | MMBTU/H | TURBINE AND WASTE HEAT RECOVERY BOILER BOTH EXHAUST THROUGH SN-65 THROUGHPUT: 68 MMBTU/H AND 79 MMBTU/H | Nitrogen Oxides (NOx) | P | LOW NOX COMBUSTORS | 25 | PPM @ 15% O2 |  | 0 |  |  | 0 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HIGH PRESSURE BOILER #2-R2 | 13.31 | FUEL OIL | 0.3 | MMBTU/H | PERMIT NO: 97-A-416 FUEL OIL < 10,674,202 GALLONS/Y PER WHOLE FACILITY SULFUR CONTENT OF FUEL OIL < 0.05 % BY WEIGHT | Nitrogen Oxides (NOx) | P | LOW NOX/FGR ALTERNATE EMISSION LIMIT:130 PPM | 1.66 | LB/H |  | 5.69 | T/YR |  |  |  |  | 5.5 | LB/MMBTU (Outlier)
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #3 B3 | 13.31 | NATURAL GAS | 2.3 | MMBTU/HR | BOILER BURNS NATURAL GAS OR FUEL OIL. PERMIT NO: 97-A-408 20% OPACITY PER NSPS SUBPART DC SO2 SET AT 9.46 TPY TO STAY UNDER PSD SIGNIFICANCE | Nitrogen Oxides (NOx) | P | LOW NOX BURNER, FLUE GAS RECIRC. ADDITIONAL EMISSION LIMIT: 70 PPM | 6.81 | LB/H |  | 11.79 | T/YR |  |  |  |  | 3 | LB/MMBTU (Outlier)
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #2 B2 | 13.31 | NATURAL GAS | 2.3 | MMBTU/H | 20% OPACITY BY NSPS SUBPART DC SO2 - 9.46 TPY TO STAY UNDER PSD SIGNIFICANCE | Nitrogen Oxides (NOx) | P | LOW NOX BURNER FLUE GAS RECIRC. ADDITIONAL EMISSION LIMIT: 70 PPM | 6.8 | LB/H |  | 11.79 | T/YR |  |  |  |  | 3 | LB/MMBTU (Outlier)
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #1 | 13.31 | NATURAL GAS | 2.3 | MMBTU/H | FUEL IS NATURAL GAS AND FUEL OIL ONLY. PERMIT NUMBER: 97-A-377. 20 % OPACITY NSPS SUBPART BC SO2 - 9.46 TPY, SET TO STAY UNDER PSD SIGNIFICANCE LEVELS | Nitrogen Oxides (NOx) | P | LOW NOX BURNER, FLUE GAS RECIRC. | 6.81 | LB/H |  | 11.79 | T/YR |  |  |  |  | 3 | LB/MMBTU (Outlier)
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HYDROGEN PLANT BURNER R9 | 13.31 |  |  |  | PERMIT NUMBER: 97-A-391 20% OPACITY - 1A 23.3(2)D. THIS PROCESS GENERATES HYDROGEN FROM NATURAL GAS. THE HYDROGEN IS USED FOR THE HYDROGENATION OF THE SOYBEAN OIL. | Nitrogen Oxides (NOx) | N |  | 2.1 | LB/H |  | 9.2 | T/YR |  | 0.14 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HIGH PRESSURE BOILER #1 | 13.31 | NATURAL GAS | 0.3 | MMBTU/H | FUELS ARE NATURAL GAS AND #2FUEL OIL. PERMIT NUMBER 97-A-390 20% OPACITY BY NSPS SUBPART DC SO2 LIMIT 1.26 TPY TO STAY UNDER PSD SIGNIFICANCE | Nitrogen Oxides (NOx) | N | ADDITIONAL EMISSION LIMIT: 130 PPM | 1.66 | LB/H |  | 5.96 | T/YR |  |  |  |  | 5.5 | LB/MMBTU (Outlier)
KY-0068 | TOYOTA MOTOR MANUFACTURING, USA, INC | TOYOTA MOTOR MANUFACTURING, USA, INC | KY | KENTUCKY DEP, DIV FOR AIR QUALITY | 1997-05-29 | 1997 | MODIFICATION OF AN AUTOMOBILE ASSEMBLY PLANT (THIRD REVISION OF PERMIT) | BOILER (NATURAL GAS) | 13.31 | NATURAL GAS | 96 | MMBTU/H | A SEPARATELY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING FUEL OIL (BACKUP FUEL). WHEN FIRING NATURAL GAS, ANNUAL OPERATING HOURS SHALL NOT EXCEED 6132 H/YR. | Nitrogen Oxides (NOx) | N | N/A | 0.1 | LB/MMBTU |  |  |  |  | 0.1 | LB/MMBTU
AL-0139 | ANNISTON ARMY DEPOT | U.S. ARMY - ANNISTON ARMY DEPOT | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-06-19 | 1997 |  | BOILER, NATURAL GAS FIRED, 2 | 13.31 | NATURAL GAS | 13.4 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS, CLEAN FUEL | 0.03 | LB/MMBTU |  | 0.8 | LB/H |  | 0.03 | LB/MMBTU
AL-0140 | ANNISTON ARMY DEPOT | U.S. ARMY - ANNISTON ARMY DEPOT | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-06-19 | 1997 |  | BOILER, NATURAL GAS FIRED, 2 | 13.31 | NATURAL GAS | 11.7 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | CLEAN FUEL, LOW NOX BRUNERS | 0.03 | LB/MMBTU |  | 0.7 | LB/H |  | 0.03 | LB/MMBTU
WI-0188 | GOLDEN BOOKS PUBLISHING COMPANY INC. | GOLDEN BOOKS PUBLISHING COMPANY INC. | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 1997-06-24 | 1997 | PRINTING FACILITY | SPACE HEAT & COMBUSTION SOURCES, (P01 S01) | 13.31 | NATURAL GAS | 93 | MMBTU/H | SECOND FUEL: PROPANE | Nitrogen Oxides (NOx) | N | REGULATORY BASIS: STATE REGULATION. | 18.8 | LB/H |  |  |  |  | 0.2 | LB/MMBTU
LA-0115 | GEISMAR PLANT | SHELL CHEMICAL COMPANY | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1997-11-03 | 1997 | PERMIT FOR A NEW POLYMER PRODUCTION COMPLEX AT AN EXISTING SOCMI FACILITY | HEATER, HOT OIL | 13.31 | NATURAL GAS | 54.9 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND INTERNAL FLUE GAS RECIRCULATION | 0.06 | LB/MMBTU |  | 0 |  |  | 0.06 | LB/MMBTU
PA-0149 | BUCKNELL UNIVERSITY | BUCKNELL UNIVERSITY | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 1997-11-26 | 1997 |  | HEAT RECOVERY BOILER | 13.31 | NG SUPPLEMENT | 24000 | LB/HR STEAM | COMPLIANCE WILL BE VERIFIED BY STACK TESTS. ENERGY RECOVERY INTERNATIONAL HSRG RATED AT 70,000 LB STEAM/HR WHEN SUPPLEMENTAL FUEL IS FIRED. EMISSION LIMITATIONS APPLY WHEN TURBINE IS IN OPERATION. | Nitrogen Oxides (NOx) | N |  | 0.1 | LB/MMBTU |  | 5.03 | LB/HR |  | 0.1 | LB/MMBTU
LA-0113 | BASF CORPORATION | BASF CORPORATION | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1997-12-30 | 1997 |  | DUCT BURNER, COGEN UNIT NO. 2 | 13.31 | NATURAL GAS | 0.4 | MMLB/H STEAM |  | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS AND SCR TO LIMIT NOX TO 8 PPM FOR NATURAL GAS AND 25 PPM FOR WASTE GAS (80% H2) | 8 | PPMV NAT. GAS |  | 25 | PPM 80% H2 |  | 0.0295 | LB/MMBTU
WY-0034 | SOLVAY SODA ASH JOINT VENTURE TRONA MINE/SODA ASH | SOLVAY SODA ASH JOINT VENTURE TRONA MINE/SODA ASH | WY | WYOMING AIR QUAL DIV, DEPT OF ENV QUAL | 1998-02-06 | 1998 |  | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 100 | MMBTU/H | HEATING MINE VENTILATION AIR | Nitrogen Oxides (NOx) | P | LOW NOX" BURNER SYSTEM" | 0.038 | LB/MMBTU |  | 0 |  |  | 0.038 | LB/MMBTU
AK-0036 | KUPARUK CENTRAL PRODUCTION FACILITY | ARCO ALASKA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1998-02-13 | 1998 |  | PROCESS HEATER | 13.31 | NATURAL GAS | 8 | MMBTU/H | OTHER COMPLIANCE: FACILITY OPERATING REPORTS. PERMIT LIMITS NOX AND H2S IN FUEL (SO2, PM10 AND VE). CO AND VOC ARE NOT INCLUDED IN THIS PERMIT. | Nitrogen Oxides (NOx) | P | CZ LINER LEAN-HEAD COMBUSTION TECHNOLOGY | 150 | PPMVD |  | 266 | LB/H |  |  |  |  | 33.25 | LB/MMBTU | CALCULATED (Outlier)
LA-0112 | GEISMAR FACILITY | AIR LIQUIDE AMERICA CORP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1998-02-13 | 1998 | AIR SEPARATION TO PRODUCE NITROGEN AND OXYGEN IN LIQUIDIZED GAS FORMS - ALSO TRANSPORT. PROJECT: NEW COGEN UNIT, NATURAL GAS FIRED FRAME 7 GE TURBINE WITH DUCT BURNER. | BOILER NO. 1 | 13.31 | NATURAL GAS | 95 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 4.75 | LB/H | HOURLY MAXIMUM | 20.81 | T/YR | ANNUAL MAXIMUM | 0.05 | LB/MMBTU | THREE ONE-HOUR TEST AVERAGE
LA-0112 | GEISMAR FACILITY | AIR LIQUIDE AMERICA CORP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1998-02-13 | 1998 | AIR SEPARATION TO PRODUCE NITROGEN AND OXYGEN IN LIQUIDIZED GAS FORMS - ALSO TRANSPORT. PROJECT: NEW COGEN UNIT, NATURAL GAS FIRED FRAME 7 GE TURBINE WITH DUCT BURNER. | REACTIVATION HEATERS (2) | 13.31 |  | 9 | MMBTU/H | THROUGHPUT FOR EACH UNIT | Nitrogen Oxides (NOx) | N |  | 0.39 | LB/H | HOURLY MAXIMUM | 1.71 | T/YR | ANNUAL MAXIMUM | 0.043 | LB/MMBTU | CALCULATED
WY-0042 | LOUISIANA LAND AND EXPLORATION COMPANY-LOST CABIN | LOUISIANA LAND AND EXPLORATION COMPANY-LOST CABIN | WY | WYOMING AIR QUAL DIV, DEPT OF ENV QUAL | 1998-04-03 | 1998 |  | BOILER, AUXILIARY, NATURAL GAS | 13.31 |  | 22.89 | MMBTU/H | CLEAVER-BROOKS BOILER TO PROVIDE PLANT START UP AND AUXILIARY STEAM. | Nitrogen Oxides (NOx) | N |  | 2.3 | LB/H |  | 0 |  |  | 0.10048 | LB/MMBTU
MI-0283 | WESTERN MICHIGAN UNIVERSITY | WESTERN MICHIGAN UNIVERSITY | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 1998-04-27 | 1998 | POWER PLANT | DUCT BURNER, 2 EACH | 13.31 | NATURAL GAS | 85 | MMBTU/H | THROUGHPUT FOR EACH. BY STACK TESTING IT WAS FOUND THAT WHEN OPERATED WITHOUT THE UPSTREAM TURBINE (IN THE FRESH AIR FIRING MODE), THE DUCT BURNERS PERFORMED NO BETTER THAN 0.17 LB/MMBTU. ONLY CO AND NOX WERE ADDRESSED IN THIS DETERMINATION. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS. EMISSION LIMITS APPLY TO EACH HRSG UNIT, WHILE PPERATING IN THE FRESH AIR MODE.. | 15.3 | LB/H |  | 44.7 | T/YR |  | 0.18 | LB/MMBTU
WY-0051 | UNION PACIFIC RESOURCES - PATRICK DRAW GAS PLANT | UNION PACIFIC RESOURCES - PATRICK DRAW GAS PLANT | WY | WYOMING AIR QUAL DIV, DEPT OF ENV QUAL | 1998-05-18 | 1998 |  | HEATER, 2 EA | 13.31 | NATURAL GAS | 45 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX LEAN BURN TECHNOLOGY | 0.03 | LB/MMBTU |  | 0 |  |  | 0.03 | LB/MMBTU
WY-0052 | UNION PACIFIC RESOURCES - PATRICK DRAW GAS PLANT | UNION PACIFIC RESOURCES - PATRICK DRAW GAS PLANT | WY | WYOMING AIR QUAL DIV, DEPT OF ENV QUAL | 1998-05-18 | 1998 |  | HEATER, 2 EA | 13.31 | NATURAL GAS | 45 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS. | 0.03 | LB/MMBTU |  | 0 |  |  | 0.03 | LB/MMBTU
IA-0048 | CARGILL INC - SIOUX CITY | CARGILL INC - SIOUX CITY | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1998-06-01 | 1998 | SOYBEAN OIL MILL | BOILER, BACKUP | 13.31 |  | 77 | MMBTU/H | PERMIT NUMBER FOR THIS PROCESS IS 86-A-036-S1. permit for PM/PM10 and NOx only | Nitrogen Oxides (NOx) | N |  | 13.6 | LB/H |  |  |  |  | 0.18 | LB/MMBTU |  | Synthetic minor. PROJECT NOT SIGNIFICANT FOR NOX - NO BACT DETERMINATI0N REQUIRED.
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | 1998 | VEGETABLE OIL PLANT | BOILER, NEBRASKA, NAT GAS | 13.31 | NATURAL GAS | 28 | MMBTU/H | See separate process for backup fuel (No. 2 oil) requirements. | Nitrogen Oxides (NOx) | N |  | 5.8 | LB/H |  |  |  |  | 0.21 | LB/MMBTU
IN-0104 | CON AGRA SOYBEAN PROCESSING CO. | CON AGRA SOYBEAN PROCESSING CO. | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1998-08-14 | 1998 | SOYBEAN PROCESSING | BOILERS, REFINERY & HYDROGEN PLANT REFORMER | 13.31 | NATURAL GAS | 10 | MMBTU/H | 2 refinery boilers: 10 mmBtu/h each; 1 hydrogen plant reformer boiler: 20 mmBtu/h | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 0.0365 | LB/MMBTU |  |  |  |  | 0.0365 | LB/MMBTU
CA-0862 | H&H HEAT TREATING | H&H HEAT TREATING | CA | SOUTH COAST AQMD, CA | 1998-09-29 | 1998 |  | FURNACE, HEAT TREATING, ABAR ISPEN | 13.31 | NATURAL GAS | 7 | MMBTU/H | ARB RECORD #: A310-873-99 | Nitrogen Oxides (NOx) | P | ELEVEN LOW NOX BURNERS, NORTH AMERICAN MODELS (FIVE) 4442-3 AND (SIX) 4442-5 | 0 |  |  | 0
TX-0300 | SALT CREEK GAS PLANT | MOBIL EXPLORATION & PRODUCING US INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-10-13 | 1998 | MOBIL EXPLORATION & PRODUCING US INC HAS REQUESTED AN AMENDMENT TO PERMIT NO 20660 AND A MODIFICATION TO PSD-TX-795 TO (1) INCREASE THE CO AND VOC ALLOWABLES ON THEIR COOPER-BESSEMER GMVH-12C2 ENGINES TO ALLOW THEM TO BETTER CONTROL NOX TO THE 2 G/HP-H LE | HOT OIL HEATER, EPN 26 | 13.31 | NAT GAS | 32.2 | MMBTU/H |  | Nitrogen Oxides (NOx) | N | NONE INDICATED | 7.27 | T/YR |  | 1.66 | LB/H |  | 0.06 | LB/MMBTU
MS-0041 | VICKSBURG CHEMICAL COMPANY |  | MS | MISSISSIPPI DEPT OF ENV QUALITY | 1998-10-27 | 1998 |  | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 99 | MMBTU/H | NOX IS THE ONLY POLLUTANT THE PROCESS IS PSD FOR. | Nitrogen Oxides (NOx) | B | LOW NOX BURNER AND FLUE GAS RECIRCULATION. EMISSION LIMIT BASIS IS PSD AND NSPS. | 0.042 | LB/MMBTU |  |  |  |  | 0.042 | LB/MMBTU
OH-0245 | REPUBLIC TECHNOLOGIES INTERNATIONAL | REPUBLIC TECHNOLOGIES INTERNATIONAL/CANTON | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 1999-01-27 | 1999 | STEEL MILL. THIS PLANT IS PSD FOR PM, SO2, NOX, CO, AND VOC. THIS MODIFICATION IS A SIGNIFICANT INCREASE FOR NOX. | ECCENTRIC BOTTOM TAPPING LADLE PREHEATER FURNACE | 13.31 | NATURAL GAS | 14 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNER | 1.25 | LB/H |  | 5.5 | T/YR |  | 0.089 | LB/MMBTU
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | WASTE HEAT RECOVERY, UNIT 10 | 13.31 | NATURAL GAS | 52.8 | MMBTU/H | MAXIMUM OPERATION DURING COMMISSIONING PERIOD: 1848 H MAXIMUM OPERATION AFTER COMMISSIONING PERIOD: 1000 H UNDER NORMAL LONG-TERM OPERATIONS, THE WASTE HEAT RECOVERY SUPPLEMENTAL BURNER WILL NOT BE OPERATED. OPERATION OF THIS BURNER IS UNDER AN ALTERNATIV | Nitrogen Oxides (NOx) | N | NONE INDICATED | 0.12 | LB/MMBTU |  |  |  |  | 0.12 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 1 (NATURAL GAS) | 13.31 | NATURAL GAS | 84.4 | MMBTU/H | MFR. IS COMBUSTION ENGINEERING. ONLY NATURAL GAS, A MIXTURE OF NO. 2 OIL AND LASALOCID OIL, AND NO. 2 OIL SHALL BE FIRED IN BOILER 1. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. AFTER APRIL 3 | Nitrogen Oxides (NOx) | N |  | 33.8 | LB/H |  | 0.4 | LB/MMBTU |  | 0.4 | LB/MMBTU
CO-0040 | AMERICAN SODA, LLP, PARACHUTE FACILITY |  | CO | COLORADO DEPT OF HEALTH - AIR POLL CTRL | 1999-05-06 | 1999 |  | INDUSTRIAL BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 80.8 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX COMBUSTION SYSTEM. CAPITAL COSTS ARE INCLUDED IN EQUIPMENT COSTS; ANNUALIZED COSTS ARE INCLUDED IN OPERATION AND MAINTENANCE | 0.05 | LB/MMBTU |  |  |  |  | 0.05 | LB/MMBTU
CO-0041 | AMERICAN SODA, LLP, PINEANCE FACILITY |  | CO | COLORADO DEPT OF HEALTH - AIR POLL CTRL | 1999-05-06 | 1999 |  | BOILER NO.2, TEST MINE HOT WATER (1) | 13.31 | NATURAL GAS | 51.08 | MMBTU | NATURAL GAS FIRED HOT WATER BOILER PRODUCES HIGH PRESSURE HOT WATER FOR INJECTION INTO THE WELLS. ONLY NOX, CO AND PM EMISSION LIMITS HAVE BEEN PROVIDED FOR THIS PROCESS. | Nitrogen Oxides (NOx) | P | LOW NOX COMBUSTION SYSTEM. NO ADD-ON COSTS. COSTS PART OF OPERATION. | 0.05 | LB/MMBTU |  |  |  |  | 0.05 | LB/MMBTU
IN-0079 | STEEL DYNAMICS, INC. | STEEL DYNAMICS, INC. | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1999-07-07 | 1999 |  | DRYERS, NATURAL GAS FIRED; (PREHEATERS) | 13.31 | NATURAL GAS | 10 | MMBTU/H | THESE HEATERS AND DRYERS ARE FOR THE TUNDISH AND LADLES. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.1 | LB/MMBTU |  | 0 |  |  | 0.1 | LB/MMBTU
IN-0080 | STEEL DYNAMICS, INC. | STEEL DYNAMICS, INC. | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 1999-07-07 | 1999 |  | PREHEATERS, NATURAL GAS FIRED | 13.31 | NATURAL GAS | 10 | MMBTU/H | THESE HEATERS AND DRYERS ARE FOR THE TUNDISH AND LADLES. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.1 | LB/MMBTU |  | 0 |  |  | 0.1 | LB/MMBTU
CA-0917 | SOUTHERN CALIFORNIA GAS COMPANY | SOUTHERN CALIFORNIA GAS COMPANY | CA | SOUTH COAST AQMD, CA | 1999-08-17 | 1999 |  | HOT OIL HEATER, AMERICAN HEATER COMPANY | 13.31 | NATURAL GAS | 6.5 | MMBTU/H | ARB RECORD # A310-944-00 AMERICAN HEATER COMPANY MODEL AHE-650 HOT OIL HEATER USED TO REGENERATE LIQUID ABSORBENT (TRIETHYLENE GLYCOL) BY HEATING IT TO APPROXIMATELY 450 DEGREES F. TO REMOVE ABSORBED WATER. PERMIT SETS LIMITS FOR NOX AND CO, NO OTHER POLL | Nitrogen Oxides (NOx) | P | POWER FLAME MODEL C5-G-30B LOW-NOX BURNER. | 20 | PPMVD @ 3% O2 | [6 empty] | Not Available | PERMIT LIMITS SET IN PPM, STANDARD UNITS NOT AVAILABLE.
CA-0948 | MARUCHAN, INC. | MARUCHAN, INC. | CA | SOUTH COAST AQMD, CA | 1999-09-09 | 1999 | PASTA AND MACARONI PRODUCTION FACILITY | BOILER, (2) | 13.31 | NATURAL GAS | 8.18 | MMBTU/H | 2 BOILERS, MIURA MODEL LX-200SG | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 15 | PPMVD | Corrected to 3% O2 |  |  |  | 0.018 | LB/MMBTU | Calculated using F-Factor | NOX 15 MIN @ 3% O2
MA-0029 | SITHE MYSTIC DEVELOPMENT LLC | SITHE MYSTIC DEVELOPMENT LLC | MA | MASSACHUSETTS DIV OF AIR QUAL CONTROL | 1999-09-29 | 1999 | COMBINED CYCLE ELECTRIC GENERATING FACILITY | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 96 | MMBTU/H |  | Nitrogen Oxides (NOx) | A | SCR | 3.4 | LB/H |  |  |  |  | 0.035 | LB/MMBTU
OK-0051 | GREEN COUNTRY ENERGY PROJECT | COGENTRIX ENERGY INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 1999-10-01 | 1999 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS |  |  |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.049 | LB/MMBTU |  |  |  |  | 0.049 | LB/MMBTU
CA-0923 | ARAMARK UNIFORM CLEANERS | ARAMARK UNIFORM CLEANERS | CA | SAN JOAQUIN VALLEY APCD - CENTRAL REGIONAL OFFICE, CA | 1999-10-04 | 1999 | FACILITY PROCESS SOLVENT-LADEN TOWELS AND UNIFORMS. ITEMS ARE COUNTED ON A TABLE SERVED BY AN UNCONTROLLED EXHAUST HOOD AND PLACED INTO INDUSTRIAL WASHERS AND DRYERS (CHALLENGER CPG4-3S3L BURNERS, 2.75 MMBTU/H) | DRYER, NATURAL GAS | 13.31 | NATURAL GAS | 2.75 | MMBTU/H | ARB RECORD # A340-951-00. DRYER PROCESSES SOLVENT LADEN TOWELS, < 950 LB TOWELS/DAY. BACT NOT TRIGGERED FOR PM10 OR SOX | Nitrogen Oxides (NOx) | P | NATURAL GAS-FIRED BURNER | 49.3 | PPMV |  |  |  |  | 0.0608 | LB/MMBTU
OK-0029 | PSO NORTHEASTERN POWER STA | PUBLIC SVC CO OF OK | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 1999-10-18 | 1999 | ELECTRICITY GENERATOR | DUCT BURNER | 13.31 | NATURAL GAS | 99 | MMBTU |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.009 | LB/MMBTU |  |  |  |  | 0.009 | LB/MMBTU
CA-0929 | FEDERAL BUREAU OF PRISONS | FEDERAL BUREAU OF PRISONS | CA | SAN JOAQUIN VALLEY APCD, CA | 1999-11-12 | 1999 |  | GAS ABSORPTION CHILLERS (GAC) FOR AIR CONDITIONING | 13.31 | NATURAL GAS | 7.6 | MMBTU/H | ARB RECORD # A310-958-00 BACT NOT TRIGGERED FOR VOC, CO, SOX, PM10 NOX NOT AVAILABLE IN LB/MMBTU. | Nitrogen Oxides (NOx) | P | LOW-NOX BURNER | 20 | PPMV @ 3% O2 |  |  |  |  | 0.024 | LB/MMBTU
CA-0919 | COCA COLA | COCA COLA | CA | SOUTH COAST AQMD, CA | 1999-11-23 | 1999 |  | BOILER, FIRE TUBE | 13.31 | NATURAL GAS | 31.5 | MMBTU/H | ARB RECORD # A310-947-00 SCOTCH MARINE CUSTOM FIRE-TUBE BOILER USED TO PROVIDE STEAM FOR SANITATION. BACT LIMITS ARE APPLIED TO NOX AND CO LEVELS. NO BACT LIMITS WERE APPLIED TO PM, ROG, AND SOX. DEFAULT EMISSION FACTORS ARE THE BASIS OF THE PM, ROG AND S | Nitrogen Oxides (NOx) | B | COEN LOW-NOX BURNER, PEERLESS MFG. COMPANY SELECTIVE CATALYTIC REDUCTION SYSTEM WITH NH3 INJECTION | 7 | PPMVD @ 3% O2 |  |  |  |  | 0.0085 | LB/MMBTU
CA-0918 | SCHI SANTA MONICA BEACH HOTEL ASSOCIATES | SCHI SANTA MONICA BEACH HOTEL ASSOCIATES | CA | CALIFORNIA AIR RESOURCES BOARD | 1999-12-02 | 1999 |  | CLAYTON WATER-TUBE BOILER | 13.31 | NATURAL GAS | 4.29 | MMBTU/H | ARB RECORD # A310-945-00 CLAYTON MODEL E6100-LNB WATER TUBE BOILER USED TO SUPPLY HOT WATER BACT LIMITS SET FOR NOX AND CO. NO EMISSIONS LIMITS ON PM, VOC AND SOX. | Nitrogen Oxides (NOx) | P | ULTRA LOW-NOX BURNER SYSTEM | 12 | PPMVD @ 3% O2 |  |  |  |  | 0.015 | LB/MMBTU
CA-0938 | CHILDREN'S HOSPITAL LOS ANGELES | CHILDREN'S HOSPITAL LOS ANGELES | CA | SOUTH COAST AQMD, CA | 1999-12-02 | 1999 | BOILERS USED TO PRODUCE STEAM. | BOILER, (3) | 13.31 | NATURAL GAS | 33.9 | MMBTU/H | 3 boilers, one 33.9 MMBtu/h and two 24.2 MMBtu/h each. Limits and controls for each boiler are the same. BACT review for CO and NOx, NH3 also included. | Nitrogen Oxides (NOx) | A | HONEYCOMB TYPE CATALYST BED WITH ANHYDROUS AMMONIA INJECTION GRID (SCR) | 7 | PPMVD | at 3% O2 |  |  |  | 0.0085 | LB/MMBTU | Calculated using F-Factor
CA-1021 | DAMAPONG TEXTILES | DAMAPONG TEXTILES | CA | SOUTH COAST AQMD, CA | 1999-12-07 | 1999 |  | BOILER: 16.5 MMBTU/H | 13.31 | NATURAL GAS | 16.5 | MMBTU/H | EQUIP: NATURAL GAS FIRED-TUBE BOILER, MFR: SELLERS ENGINEERING, MODEL: 105E-395 HP, FUNC EQUIP: TO PROVIDE STEAM FOR A DYE TANK, SCHEDULE: VARIABLE, | Nitrogen Oxides (NOx) | N | SELCTIVE CATALYTIC REDUTION, AMMONIA SLIP 5 PPMVD @ 3%O2 | 7 | PPMVD@3% O2 | 15-MIN AVG | [5 empty] | NOT AVAILABLE
CA-0939 | HI-COUNTRY | HI-COUNTRY FOODS | CA | SOUTH COAST AQMD, CA | 1999-12-16 | 1999 | BOILER USED TO SUPPLY STEAM TO HEAT EVAPORATORS AND PASTEURIZING SYSTEMS. | BOILER | 13.31 | NATURAL GAS | 20.9 | MMBTU/H | Fire tube boiler equipped with low NOx burners. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 9 | PPMVD | Corrected to 3% O2 |  |  |  | 0.011 | LB/MMBTU | Calculated using F-Factor | NOX 15 MIN @ 3% O2
CA-1006 | HI-COUNTRY | HI-COUNTRY | CA | SOUTH COAST AQMD, CA | 1999-12-16 | 1999 |  | BOILER, 20.9 MMBTU/H | 13.31 | NATURAL GAS | 20.9 | MMBTU/H | EQUIP: ALZETA, ULTRA LOW NOX BURNER, MFR: CLEAVER BROOKS, TYPE: FIRE TUBE, MODEL: CB 700, FUNC EQUIP: SUPPLY STEAM TO HEAT EVAPORATOR/PASTEURIZING SYS., FUEL_TYPE: , SCHEDULE: CONTINUOUS, H/D: 24, D/W: 7, W/Y: 52, NOTES: SOURCE TEST RESULTS: AVG. NOX (PPM | Nitrogen Oxides (NOx) | A | LOW NOX BURNER | 9 | PPMVD@3%O2 | 15 MIN AVG |  |  |  | 0.01 | LB/MMBTU | CALCULATED
OK-0041 | MCCLAIN ENERGY FACILITY | NRG MCCLAIN LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2000-01-19 | 2000 | POWER PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 22 | MMBTU/H | See RBLC ID OK-0071 for updated emission limits based on increased hours of operatuion. | Nitrogen Oxides (NOx) | P | COMBUSTION CONTROL | 0.035 | LB/MMBTU |  |  |  |  | 0.035 | LB/MMBTU
OK-0050 | ONETA GENERATING STA | CALPINE CORP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2000-01-21 | 2000 | ELECTRIC GENERATION PLANT | DUCT BURNERS (4) | 13.31 | NATURAL GAS | 328 | MMBTU/H | The emission limits indicted are for the duct burners only. Emission limits for the turbines associated with these duct burners are provided under the process Combustion Turbines | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.08 | LB/MMBTU |  |  |  |  | 0.08 | LB/MMBTU
CA-0941 | SANTA MONICA - UCLA MEDICAL CENTER | SANTA MONICA - UCLA MEDICAL CENTER | CA | SOUTH COAST AQMD, CA | 2000-01-28 | 2000 | BOILER USED TO PRODUCE HOT WATER AND STEAM | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 16.3 | MMBTU/H | CLEAVER BROOKS MODEL CE (LE) 200-400 FIRE-TUBE BOILER | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 15 | PPMVD | Corrected to 3% O2 |  |  |  | 0.018 | LB/MMBTU | Calculated using F-Factor | NOX 15 MIN @ 3% O2
TX-0309 | FORMOSA PLASTICS TEXAS | FORMOSA PLASTICS CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-02-10 | 2000 | THIS PERMIT AUTHORIZES THE OPERATION OF THE FORMOSA ETHYLENE GLYCOL PLANT & A PRODUCTION INCREASE, EQUIPMENT UPGRADES & CHANGES, ADDITIONAL FUGITIVE EMISSIONS, & AN ADDITIONAL COOLING TOWER CELL. THE APPLICANT WISHES TO CONSOLIDATE ALL FUGITIVE EMISSION P | WASTE HEAT BOILER, 70Z401 | 13.31 | NAT GAS |  |  | SHALL BE MAINTAINED AT A MINIMUM COMBUSTION CHAMBER TEMP OF 1450 F. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 166 | LB/H |  | 170 | T/YR |  | 0.13 | LB/MMBTU |  | ADDITIONAL EMISSION LIMITS: 150 PPM AT 24 H AV.
CA-0942 | SAN BERNARDINO COUNTY MEDICAL CENTER | SAN BERNARDINO COUNTY MEDICAL CENTER | CA | SOUTH COAST AQMD, CA | 2000-02-15 | 2000 | BOILER USED TO PRODUCE STEAM TO HEAT BUILDING. | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 6 | MMBTU/H | CLEAVER BROOKS MODEL FLX-700-600 | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 12 | PPMVD | Corrected to 3% O2 |  |  |  | 0.015 | LB/MMBTU | Calculated using F-Factor | NOX 15 MIN @ 3% O2
CA-0942 | SAN BERNARDINO COUNTY MEDICAL CENTER | SAN BERNARDINO COUNTY MEDICAL CENTER | CA | SOUTH COAST AQMD, CA | 2000-02-15 | 2000 | BOILER USED TO PRODUCE STEAM TO HEAT BUILDING. | BOILER, LPG | 13.31 | LPG | 6 | MMBTU/H | CLEAVER BROOKS MODEL FLX-700-600. LPG USED AS EMERGENCY FUEL | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 30 | PPMVD | Corrected to 3% O2 |  |  |  | 0.037 | LB/MMBTU | Calculated using F-Factor
PA-0165 | PROCTER & GAMBLE PAPER PRODUCTS COMPANY | PROCTER & GAMBLE PAPER PRODUCTS COMPANY | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2000-02-24 | 2000 | THIS LATEST MODIFICATION UPDATES CHANGES TO PLANT WHICH INCLUDES GENERATION OF ERCS FROM THE SHUT DOWN OF SOURCES AS APPROVED BY RACT PERMIT. | BOILERS, (3) | 13.31 | NATURAL GAS | 90 | MMBTU/H | INSTALLATION OF LOW NOX BURNERS TO 3 BOILERS | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.1 | LB/MMBTU |  |  |  |  | 0.1 | LB/MMBTU
AL-0142 | HONDA MANUFACTURING OF ALABAMA, LLC | HONDA | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2000-02-29 | 2000 |  | BOILERS, NATURAL GAS FIRED | 13.31 | NATURAL GAS | 10 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | NATURAL GAS FUEL ONLY, LOW NOX BURNERS | 0.35 | LB/H |  | 0.035 | LB/MMBTU |  | 0.035 | LB/MMBTU
CA-0944 | BUMBLE BEE SEAFOODS, INC. | BUMBLE BEE SEAFOODS, INC. | CA | SOUTH COAST AQMD, CA | 2000-03-10 | 2000 | BOILER PRODUCES STEAM FOR FACILITY | BOILER | 13.31 | NATURAL GAS | 16.3 | MMBTU/H | SUPERIOR MOHAWK MODEL 4X-2007-S150 FIRE TUBE BOILER | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 12 | PPMVD | Corrected to 3% O2 |  |  |  | 0.015 | LB/MMBTU | Calculated using F-Factor | NOX 15 MIN @ 3% O2
CA-0940 | NATION WIDE BOILER | NATION WIDE BOILER | CA | SOUTH COAST AQMD, CA | 2000-03-15 | 2000 | EMERGENCY RENTAL BOILER TO PRODUCE HOT WATER AND STEAM | BOILER, PORTABLE | 13.31 | NATURAL GAS | 28.8 | MMBTU/H |  | Nitrogen Oxides (NOx) | P |  | 9 | PPMVD | Corrected to 3% O2 |  |  |  | 0.011 | LB/MMBTU | Calculated using F-Factor | NOX 15 MIN @ 3% O2
CA-0947 | RRR REAL ESTATE | RRR REAL ESTATE | CA | SOUTH COAST AQMD, CA | 2000-03-15 | 2000 | BOILER USED TO PRODUCE HOT WATER AND HEAT | BOILER | 13.31 | NATURAL GAS | 7.5 | MMBTU/H | CLEAVER BROOKS CB-200 | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 12 | PPMVD | Corrected to 3% O2 |  |  |  | 0.015 | LB/MMBTU | Calculated using F-Factor | NOX 15 MIN @ 3% O2
CA-1005 | COLLEGE OF THE DESERT | COLLEGE OF THE DESERT | CA | SOUTH COAST AQMD, CA | 2000-03-16 | 2000 |  | BOILER, 5.05 MMBTU/H | 13.31 | NATURAL GAS | 5.05 | MMBTU/H | EQUIP MFR: TRANE, TYPE: DIRECT FIRED, MODEL: ABDA 0440, FUNC EQUIP: PROVIDE COOLING, SCHEDULE: CONTINUOUS | Nitrogen Oxides (NOx) | P | LOW NOX BURNER AND FLUE GAS RECIRCULATION | 20 | PPMV @ 3% O2 | 15 MIN AVG |  |  |  | 0.015 | LB/MMBTU | CALCULATED
CA-0945 | LIBERTY CONTAINER CO | LIBERTY CONTAINER CO, KEY CONTAINER | CA | SOUTH COAST AQMD, CA | 2000-03-17 | 2000 | MANUFACTURER OF CONTAINERS | BOILER | 13.31 | NATURAL GAS | 16.3 | MMBTU/H | CLEAVER BROOKS CB (LE) 700-400 | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNER | 12 | PPM @ 3% O2 | 15 MINUTE AVERAGE | 127 | LB/MO |  | 0.015 | LB/MMBTU | CALCULATED USING F-FACTOR | NOX 15 MIN @ 3% O2
AK-0053 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFI | CRUDE HEATER, CF-H-31003A | 13.31 | FUEL GAS | 65.6 | MMBTU/H | PERMIT INFORMATION LISTS FUEL TYPE AS FUEL GAS" BUT TECHNICAL DOCUMENTS INDICATE THAT FUEL IS NATURAL GAS. SCC AND PROCESS CODES WERE CHOSEN FOR NATURAL GAS." | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.08 | LB/MMBTU |  |  |  |  | 0.08 | LB/MMBTU
AK-0053 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFI | CRUDE HEATER, CF-H-31003B | 13.31 | FUEL GAS | 65.6 | MMBTU/H | PERMIT INFORMATION INDICATES FUEL TYPE IS FUEL GAS" BUT TECHNICAL INFORMATION INDICATES FUEL GAS IS NATURAL GAS. SCC AND PROCESS CODES WERE CHOSEN FOR NATURAL GAS. UNIT IS DESCRIBED AS BORN." | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.08 | LB/MMBTU |  |  |  |  | 0.08 | LB/MMBTU
TX-0274 | SOLAR GAS TURBINE COGEN. | AMERIPOL SYNPOL CORP. | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-04-03 | 2000 | AMERIPOL PROPOSES TO CONSTRUCT A COGENERATION FACILITY, TURBINE WITH DUCT BURNER FIRED HEAT RECOVERY STEAM GENERATOR (HRSG) AND AN AUXILLIARY BOILER. THE TURBINE IS A 4.4 MW (DESIGN CAPACITY AT ISO CONDITIONS, BASE LOAD) NATURAL GAS FIRED SOLAR TURBINE, M | AUXILIARY BOILER | 13.31 | NATURAL GAS | 54.01 | MMBTU/H | WILL BE OPERATED 175 H/YR ONLY DURING PERIODS OF CTG DOWNTIME. | Nitrogen Oxides (NOx) | N | NONE INDICATED | 5.4 | LB/H |  | 0.47 | T/YR |  | 0.1 | LB/MMBTU |  | EMISSIONS REGULATED UNDER PSD-TX-957 PERMIT AUTHORIZATION
CA-0943 | L & N UNIFORM SUPPLY CO INC. | L & N UNIFORM SUPPLY CO INC. | CA | SOUTH COAST AQMD, CA | 2000-04-06 | 2000 | BOILER USED TO GENERATE STEAM FOR LAUNDRY | BOILER | 13.31 | NATURAL GAS | 6.3 | MMBTU/H | SUPERIOR BOILER MODEL 5-ACT-625-150M. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 12 | PPMVD | Corrected to 3% O2 |  |  |  | 0.015 | LB/MMBTU | Calculated using F-Factor | NOX 15 MIN @ 3% O2
CA-1020 | MARGARETIS TEXTILE SERVICES/MTS INC. | MARGARETIS TEXTILE SERVICES/MTS INC. | CA | SOUTH COAST AQMD, CA | 2000-05-01 | 2000 |  | BOILER 4.2 MMBTU/H | 13.31 | NATURAL GAS | 4.2 | MMBTU/H | MFR: KEWANCE, TYPE: FIRE TUBE, MODEL: 100 HP, FUNC EQUIP: STEAM GENERATOR, FUEL_TYPE: , SCHEDULE: CONTINUOUS, H/D: 24, D/W: 7, W/Y: 52, NOTES: THE APPLICANT REQUESTED 2 PPM NOX BASED ON THE GUARANTEE OF THE CONTROL TECHNOLOGY MANUFACTURE. AT THIS TIME, 2 | Nitrogen Oxides (NOx) | A | SCONOX CATALYTIC ABSORPTION SYSTEM | 2 | PPMVD @ 3% O2 | 15-MIN AVG | [5 empty] | NOT AVAILABLE
CA-1060 | COLOR AMERICA TEXTILE PROCESSING, INC. | COLOR AMERICA TEXTILE PROCESSING, INC. | CA | SOUTH COAST AQMD, CA | 2000-05-01 | 2000 |  | DRYER OR OVEN, DIRECT OR INDIRECT | 13.31 | NATURAL GAS | 6 | MMBTU/H | EQUIP: , MFR: KRANTZ, TYPE: TENTER FRAME FABRIC DRYER, MODEL: K10, FUNC EQUIP: DRY COTTON AND COTTON BLEND FABRICS, FUEL_TYPE: , SCHEDULE: CONTINUOUS, H/D: 24, D/W: 7, W/Y: 52, NOTES: SOURCE TEST RESULTS: O2, % (DRY) 19.66 NOX, PPMVD 3.02 (43.6 PPMVD@3%O2 | Nitrogen Oxides (NOx) | A | LOW NOX BURNER | 60 | PPMVD @ 3 % O2 | [7 empty] | SOURCE TEST RESULTS: O2, % (DRY) 19.66 NOX, PPMVD 3.02 (43.6 PPMVD@3%O2) CO2, % (DRY) 0.463 CO, PPMVD 15.01 FLUE GAS FLOW RATE, DSCFM 8,138 AQMD'S MONITORING AND SOURCE TEST ENGINEERING GROUP APPROVED THIS SOURCE TEST AS SHOWING THE NOX TO BE LESS THAN 60
MI-0301 | ALCHEM ALUMINUM | ALCHEM ALUMINUM, INC. | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 2000-05-02 | 2000 | SECONDARY ALUMINUM PRODUCTION. | FLUES | 13.31 | NATURAL GAS | 42000 | LB/H | HOLDING CAPACITIES ARE 170,000 AND 250,000 LBS. BURNER CAPACITIES ARE 34,000,000 AND 48,000,000 BTU/HR. | Nitrogen Oxides (NOx) | N | FLUES CARRY PRODUCTS OF COMBUSTION WITHOUT ADD-ON CONTROLS. GAS CAPACITY 82MMBTU/H, TOTAL. | 1.18 | LB/H |  | 3.28 | T/YR |  |  | LB/MMBTU
MA-0027 | CABOT POWER CORPORATION | CABOT POWER CORPORATION | MA | MASSACHUSETTS DIV OF AIR QUAL CONTROL | 2000-05-07 | 2000 | COMBINED CYCLE ELECTRIC GENERATING FACILITY. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 26.6 | MMBTU/H | PROCESS RESTRICTED TO 500 HOURS PER YEAR (12,881,000 SCF NATURAL GAS) | Nitrogen Oxides (NOx) | B | SCR, DRY LOW NOX COMBUSTOR | 1.1 | LB/H |  |  |  |  | 0.04 | LB/MMBTU
LA-0146 | SHELL CHEMICAL COMPANY - GEISMAR PLANT | SHELL CHEMICAL COMPANY - GEISMAR PLANT | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2000-05-10 | 2000 | SHELL CHEMICAL PROPOSES TO INSTALL AN IDENTICAL SHOP 3 UNIT AND AN OLEFINS FEED PROCESSING UNIT (OFP). THE OFP UNIT WILL UTILIZE INTERNAL OLEFINS (C15/16) FROM SHOP 1, 2, AND 3. THIS UNIT WILL ALSO CONVERT THE INTERNAL OLEFINS INTO HIGH SOLUBILITY OLEFINS | C15/C16 COLUMN REBOILER FURNACE | 13.31 | NATURAL GAS | 20.75 | MMBTU/H (LHV) | EMISSION POINT 120-99 | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.83 | LB/H |  | 2.91 | T/YR |  | 0.04 | LB/MMBTU
TX-0430 | DIAMOND SHAMROCK MCKEE PLANT | DIAMOND SHAMROCK REFINING CO. | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-05-23 | 2000 | LOCATED AT 6701 FM 119, SUNRAY, TX | HEATERS, REFINERY | 13.3 | NATURAL GAS |  |  | MULTIPLE HEATERS, FIRING NATURAL GAS AND REFINERY FUEL GAS | Nitrogen Oxides (NOx) | N |  | 0.05 | LB/MMBTU |  |  |  |  | 0.05 | LB/MMBTU
CA-0946 | LACORR PACKAGING | LACORR PACKAGING | CA | SOUTH COAST AQMD, CA | 2000-07-12 | 2000 | PROVIDE STEAM FOR CARDBOARD MANUFACTURING | BOILER | 13.31 | NATURAL GAS | 21 | MMBTU/H | CLEAVER BROOKS MODEL CB-LE 500 BOILER | Nitrogen Oxides (NOx) | A | SELECTIVE CATALYTIC REDUCTION | 7 | PPMVD | Corrercted to 3% O2 |  |  |  | 0.009 | LB/MMBTU | Calculated using F-Factor | NOX 15 MIN @ 3% O2
CA-1100 | LACORR PACKAGING | LACORR PACKAGING | CA | SOUTH COAST AQMD, CA | 2000-07-12 | 2000 |  | BOILER: 5 TO < 33.5 MMBTU/HR | 13.31 | NATURAL GAS | 21 | MMBTU/H | EQUIP: , MFR: CLEAVER BROOKS, TYPE: FIRE-TUBE, MODEL: CB-LE 500, FUNC EQUIP: PROVIDE STEAM FOR CARDBOARD MANUFACTURING, FUEL_TYPE: , SCHEDULE: CONTINUOUS, H/D: 24, D/W: 5, W/Y: 52, NOTES: BACT NH3: 5 PPMD CORRECTED TO 3% O2, 15 CONSECUTIVE MINUTES SOURCE | Nitrogen Oxides (NOx) | A | SCR | 7 | PPMVD@3% O2 | 15MIN | [5 empty] | NOT AVAILABLE
WY-0056 | LA LAND & EXPLORATION CO. - LOST CABIN GAS PLANT | LOUISIANA LAND & EXPLORATION CO. - LOST CABIN GAS | WY | WYOMING AIR QUAL DIV, DEPT OF ENV QUAL | 2000-07-25 | 2000 | NATURAL GAS TREATMENT - SOUR GAS SWEETENING (H2S REMOVAL) | BOILER (AUXILLARY), TRAIN III | 13.31 | NATURAL GAS | 76.7 | MMBTU/H | ONLY USED FOR START UP / SHUT DOWN, IDLES OTHERWISE, EMISSIONS BASED ON AN-42 EMISSION FACTORS (EXCEPT FOR NOX), ASSUMING 15% LOAD 7884 H/YR AND 100% LOAD 876 H/YR. LIMITS FOR NOX AND CO ONLY. | Nitrogen Oxides (NOx) | P | LOW NOX BURNER | 9.5 | T/YR |  | 9.2 | LB/HR |  | 0.12 | LB/MMBTU
WI-0181 | CHARTER STEEL | CHARTER STEEL | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2000-08-02 | 2000 | STEEL MILL | BOILER | 13.31 | NATURAL GAS | 10 | MMBTU/H | THIS BOILER IS SUBJECT TO NSPS | Nitrogen Oxides (NOx) | P | NATURAL GAS FUEL, LOW -NOX BURNER(LNB`S) AND FLU GAS RECIRCULATION (FGR). | 30 | PPMVD AT 3% OXYGEN |  | 0.035 | LB/MMBTU |  | 0.035 | LB/MMBTU
WI-0181 | CHARTER STEEL | CHARTER STEEL | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2000-08-02 | 2000 | STEEL MILL | SPACE HEATERS | 13.31 |  | 5 | MMBTU/H | SPACE HEATERS' THROUGHPUT IS NO MORE THAN 5 MMBTU/H EACH. | Nitrogen Oxides (NOx) | P | BACT FOR NOX IS DETERMINED TO BE GOOD COMBUSTION CONTROL AND THE USE OF NATURAL GAS TO FUEL THE SPACE HEATERS AND SIMILAR COMBUSTION APPLIANCES | 0.12 | LB/MMBTU |  |  |  |  | 0.12 | LB/MMBTU
CA-1061 | NELCO PRODUCTS. INC, | NELCO PRODUCTS. INC, | CA | SOUTH COAST AQMD, CA | 2000-08-04 | 2000 |  | HEATER: REFINERY PROCESS, FORCED DRAFT < 50 MMBTU/HR | 13.31 | NATURAL GAS | 19 | MMBTU/H | EQUIP: , MFR: AMERICAN HYDROTHERM, TYPE: FORCED CIRCULATION, MODEL: 1200-4D-90, FUNC EQUIP: HEATS RECIRCULATING OIL USED IN LAMINATING PRESSES, FUEL_TYPE: , SCHEDULE: VARIABLE, H/D: 24, D/W: 7, W/Y: 52, NOTES: THE APPLICANT PROPOSED TO USE THE ALZETA ULNB | Nitrogen Oxides (NOx) | A | ULTRA-LOW NOX BURNER-ALZETA CORP. | 12 | PPMVD 3% O2 | [7 empty] | THE APPLICANT PROPOSED TO USE THE ALZETA ULNB. ALTHOUGH THE MODEL CBS BURNER HAS NOT BEEN DEMONSTRATED IN A PROCESS HEATER, IT HAS BEEN SUCCESSFULLY DEMONSTRATED IN A VARIETY OF WATER-TUBE AND FIRED-TUBE BOILERS. WHILE THIS APPLICATION HAS NOT YET BEEN SO
AL-0217 | BIRMINGHAM SLAG | HOLCIM, INC. | AL | JEFFERSON COUNTY DEPT OF HEALTH, AL | 2000-11-02 | 2000 | THE PLANT PRODUCES GRANCEM, A SPECIAL CEMENT MANUFACTURED FROM GROUND GRANULATED BLAST FURNACE SLAG, A BYPRODUCT OF THE STEEL-MAKING PROCESS. | NATURAL GAS FIRED FLASH DRYER | 13.31 | NATURAL GAS | 80 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 8 | LB/H |  |  |  |  | 0.1 | LB/MMBTU
TX-0363 | SAINT-GOBAIN VETROTEX AMERICA | VETROTEX AMERICA | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-11-13 | 2000 | VETROTEX AMERICA (VETROTEX) OPERATES A FIBER GLASS MANUFACTURING PLANT. THE VETROTEX PLANT PRODUCES FIBERGLASS REINFORCEMENT PRODUCTS AND IS COMPRISED OF FIVE GLASS MANUFACTURING FURNACES AND ASSOCIATED EQUIPMENT. THESE REFINFORCEMENT PRODUCTS ARE USED IN | BOILER NO 3 | 13.31 | NAT GAS |  |  |  | Nitrogen Oxides (NOx) | N | NONE INDICATED | 2.29 | LB/H |  | 10.01 | T/YR |  |  |  | NOT AVAILABLE
SC-0065 | BROAD RIVER INVESTORS - GAFFNEY | BROAD RIVER INVESTORS, LLC | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 2000-12-21 | 2000 | ELECTRIC GENERATION FACILITY | HOT WATER HEATERS, NAT. GAS (2) | 13.31 | NATURAL GAS | 11 | MMBTU/H (EACH) |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 1.72 | LB/H | EACH |  |  |  | 0.15636 | LB/MMBTU
AR-0040 | DUKE ENERGY HOT SPRINGS | DUKE ENERGY HOT SPRINGS | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2000-12-29 | 2000 | NATURAL GAS FIRED POWER PLANT | BOILERS, AUXILIARY 2 | 13.31 | NATURAL GAS | 44.1 | MMBTU/H | THROUGHPUT FOR EACH | Nitrogen Oxides (NOx) | P | LOW NOX COMBUSTER & PROPER OPERATION. LB/HR LIMIT FOR EACH BOILER. | 0.12 | LB/MMBTU |  | 5.3 | LB/H |  | 0.12 | LB/MMBTU
NM-0042 | DEMING ENERGY FACILITY | DUKE ENERGY LUNA | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2000-12-29 | 2000 | THIS FACILITY WILL GENERATE APPROXIMATELY 640 MW (NOMINAL). IT WILL BE A COMBINED CYCLE FACILITY CONSISTING OF 2 GENERAL ELECTRIC PG7241 (FA) COMBUSTION TURBINES, 2 DUCT BURNERS, AN AUXILIARY BOILER, AND A COOLING TOWER. THE NOX FROM THE COMBUSTION TURBIN | AUX-1 AUXILARY BOILER | 13.31 | NATURAL GAS | 44.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | B | DRY LOW NOX BURNERS, NATURAL GAS COMBUSTION, AND GOOD ENGINEERING PRACTICE. | 1.5 | LB/H |  |  |  |  | 0.03 | LB/MMBTU | CALCULATED
AL-0178 | ANNISTON ARMY DEPOT | US ARMY - Anniston Army Depot | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-01-05 | 2001 | CHEMICAL WEAPONS INCINERATOR | TWO (2) 13.4 MMBTU/H BOILERS | 13.31 | NATURAL GAS | 13.4 | MMBTU/H | LP Backup | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.036 | LB/MMBTU |  | 0.75 | LB/H |  | 0.036 | LB/MMBTU
AL-0178 | ANNISTON ARMY DEPOT | US ARMY - Anniston Army Depot | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-01-05 | 2001 | CHEMICAL WEAPONS INCINERATOR | TWO (2) 11.7 MMBTU/H BOILERS | 13.31 | NATURAL GAS | 11.7 | MMBTU/H | LP Backup | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.036 | LB/MMBTU |  | 0.53 | LB/H |  | 0.036 | LB/MMBTU
AL-0168 | GENPOWER KELLEY LLC | GENPOWER KELLEY LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-01-12 | 2001 | ELECTRIC GENERATION | BOILER | 13.31 | NATURAL GAS | 83 | MMBTU/H | BOILER OPERATION LIMITED TO 1000 HR/YR | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.05 | LB/MMBTU |  | 4.18 | LB/H |  | 0.05 | LB/MMBTU
IN-0090 | NUCOR STEEL | NUCOR STEEL | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-01-19 | 2001 |  | LADLE PREHEATERS | 13.31 | NATURAL GAS | 15 | MMBTU/HR EACH | TUNDISH PREHEATERS 6 MMBTU/H EACH, TUNDISH NOZZLE PREHEATERS 1 MMBTU/H EACH, TUNDISH DRYERS 9 MMBTU/H, TRANSITION PIECE PREHEATERS 15 MMBTU/H | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.1 | LB/MMBTU |  |  |  |  | 0.1 | LB/MMBTU
IN-0090 | NUCOR STEEL | NUCOR STEEL | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-01-19 | 2001 |  | TUNDISH PREHEATERS (2) | 13.31 |  | 6 | MMBTU/H | THROUGHPUT FOR EACH | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS, BTU LIMIT | 0.15 | LB/MMBTU |  |  |  |  | 0.15 | LB/MMBTU
CA-1108 | INTERNATIONAL EXTRUSION CORPORATION | INTERNATIONAL EXTRUSION CORPORATION | CA | SOUTH COAST AQMD, CA | 2001-01-22 | 2001 |  | METAL HEATING FURNACE | 13.31 | NATURAL GAS | 8.8 | MMBTU/H, BATCH SIZE IS APPROX. 40 TONS | EQUIP: RECEIVES MOLTEN ALUMINUM FROM MELTING FURNACE, MFR: THORPE INDUSTRIAL FURNACE, FUNC EQUIP: ALLOYS AND NITROGEN GASSES MOLTEN ALUMIMUM, FUEL_TYPE: NATURAL GAS, SCHEDULE: CONTINUOUS, H/D: 24, D/W: 5, W/Y: 50, NOTES: THIS IS A RECLAIM FACILITY. THE FA | Nitrogen Oxides (NOx) | A | LOW-NOX BURNER | 40 | PPMVD @ 3% O2 | [7 empty] | THIS IS A RECLAIM FACILITY. THE FACILITY REQUESTED A PERMIT MODIFICATION TO APPLY A RECLAIM CONCENTRATION LIMIT OF 40 PPMVD (CORRECTED TO 3% O2) TO THIS FURNACE. THIS LOW-NOX BURNER IS CONSIDERED ACHIEVED IN PRACTICE. ALTHOUGH THIS BURNER IS CAPABLE OF ME
AL-0169 | BLOUNT MEGAWATT FACILITY | BLOUNT COUNTY ENERGY LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-02-05 | 2001 | ELECTRIC GENERATING FACILITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 40 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.08 | LB/MMBTU |  | 3.2 | LB/H |  | 0.08 | LB/MMBTU
OH-0258 | PRO TEC COATING COMPANY | USS GALVANIZING, INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-02-15 | 2001 | STEEL FINISHING MILL: METAL COATING WITH 2 NON-INSIGNIFICANT ANNEALING FURNACES AND 4 BOILERS | BOILERS (4) | 13.31 | NATURAL GAS | 20.9 | MMBTU/H | This permit is a modification to only 2 of the 4 boilers at this facility. Permit limits the same for each of the boilers being modified. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS. | 0.69 | LB/H |  | 3.02 | T/YR |  | 0.033 | LB/MMBTU |  | Limits are for each boiler. Only 2 of the 4 boilers modified in this permit.
OH-0255 | PSEG WATERFORD ENERGY LLC | PSEG WATERFORD ENERGY LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-03-29 | 2001 | THREE 170 MW NATURAL GAS-FIRED COMBUSTION TURBINES; STAGE I SIMPLE CYCLE TO STAGE II COMBINED CYCLE | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 85.2 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 3.07 | LB/H |  | 13.4 | T/YR |  | 0.036 | LB/MMBTU
MS-0045 | NISSAN NORTH AMERICA, INC. | NISSAN NORTH AMERICA, INC. | MS | MISSISSIPPI DEPT OF ENV QUALITY | 2001-04-02 | 2001 | AUTOMOBILE MANUFACTURING FACILITY | BOILER | 13.31 | NATURAL GAS | 35 | MMBTU | For this process, only NOx has an emission rate limit set in this permit. BACT for other pollutants: PM, SO2, CO, and VOC is the use of natural gas as fuel. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.12 | LB/MMBTU |  |  |  |  | 0.12 | LB/MMBTU
OK-0074 | KIAMICHI ENERGY FACILITY | KIOWA POWER PARTNERS LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-05-01 | 2001 | ENERGY PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 27.5 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.1 | LB/MMBTU |  |  |  |  | 0.1 | LB/MMBTU
IN-0086 | MIRANT SUGAR CREEK, LLC | MIRANT SUGAR CREEK, LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-05-09 | 2001 |  | AUXILARY BOILER, NATURAL GAS (2) | 13.31 | NATURAL GAS | 35 | MMBTU/H | AUXILARY BOILERS ARE LIMITED TO 5,000 H/YR OF OPERATION. THROUGH PUT IS FOR EACH BOILER. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS. GOOD COMBUSTION. NATURAL GAS. LB/H LIMIT IS FOR EACH BOILER. | 0.049 | LB/MMBTU |  | 1.72 | LB/H |  | 0.049 | LB/MMBTU
OK-0046 | THUNDERBIRD POWER PLT | THUNDERBIRD GENERATION LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-05-17 | 2001 | ELECTRICAL PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 20 | MMBTU/H | CO limits are not provided in permit. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.049 | LB/MMBTU |  |  |  |  | 0.049 | LB/MMBTU
NV-0039 | CHUCK LENZIE GENERATING STATION | NEVADA POWER COMPANY | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2001-06-01 | 2001 | A NEW ELECTRIC POWER PLANT CONSISTING OF FOUR COMBUSTION TURBINE GENERATORS, FOUR HEAT RECOVERY STEAM GENERATORS EACH WITH DUCT FIRING, AND TWO STEAM TURBINE GENERATORS FOR A TOTAL NOMINAL OUTPUT OF 1170 MW. THE FACILITY IS LOCATED AT 11405 U.S. HIGHWAY 9 | AUXILIARY BOILERS | 13.31 | NATURAL GAS | 44.1 | MMBTU/H | THESE (TWO) BOILERS WILL EACH BE OPERATED A MAXIMUM OF 6,000 HOURS PER YEAR ACCORDING TO THE APPLICATION FOR ATC. | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION CONTROL | 30 | PPMVD@3% O2 | ONE-HOUR AVERAGE | 5.2 | LB/H |  | 0.118 | LB/MMBTU |  | EMISSION LIMIT 1 IS AN EMISSION STANDARD PER SECTION 49 OF THE AIR QUALITY REGULATIONS. EMISSION LIMIT 2 APPLIES TO EACH AUXILIARY BOILER.
IN-0087 | DUKE ENERGY, VIGO LLC | DUKE ENERGY, VIGO LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-06-06 | 2001 |  | AUXILARY BOILER, NATURAL GAS (2) | 13.31 | NATURAL GAS | 46 | MMBTU/H | NATURAL GAS FIRED BOILERS (THROUGHPUT FOR EACH) LIMITED TO 500 H/YR OPERATION | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION. LOW NOX BURNERS. LIMIT IS FOR EACH BOILER. | 0.049 | LB/MMBTU |  | 2.28 | LB/H |  | 0.049 | LB/MMBTU
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-5302A AND H-5302B | 13.31 | NATURAL GAS | 35 | MMBTU/H EA | 35 MMBTU/H MAXIMUM RATE/CAPACITY EA, 30 MMBTU/H NOMINAL CAPACITY EA. | Nitrogen Oxides (NOx) | P | LIMIT EXTENDED FROM PREVIOUS PERMIT TO AVOID PSD REVIEW. | 0.05 | LB/MMBTU | EACH |  |  |  | 0.05 | LB/MMBTU | EACH
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-4510A AND H-4510B | 13.31 | NAT GAS | 14.4 | MMBTU/H EACH |  | Nitrogen Oxides (NOx) | N | LIMIT EXTENDED FROM PREVIOUS PERMIT TO AVOID PSD REVIEW. | 0.08 | LB/MMBTU | EACH |  |  |  | 0.08 | LB/MMBTU | EACH
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-5701A AND H-5701B | 13.31 | NAT GAS | 29 | MMBTU/H EACH | 29 MMBTU/H MAXIMUM RATE/CAPACITY EA, 22.7 MMBTU/H NOMINAL CAPACITY EA. HEATERS BURN BOTH NATURAL GAS AND DIESEL FUELS. OPERATING RESTRICTION OF NO MORE THAN 200 H DURING ANY 12 CONSECUTIVE MOS, COMBINED, WHILE FIRING FUEL OIL. OPERATING RESTRICTION OF COM | Nitrogen Oxides (NOx) | N | BACT LIMIT EXTENDED FROM PREVIOUS PERMIT TO AVOID PSD REVIEW. | 11.3 | LB/H | EA, BASED ON HHV, FIRING FUEL OIL |  |  |  | 0.08 | LB/MMBTU | EA, FIRING NAT GAS
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-2001A AND H-2001B | 13.31 | NAT GAS | 17.5 | MMBTU/H EACH | 17.5 MMBTU/H MAXIMUM RATE/CAPACITY EA, 13.1 MMBTU/H NOMINAL CAPACITY EA. | Nitrogen Oxides (NOx) | P | BACT LIMIT EXTENDED FROM PREVIOUS PERMIT TO AVOID PSD REVIEW. DO NOT OPERATE HEATERS ON FUEL OIL AT ANY TIME. REPLACE BOTH HEATERS WITH LOW NOX BURNERS NO LATER THAN 180 D AFTER PERMIT ISSUANCE. | 0.08 | LB/MMBTU | AT ANY TIME |  |  |  | 0.08 | LB/MMBTU | AT ANY TIME
AL-0190 | GE PLASTICS | GE PLASTICS | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-07-13 | 2001 | SYNTHETIC ORGANIC CHEMICAL MANUFACTURER THAT PRODUCES POLYCARBONATE RESIN PELLETS | FURNACE, HOT OIL, 10 MMBTU/H | 13.31 | NATURAL GAS | 10 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICES | 0.5 | LB/H |  | 0.05 | LB/MMBTU |  | 0.05 | LB/MMBTU
AL-0190 | GE PLASTICS | GE PLASTICS | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-07-13 | 2001 | SYNTHETIC ORGANIC CHEMICAL MANUFACTURER THAT PRODUCES POLYCARBONATE RESIN PELLETS | FURNACE, HOT OIL, 20 MMBTU/H | 13.31 | NATURAL GAS | 20 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICES | 1.2 | LB/H |  | 0.06 | LB/MMBTU |  | 0.06 | LB/MMBTU
OH-0263 | FREMONT ENERGY CENTER, LLC | CALPINE CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-08-09 | 2001 | TWO 180 MW COMBINED CYCLE TURBINES (2 HRSGS),USING SELECTIVE CATALYTIC REDUCTION (SCR) AND OXIDATION CATALYST | AUXILIARY BOILER | 13.31 | NATURAL GAS | 80 | MMBTU/H | Auxiliary boiler, natural gas-fired, 80 mmBtu/hr | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 2.72 | LB/H |  | 11.9 | T/YR |  | 0.034 | LB/MMBTU | Calculated
OK-0044 | SMITH POCOLA ENERGY PROJECT | SMITH COGENERATION OK INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-16 | 2001 | ELEC. POWER GENERATION | AUXILIARY BOILERS, (2) | 13.31 | NATURAL GAS | 48 | MMBTU/H | THROUGHPUT FOR EACH | Nitrogen Oxides (NOx) | P | DRY LOW NOX BURNERS, OPERATES IN PRE-MIX MODE. | 9.41 | LB/H | combined | 41.22 | T/YR | combined | 0.1 | LB/MMBTU
OK-0054 | QUAD GRAPHICS OKC FACILITY | QUAD GRAPHICS INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-21 | 2001 | PRINT SHOP | BOILERS | 13.31 | NATURAL GAS | 62.77 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.035 | LB/MMBTU |  | 2.48 | LB/H | See Pollutant Notes | 0.035 | LB/MMBTU |  | Emission limit 2 is the maximum emission rate per heater / oxidizer combination. In addition, an annual emission limit of 5.23 T/YR applies to the same combination.
OK-0054 | QUAD GRAPHICS OKC FACILITY | QUAD GRAPHICS INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-21 | 2001 | PRINT SHOP | HEATERS/OXIDIZERS | 13.31 | NATURAL GAS | 16 | MMBTU/H | THESE UNITS INCLUDE HEATERS FOR INK DRYING AND OXIDIZERS ASSOCIATED WITH CONTROLLING EMISSIONS. EMISSION LIMITS ARE FOR PRODUCTS OF COMBUSTION. | Nitrogen Oxides (NOx) | P | FUEL LIMITS AND MAINTENANCE PER MANUFACTURERS SPECS | 2.48 | LB/H | See Pollutant Notes | 5.23 | T/YR | See Pollutant Noes | 0.155 | LB/MMBTU | Not Available | Limits are for heater / oxidizer combination.
WV-0013 | MARTINSBURG PLANT | Quad/Graphics, Inc. | WV | WEST VIRGINIA AIR POLLUTION CONTROL COMM | 2001-08-30 | 2001 | COMPANY OPERATES A PRINTING AND PUBLISHING FACILITY IN MARTINSBURG, WV. THE FACILITY IS LOCATED IN THE CUMBO YARD INDUSTRIAL PARK ADJACENT TO I-81 AND IS NORTH OF DOWNTOWN MARTINSBURG. THE PLANT PRINTS CATALOGS, MAGAZINES, AND INSERTS FOR PERIODICALS. IT | BOILERS, 3 | 13.31 | NATURAL GAS | 65.78 | MMBTU/H | THREE IDENTICAL BOILERS W/MAX. DEVICE HEAT INPUT( MDHI) OF 65.78 MMBTU/HR W/ PROPANE BACK-UP. FOR THIS PROCESS, ONLY NOX IS SUBJECT TO PSD. | Nitrogen Oxides (NOx) | B | LOW-NOX BURNERS AND FLUE-GAS RECIRCULATION | 0.035 | LB/MMBTU |  |  |  |  | 0.035 | LB/MMBTU
WV-0013 | MARTINSBURG PLANT | Quad/Graphics, Inc. | WV | WEST VIRGINIA AIR POLLUTION CONTROL COMM | 2001-08-30 | 2001 | COMPANY OPERATES A PRINTING AND PUBLISHING FACILITY IN MARTINSBURG, WV. THE FACILITY IS LOCATED IN THE CUMBO YARD INDUSTRIAL PARK ADJACENT TO I-81 AND IS NORTH OF DOWNTOWN MARTINSBURG. THE PLANT PRINTS CATALOGS, MAGAZINES, AND INSERTS FOR PERIODICALS. IT | BOILER | 13.31 | NATURAL GAS | 54.4 | MMBTU/H | PROPANE BACK-UP. FOR THIS PROCESS, ONLY NOX IS SUBJECT TO PSD. | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS AND FLUE-GAS RECIRCULATION | 0.035 | LB/MMBTU |  |  |  |  | 0.035 | LB/MMBTU
CA-1099 | COSMETIC LABORATORIES | COSMETIC LABORATORIES | CA | SOUTH COAST AQMD, CA | 2001-09-04 | 2001 |  | BOILER: 5 TO < 33.5 MMBTU/HR | 13.31 | NATURAL GAS | 21.46 | MMBTU/H | EQUIP: , MFR: CLAYTON INDUSTRIES, TYPE: WATER-TUBE, MODEL: EG504-1-FMB, FUNC EQUIP: PROCESS STEAM FOR MANUFACTURING PROCESSES, FUEL_TYPE: , SCHEDULE: CONTINUOUS, H/D: 24, D/W: 5, W/Y: 52, NOTES: AQMD UNANNOUNCED EMISSIONS TEST 6/28/2002 USING PORTABLE ANA | Nitrogen Oxides (NOx) | A | ULTRA LOW-NOX BURNER | 9 | PPMD @ 3% O2 | 15-MIN | [5 empty] | NOT AVAILABLE
CA-0903 | DISNEYLAND RESORT | DISNEYLAND RESORT | CA | SOUTH COAST AQMD, CA | 2001-09-27 | 2001 |  | BOILER, CLEAVER BROOKS WATER-TUBE | 13.31 | NATURAL GAS | 8.5 | MMBTU/H | ARB RECORD # A310-946-00; AUTHORITY TO CONSTRUCT # 360389 (12/21/99) CLEAVER BROOKS MODEL FLX WATER-TUBE BOILER USED TO SUPPLY HOT WATER. BACT DETERMINATION FOR NOX AND CO ONLY, THIS PROCESS DOES NOT HAVE EMISSION LIMITS SET FOR SOX, VOC, OR PM. | Nitrogen Oxides (NOx) | P | ALZETA ULTRA LOW-NOX BURNER, GOOD COMBUSTION | 12 | PPMVD @ 3% O2 |  |  |  |  | 0.015 | LB/MMBTU
MD-0033 | KELSON RIDGE | FREE STATE ELECTRIC, LLC | MD | MARYLAND, OTHER | 2001-09-27 | 2001 | FACILITY WAS LICENSED; PROJECT WAS THEN CANCELLED BY APPLICANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 40 | MMBTU/H | EMISSIONS LIMITS APPLY TO EACH BOILER | Nitrogen Oxides (NOx) | B | EXCLUSIVE USE OF NATURAL GAS, ADVANCED DRY LOW-NOX BURNERS; GOOD COMBUSTION CONTROLS HEAT INPUT TO THE AUXILIARY BOILERS (2) SHALL BE LIMITED TO 210,240 MMBTU FOR ANY CONSECUTIVE 12-MONTH PERIOD |  |  | SEE NOTE | [6 empty] | HEAT INPUT TO THE AUXILIARY BOILERS (2) SHALL BE LIMITED TO 210,240 MMBTU FOR ANY CONSECUTIVE 12-MONTH PERIOD
AL-0179 | TENASKA TALLADEGA GENERATING STATION | TENASKA ALABAMA IV PARTNERS, LP | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-10-03 | 2001 | NATURAL GAS/DISTILLATE OIL FIRED COMBINED CYCLE ELECTRIC GENERATING FACILITY. | 30 MMBTU/HR AUXILIARY BOILER | 13.31 | NATURAL GAS | 30 | MMBTU/H | Operation limited to 1000 h/yr. | Nitrogen Oxides (NOx) | P | LOW NOX COMBUSTION | 0.096 | LB/MMBTU |  | 2.9 | LB/H |  | 0.096 | LB/MMBTU
IN-0110 | COGENTRIX LAWRENCE CO., LLC | COGENTRIX LAWRENCE CO., LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-10-05 | 2001 | POWER PLANT | BOILER, AUXILIARY, NATURAL GAS | 13.31 | NATURAL GAS | 35 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | CLEAN FUEL, LOW NOX BURNERS | 0.08 | LB/MMBTU |  | 2.8 | LB/H |  | 0.08 | LB/MMBTU
OH-0265 | DRESDEN ENERGY LLC | Dresden Energy | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-10-16 | 2001 | TWO 171.7 MW NATURAL GAS AND FUEL OIL- FIRED COMBUSTION TURBINES, COMBINED CYCLE; 49 MMBTU/HR NATURAL GAS FIRED BOILER; 2,250,000 GALLON FIXED ROOF STORAGE TANK FOR #2 FUEL OIL. | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 49 | MMBTU/H | Boiler is restricted to 800 hour of operation per a rolling 12 months. | Nitrogen Oxides (NOx) | N |  | 4.9 | LB/H |  | 1.96 | T/YR |  | 0.1 | LB/MMBTU |  | Boiler is restricted to 800 hours or operation per a rolling 12 months.
OK-0043 | WEBERS FALLS ENERGY FACILITY | ENERGETIX | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-10-22 | 2001 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 30 | MMBTU/H | BOILER OPERATIONS LIMITED TO 3,000 HOURS/YEAR. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.05 | LB/MMBTU |  |  |  |  | 0.05 | LB/MMBTU
AL-0181 | DUKE ENERGY AUTAUGA, LLC | DUKE ENERGY AUTAUGA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-10-23 | 2001 | COMBINED CYCLE ELECTRIC GENERATING PLANT. | 31.4 MMBTU/HR NATURAL GAS FIRED BOILER | 13.31 | NATURAL GAS | 31.4 | MMBTU/H | Operation limited to 2500 hrs/yr. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.108 | LB/MMBTU |  | 3.77 | LB/H
*WA-0292 | SATSOP COMBUSTION TURBINE PROJECT | GRAYS HARBOR ENERGY LLC | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2001-10-23 | 2001 | GE F7 TURBINE BASED COMBINED CYCLE NATURAL GAS ONLY FUELED COMBUSTION TURBINE INCLUDES COOLING TOWER AND EMERGENCY ICE GENERATOR AND FIRE WATER ENGINES | AUXILIARY BOILER | 13.31 | NAT GAS | 29.3 | MMBTU/H | 29.3 MMBTU/H IS THE DESIGN HEAT INPUT RATE FOR THE BOILER, AS PROVIDED BY THE STATE CONTACT PERSON. | Nitrogen Oxides (NOx) | P | FGR AND LOW-NOX BURNERS | 1.03 | LB/H | 1-HR | 30 | PPM @ 3% O2 | 1-HR |  |  | NOT AVAILABLE
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | 2001 | ELECTRICITY GENERATION | FUEL GAS HEATER | 13.31 | NATURAL GAS | 16 | MMBTU/H | FUEL GAS HEATER PRE-HEATS THE PIPELINE NATURAL GAS FUEL ENTERING THE COMBUSTION TURBINE UNITS AT 70 DEGREES F | Nitrogen Oxides (NOx) | N | NONE- CONCLUDED THAT FUEL GAS HEATER HAS FAR LOWER HEAT INPUT RATE AND SUCH NOX CONTROLS ARE NOT PROBABLE BASED ON COST-EFFECTIVENESS | 0.12 | LB/MMBTU |  | 1.197 | LB/H |  | 0.12 | LB/MMBTU
OK-0071 | MCCLAIN ENERGY FACILITY | NRG MCCLAIN LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-10-25 | 2001 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | NATURAL GAS FUEL AND GOOD COMBUSTION CONTROL | 0.036 | LB/MMBTU |  |  |  |  | 0.036 | LB/MMBTU
CA-1101 | ARAMARK UNIFORM SERVICES | ARAMARK UNIFORM SERVICES | CA | SOUTH COAST AQMD, CA | 2001-10-27 | 2001 |  | DRYER OR OVEN, DIRECT OR INDIRECT | 13.31 | NATURAL GAS | 3.5 | MMBTU/H, AVERAGE LOAD EQUALS 1.5 MMBTU/H | EQUIP: , MFR: AMERICAN LAUNDRY, TYPE: TUMBLER, MODEL: 438, FUNC EQUIP: CLOTHES DRYER, FUEL_TYPE: , SCHEDULE: CONTINUOUS, H/D: 14, D/W: 5, W/Y: 52, NOTES: SOURCE TEST RESULTS: | Nitrogen Oxides (NOx) | A | LOW NOX BURNER | 30 | PPM@3% O2 | [6 empty] | NOT AVAILABLE
PR-0007 | COGENERATION PLANT (AES-PRCP) | AES PUERTO RICO | PR | PUERTO RICO ENV QUALITY BOARD, AIR PROGRAM | 2001-10-29 | 2001 | COGENERATION UNIT | LIMESTONE DRYER | 13.31 | PROPANE | 13 | MMBTU/H | LIMESTONE DRYER INCLUDES A CRUSHER. HEATED AIR BOTH CLASSIFIES THE GROUND LIMESTONE AND DRIES THE MATERIAL. UNIT IS LIMITED TO A 505 CAPACITY FACTOR CALCULATED BASED ON 4380 H/CALENDAR YR. COMBUSTION CONTROLS WILL BE USED TO MINIMIZE AIR EMISSIONS. | Nitrogen Oxides (NOx) | P | COMBUSTION CONTROLS | 1.95 | LB/H |  |  |  |  | 0.15 | LB/MMBTU
CA-1109 | SUPERIOR INDUSTRIES INTERNATIONAL | SUPERIOR INDUSTRIES INTERNATIONAL | CA | SOUTH COAST AQMD, CA | 2001-10-30 | 2001 |  | METAL HEATING FURNACE | 13.31 | NATURAL GAS | 12.6 | MMBTU/H | EQUIP: NO AIR PREHEAT, MFR: THERMAL PROCESS, TYPE: REVERBERATORY, FUNC EQUIP: ALUMINUM MELTING, FUEL_TYPE: PROPANE, SCHEDULE: CONTINUOUS, H/D: 24, D/W: 7, W/Y: 50 NOTES: THIS IS A RECLAIM FACILITY. THE FACILITY REQUESTED PERMIT MODIFICATIONS FOR FOUR ALUM | Nitrogen Oxides (NOx) | A | NEW FURNACES | 43 | PPMVD @ 3% O2 | [6 empty] | NOT AVAILABLE
TX-0378 | LA PORTE POLYPROPYLENE PLANT | ATOFINA PETROCHEMICALS INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-11-05 | 2001 | ATOFINA PROPOSES TO INSTALL A 60 MMBTU/H PACKAGE BOILER TO PROVIDE NEEDED STEAM CAPACITY. THE BURNER WILL MEET ESAD LIMIT OF 0.015 LB NOX/MMBTU FOR HOUSTON/GALVESTON. UPON STARTUP OF EPN ES-206, THE 40 MMBTU/H TEMPORARY BOILER (EPN TEMPBOILER) SHALL BE RE | PACKAGE BOILER BO-4 | 13.31 | NAT GAS | 60 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW-NOX BURNERS | 0.9 | LB/H |  | 3.94 | T/YR |  | 0.015 | LB/MMBTU
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | 2001 | SOYBEAN EXTRACTION PLANT | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. There is a separate process entry for this boiler when firing fuel oil. | Nitrogen Oxides (NOx) | P | USE OF LOW-NOX BURNERS. | 3.21 | LB/H |  | 22.7 | T/YR |  | 0.0352 | LB/MMBTU |  | EMISSION LIMITS BASED ON MANUFACTER'S TEST DATA. Additional limit: 9.6 ppm @ 15% O2 as 6-monute average.
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | 2001 | SOYBEAN EXTRACTION PLANT | DRYER, SOY PROTEIN CONCENTRATE - COMBUSTION | 13.31 | NATURAL GAS | 37 | MMBTU/H | Baghouse with 100% capture. Process is in 2 parts - dryer - combustion, and dryer - pm. | Nitrogen Oxides (NOx) | N |  | 1.88 | LB/H |  | 8.23 | T/YR |  | 0.053 | LB/MMBTU |  | Emissions from natural gas combustion, using 0.053 lb NOx/mmBtu
CA-1103 | NEWELLRUBBERMAID | NEWELLRUBBERMAID | CA | SOUTH COAST AQMD, CA | 2001-12-07 | 2001 |  | DRYER OR OVEN, DIRECT OR INDIRECT | 13.31 | NATURAL GAS | 5.4 | MMBTU/H | MFR: FERRY INDUSTRIES, MODEL: RS4-280, FUNC EQUIP: POLYETHYLENE RESIN MELTING AND CURING, SCHEDULE: CONTINUOUS, H/D: 24, D/W: 6, W/Y: 52, NOTES: THIS FACILITY REQUESTED 18 PPM LIMITS ON OVENS AS RECLAIM CONCENTRATION LIMITS IN ORDER TO MEET ITS RECLAIM NO | Nitrogen Oxides (NOx) | A | LOW NOX-BURNER | 18 | PPMVD @ 3% O2
IN-0095 | ALLEGHENY ENERGY SUPPLY CO. LLC | ALLEGHENY ENERGY SUPPLY CO. LLC (ACADIA BAY ENERGY | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-12-07 | 2001 | ELECTRIC POWER GENERATING STATION | AUXILLIARY BOILER | 13.31 | NATURAL GAS | 21 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.049 | LB/MMBTU |  |  |  |  | 0.049 | LB/MMBTU
AL-0180 | DUKE ENERGY DALE, LLC | DUKE ENERGY DALE, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-12-11 | 2001 | NATURAL GAS FIRED COMBINED CYCLE ELECTRIC GENERATING PLANT. | 35 MMBTU/HR NAT. GAS FIRED AUXILIARY BOILER | 13.31 | NATURAL GAS | 35 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.108 | LB/MMBTU |  | 3.77 | LB/H |  | 0.108 | LB/MMBTU
AR-0049 | GEORGIA PACIFIC - CROSSETT PAPER | GEORGIA PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-12-14 | 2001 | KRAFT PAPER MILL. | BURNER EXHAUST A, TAD (SN-85A) | 13.31 | NATURAL GAS | 90 | MMBTU/H | Source has not been installed yet. BACT for PM, VOC, CO and NOx. Initial & 3 yr periodic testing required for CO & NOx. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS. INITIAL TESTING TO VERIFY BACT RATE REQUIRED & EVERY 3 YRS AFTER. | 0.0913 | LB/MMBTU |  |  |  |  | 0.0913 | LB/MMBTU |  | limit for burners A and B combined: 12.8 lb/h
AR-0049 | GEORGIA PACIFIC - CROSSETT PAPER | GEORGIA PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-12-14 | 2001 | KRAFT PAPER MILL. | BURNER EXHAUST B, TAD | 13.31 | NATURAL GAS | 50 | MMBTU/H | Source not yet installed. BACT for PM, CO, NOx, VOC. Initial & 3 -yr periodic testing is required for NOx & CO. | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS. | 0.913 | LB/MMBTU |  |  |  |  | 0.913 | LB/MMBTU
AR-0049 | GEORGIA PACIFIC - CROSSETT PAPER | GEORGIA PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-12-14 | 2001 | KRAFT PAPER MILL. | BURNER, YANKEE | 13.31 | NATURAL GAS | 21 | MMBTU/H | Source is not installed yet. Initial & 3 year periodic testing required for CO & NOx using methods 10 & 7E respectively. BACT for PM, VOC, CO and NOx. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS. | 0.0913 | LB/MMBTU |  | 1.9 | LB/H |  | 0.0913 | LB/MMBTU
*PA-0210 | DART CONTAINER CORP OF PA | DART CONTAINER CORP OF PA | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2001-12-14 | 2001 | NEW BOILERS ARE SUBJECT TO 40 CFR, PART 60, SUBPART DC AND BAT AND 25 PA CODE , CHAPTER 123. | BOILER, (2) | 13.31 | NATURAL GAS | 33.5 | MMBTU/H | CLEAVER BROOKS BOILERS. Boilers subject to NSPS/BAT/SIP | Nitrogen Oxides (NOx) | P | LO-NOX BURNERS | 30 | PPMDV @ 3% O2 |  |  |  |  | 0.036 | LB/MMBTU | CALCULATED
OH-0257 | JACKSON COUNTY POWER, LLC | JACKSON COUNTY POWER, LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-12-27 | 2001 | FOUR 305 MW NATURAL-GAS FIRED COMBUSTION TURBINES, COMBINED CYCLE, WITH DLN AND SCR | AUXILIARY BOILER | 13.31 | NATURAL GAS | 76 | MMBTU/H | Limited to 3000 hours of operation per rolling 12 month period. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS INSTALLED | 6.69 | LB/H |  | 10.03 | T/YR |  | 0.08 | LB/MMBTU
NC-0094 | GENPOWER EARLEYS, LLC | GENPOWER EARLEYS, LLC | NC | NORTH CAROLINA DIV OF ENV MGMT | 2002-01-09 | 2002 | POWER GENERATING FACILITY | BOILER, AUXILIARY, NATURAL GAS | 13.31 | NATURAL GAS | 83 | MMBTU/H | Auxiliary boiler supplies steam for start up, and maintain operating temperatures for HSRGs and steam turbine when the CTs are off line. Boiler is allowed to operate < 1000 h/yr. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 4.07 | LB/H |  |  |  |  | 0.049 | LB/MMBTU | calculated
LA-0174 | PORT HUDSON OPERATIONS | GEORGIA-PACIFIC CORPORATION | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-01-25 | 2002 | PULP MILL | POWER BOILER NO. 2 | 13.31 | NAT GAS | 65.5 | MMBTU/H | EMISSION POINT NO. 6. | Nitrogen Oxides (NOx) | P | LOW-NOX BURNERS | 61.34 | LB/H |  | 40.47 | T/YR |  | 0.1 | LB/MMBTU
CA-1102 | FLETCHER COATING | FLETCHER COATING | CA | SOUTH COAST AQMD, CA | 2002-02-06 | 2002 |  | DRYER OR OVEN, DIRECT OR INDIRECT | 13.31 | NATURAL GAS | 5 | MMBTU/H, 400-600F OPERATING TEMPERATURE | EQUIP: , MFR: INDUSTRIAL PROCESS EQUIPMENT, TYPE: CONVEYORIZED, MODEL: , FUNC EQUIP: POWDER COATING CURING OVEN, FUEL_TYPE: , SCHEDULE: CONTINUOUS, H/D: 8, D/W: 5, W/Y: 52, NOTES: THE MANUFACTURER LITERATURE INDICATES THAT THIS BURNER MAINTAINS ACCEPTABLE | Nitrogen Oxides (NOx) | A | LOW-NOX BURNER | 30 | PPMVD @3% O2 | 30 MIN | [5 empty] | NOT AVAILABLE
OK-0055 | MUSTANG ENERGY PROJECT | MUSTANG POWER LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-02-12 | 2002 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 31 | MMBTU/H |  | Nitrogen Oxides (NOx) | N | COMBUSTION CONTROL | 0.01 | LB/MMBTU |  |  |  |  | 0.01 | LB/MMBTU
OK-0056 | HORSESHOE ENERGY PROJECT | MUSTANG POWER LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-02-12 | 2002 | POWER PLANT | AUXILIARY BOILERS | 13.31 | NATURAL GAS | 0 |  |  | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICES AND DESIGN | 0.1 | LB/MMBTU |  |  |  |  | 0.1 | LB/MMBTU
TX-0388 | SAND HILL ENERGY CENTER | AUSTIN ELECTRIC UTILITY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-02-12 | 2002 | ELECTRIC POWER GENERATOR CONSISTING OF NATURAL GAS-FIRED COMBUSTION TURBINE WITH HRSG. | INLET AIR HEATERS (3) | 13.31 |  |  |  |  | Nitrogen Oxides (NOx) | N |  | 0.53 | LB/H |  | 0.27 | T/YR
LA-0120 | GEISMAR PLANT | SHELL CHEMICAL LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-02-26 | 2002 | RE-EVALUATION OF BACT FOR OLEFIN AND ALCOHOL PROJECT. THIS PROJECT WAS APPROVED EARLIER UNDER PSD PERMIT NO. PSD-LA-647 (M-1) DATED JUNE 26, 2001. THE CURRENT PERMIT IS FOR THE MODIFICATION OF REGENERATIVE FURNACE, EMISSION POINT 620-99, TO INCLUDE PREMIX | REGENERATOR FURNACE #620-99 | 13.31 | NATURAL GAS | 3.3 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | PREMIX STYLE BURNERS. | 0.4 | LB/H |  | 1.16 | T/YR |  | 0.12 | LB/MMBTU
LA-0120 | GEISMAR PLANT | SHELL CHEMICAL LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-02-26 | 2002 | RE-EVALUATION OF BACT FOR OLEFIN AND ALCOHOL PROJECT. THIS PROJECT WAS APPROVED EARLIER UNDER PSD PERMIT NO. PSD-LA-647 (M-1) DATED JUNE 26, 2001. THE CURRENT PERMIT IS FOR THE MODIFICATION OF REGENERATIVE FURNACE, EMISSION POINT 620-99, TO INCLUDE PREMIX | SYLTHERM FURNACE, #321-99 | 13.31 | NATURAL GAS | 53 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS OR COMBINATION FUEL BURNERS | 6.37 | LB/H |  | 11.17 | T/YR |  | 0.04 | LB/MMBTU | SEE POLLUTANT NOTES | THIS HEATER IS PERMITTED TO USE ULTRA LOW NOX BURNERS AS CONTROL WITH AN EMISSION LIMIT OF 0.04 LB/MMBTU OR COMBINATION BURNERS AS CONTROL WITH AN EMISSION LIMIT OF 0.06 LB/MMBTU.
LA-0120 | GEISMAR PLANT | SHELL CHEMICAL LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-02-26 | 2002 | RE-EVALUATION OF BACT FOR OLEFIN AND ALCOHOL PROJECT. THIS PROJECT WAS APPROVED EARLIER UNDER PSD PERMIT NO. PSD-LA-647 (M-1) DATED JUNE 26, 2001. THE CURRENT PERMIT IS FOR THE MODIFICATION OF REGENERATIVE FURNACE, EMISSION POINT 620-99, TO INCLUDE PREMIX | HOT OIL FURNACE, #621-99 | 13.31 | NATURAL GAS | 20 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 0.81 | LB/H |  | 2.84 | T/YR |  | 0.04 | LB/MMBTU
AR-0051 | DUKE ENERGY-JACKSON FACILITY | DUKE ENERGY | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-04-01 | 2002 | 620 MW NATURAL GAS TURBINE ELECTRIC UTILITY PLANT. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 0.035 | LB/MMBTU |  |  |  |  | 0.035 | LB/MMBTU
TN-0153 | WILLIAMS REFINING & MARKETING, L.L.C. | WILLIAMS REFINING & MARKETING, L.L.C. | TN | MEMPHIS AND SHELBY CO HEALTH DEPT, TN | 2002-04-03 | 2002 | PETROLEUM REFINERY | BOILER, NO. 9 | 13.31 | NATURAL GAS | 95 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 0.084 | LB/MMBTU |  |  |  |  | 0.084 | LB/MMBTU
TN-0153 | WILLIAMS REFINING & MARKETING, L.L.C. | WILLIAMS REFINING & MARKETING, L.L.C. | TN | MEMPHIS AND SHELBY CO HEALTH DEPT, TN | 2002-04-03 | 2002 | PETROLEUM REFINERY | CCR STABILIZATION REBOILER | 13.31 | NATURAL GAS | 54 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 0.06 | LB/MMBTU |  |  |  |  | 0.06 | LB/MMBTU
IA-0058 | GREATER DES MOINES ENERGY CENTER | MIDAMERICAN ENERGY | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-04-10 | 2002 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 68 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 0.05 | LB/MMBTU |  | 16.4 | T/YR |  | 0.05 | LB/MMBTU
OK-0072 | REDBUD POWER PLT | REDBUD ENERGY LP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-05-06 | 2002 | ELECTRICAL GENERATOR | AUXILIARY BOILER | 13.31 | NATURAL GAS | 93 | MMBUT/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.075 | LB/MMBTU |  |  |  |  | 0.075 | LB/MMBTU
OH-0264 | NORTON ENERGY STORAGE, LLC | NORTON ENERGY | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-05-23 | 2002 | NINE 300 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE WITH DLN AND SCR; TEN 11.45 MMBTU/H NATURAL GAS-FIRED FUEL SUPPLY HEATERS/BOILERS; SEVEN 12.84 MMBTU/H NATURAL GAS-FIRED RECUPERATOR PRE HEATERS/BOILERS | RECUPERATOR PRE-HEATERS (9) | 13.31 | NATURAL GAS | 12.84 | MMBTU/H | Each boiler is limited to 100 hour of operation per rolling 12 months. | Nitrogen Oxides (NOx) | N |  | 1.207 | LB/H |  | 0.06 | T/YR |  | 0.094 | LB/MMBTU |  | Limits are for each boiler. Each boiler is retricted to 100 hours of operation.
OH-0264 | NORTON ENERGY STORAGE, LLC | NORTON ENERGY | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-05-23 | 2002 | NINE 300 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE WITH DLN AND SCR; TEN 11.45 MMBTU/H NATURAL GAS-FIRED FUEL SUPPLY HEATERS/BOILERS; SEVEN 12.84 MMBTU/H NATURAL GAS-FIRED RECUPERATOR PRE HEATERS/BOILERS | FUEL SUPPLY HEATERS (9) | 13.31 | NATURAL GAS | 11.45 | MMBTU/H | Each fuel supply heater is limited to a maximum annual cumulative fuel heat input of 47,630 mmBtu per rolling 12 months. | Nitrogen Oxides (NOx) | N |  | 1.076 | LB/H |  | 2.24 | T/YR |  | 0.094 | LB/MMBTU |  | Limits are for each heater.
NM-0044 | CLOVIS ENERGY FACILITY | DUKE ENERGY CURRY LLC | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2002-06-27 | 2002 | THIS IS A 1,200 MW COMBINED CYCLE MERCHANT POWER PLANT. | AUXILIARY BOILERS (AUX-1 AND AUX-2) | 13.31 | NATURAL GAS | 33 | MMBTU/H | Emission limits are for each (Aux-1 and Aux-2) Auxiliary Boiler. | Nitrogen Dioxide (NO2) | P | CLEAN FUEL, GOOD COMBUSITON PRACTICE | 1.2 | LB/H | each |  |  |  | 0.036 | LB/MMBTU | calculated
OK-0070 | GENOVA OK I POWER PROJECT | GENOVA OKLAHOMA LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-06-13 | 2002 | COMBINED CYCLE POWER PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.035 | LB/MMBTU |  |  |  |  | 0.035 | LB/MMBTU
TX-0437 | HARTBURG POWER, LP | HARTBURG POWER, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-07-05 | 2002 | LOCATED AT NE OF INDIAN LAKE RD, DEWYVILLE, TX. NEW POWER FACILITY. | BOILERS, AUXILIARY | 13.31 | NATURAL GAS | 40 | mmbtu/h |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS, CLEAN FUEL. BOILER WILL OPERATE A MAXIMUM OF 3000 H/YR |  |  | SEE NOTE | [6 empty] | BACT IS POLLUTION PREVENTION
AL-0185 | BARTON SHOALS ENERGY | BARTON SHOALS ENERGY, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2002-07-12 | 2002 | ELECTRIC GENERATION - NATURAL GAS FIRED COMBINED CYCLE | TWO (2) 40 MMBTU/H AUXILIARY BOILERS | 13.31 | NATURAL GAS | 40 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.05 | LB/MMBTU |  | 2 | LB/H |  | 0.05 | LB/MMBTU
IA-0060 | HAWKEYE GENERATING, LLC | ENTERGY | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-07-23 | 2002 | ENTERGY IS INSTALLING TWO GE 7FA (170MW) NATURAL GAS FIRED TURBINES. THEY ARE REQUIRED TO INSTALL SCR FOR CONTROL OF NOX (3 PPMVD, 3 HOUR AVG. TIME) AND CATALYTIC OXIDATION FOR THE CONTROL OF CO (5 PPMVD, 3 HOUR AVG. TIME) FOR COMBINED CYCLE OPERATION. SI | AUXILIARY BOILER (48.5 MMBTU/H) | 13.31 | NATUAL GAS | 48.69 | MILLION CF/YR |  | Nitrogen Dioxide (NO2) | B | GCP | 0.034 | LB/MMBTU |  |  |  |  | 0.034 | LB/MMBTU
AR-0070 | GENOVA ARKANSAS I, LLC | GENOVA ARKANSAS I, LLC | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-08-23 | 2002 | COMBINED CYCLE POWER PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX OPTION (LOW NOX BURNER AND/OR FLUE GAS RECIRCULATION) | 0.04 | LB/MMBTU |  |  |  |  | 0.04 | LB/MMBTU
*WA-0297 | NORTHWEST PIPELINE CORPORATION MT. VERNON | NORTHWEST PIPELINE CORPORATION | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2002-08-30 | 2002 |  | BOILER | 13.31 | NATURAL GAS | 4.19 | MMBTU/H | PSD for NOx only | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICE | 34 | PPM @ 3% O2 | 24 H AVG | 4 | LB/D |  |  |  | NOT AVAILABLE, SEE NOTE | PERMIT LIMIT IS IN PPM, AND LB/DAY. A LIMIT IN LB/MMBTU WAS NOT PROVIDED.
VA-0261 | CPV CUNNINGHAM CREEK | COMPETITIVE POWER VENTURE | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-09-06 | 2002 | TURBINES USED TO PRODUCE ELECTRICITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 80 | MMBTU/H | one auxiliary boiler | Nitrogen Dioxide (NO2) | P | LOW NOX BURNERS AND GOOD COMBUSTION PRACTICES. | 3.82 | LB/H |  | 5.73 | T/YR |  | 0.05 | LB/MMBTU
OH-0248 | LAWRENCE ENERGY | CALPINE CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-09-24 | 2002 | THREE 180 MW GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE, WITH DLN, SCR AND OXIDATION CATALYST | BOILER | 13.31 | NATURAL GAS | 99 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 4.95 | LB/H |  | 0.05 | LB/MMBTU |  | 0.05 | LB/MMBTU |  | Limits are for each boiler.
CA-1023 | LA COUNTY INTERNAL SERVICES DEPT. | LA COUNTY INTERNAL SERVICES DEPT. | CA | SOUTH COAST AQMD, CA | 2002-10-08 | 2002 |  | BOILER, 39 MMBTU/H | 13.31 | NATURAL GAS | 39 | MMBTU/H | MFR: SPRINGFIELD, TYPE: WATER TUBE, MODEL: STIRLING, FUNC EQUIP: BACKS UP COGEN SYSTEM DURING SCHEDULED MAINTENANCE, SCHEDULE: VARIABLE, H/D: 8, D/W: 1, W/Y: 12, NOTES: 90,000 THERMS PER MONTH HEAT INPUT SOURCE TEST RESULTS: TEST DATES MARCH 23-30, 2004 F | Nitrogen Oxides (NOx) | P | ULTRA-LOW NOX BURNER WITH FGR | 9 | PPMVD @ 3% O2 | [6 empty] | NOT AVAILABLE
AL-0192 | HONDA MANUFACTURING OF ALABAMA, LLC | HONDA MANUFACTURING OF ALABAMA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2002-10-18 | 2002 | AUTOMOBILE MANUFACTURING PLANT | BOILERS, NATURAL GAS, (3) | 13.31 | NATURAL GAS | 30 | MMBTU/H | throughput for each boiler. BACT for CO, NOx, PM10, and VE | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS, CLEAN FUEL, GOOD COMBUSTION | 1.05 | LB/H |  | 0.035 | LB/MMBTU |  | 0.035 | LB/MMBTU
WI-0195 | SENA NIAGARA MILL | STORA ENSO NORTH AMERICA | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2002-10-18 | 2002 |  | PROCESS HEATER, PAPER MACHINE P51 | 13.31 | NATURAL GAS | 34.4 | MMBTU/H | Throughput is total for natural gas IR and flotation dryers. | Nitrogen Oxides (NOx) | P | ANY NEW (REPLACEMENT) IR BURNERS WILL BE LOW NOX BURNERS, FIRING NATURAL GAS | 0.044 | LB/MMBTU |  |  |  |  | 0.044 | LB/MMBTU
NJ-0062 | CONSOLIDATE EDISON DEVELOPMENT (CED) | CONSOLIDATED EDISON DVPMT.- LAKEWOOD GEN. FACILITY | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2002-10-22 | 2002 | POWER GENERATION | FUEL GAS HEATERS (3 UNITS) | 13.31 | NATURAL GAS | 4.62 | MMBTU/H | INSTALLATION OF 3 NEW FUEL GAS HEATERS@ 4.62 MMBTU/HR EACH. FUEL: NATURAL GAS. | Nitrogen Oxides (NOx) | N | LOW NOX -COMBUSTOR | 0.17 | LB/H |  | 0.036 | LB/MMBTU |  | 0.036 | LB/MMBTU
GA-0101 | MURRAY ENERGY FACILITY | DUKE ENERGY MURRAY LLC | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2002-10-23 | 2002 | ELECTRIC GENERATING FACILITY | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 31.4 | MMBTU/H | HOURS OF OPERATION NOT TO EXCEED 6,000 H/YR. | Nitrogen Oxides (NOx) | P | DRY LOW NOX BURNERS, FLUE GAS RECIRCULATION | 30 | PPM @ 3% O2 |  |  |  |  | 0.037 | LB/MMBTU | CALCULATED
VA-0255 | VA POWER - POSSUM POINT | Virginia Power | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-11-18 | 2002 | THIE PERMIT WAS AMENDED AND APPROVED ON 11/18/2002 FROM THE PERMIT THAT WAS DATED 10/05/2001. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 99 | MMBTU/H | 2 Auxiliary boilers. | Nitrogen Dioxide (NO2) | P | LOW NOX BURNERS AND LOW NOX FUEL. | 0.036 | LB/MMBTU | EACH UNIT | 18 | T/YR | UNITS COMBINED | 0.036 | LB/MMBTU | EACH UNIT
VA-0260 | HENRY COUNTY POWER | Cogentrix Energy Inc | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-11-21 | 2002 | 4 COMBINED CYCLE TURBINES WITH A TOTAL ELECTRICITY PRODUCTION OF 1,100 MW. | AUXILIARY BOILER, (2) | 13.31 | NATURAL GAS | 40 | MMBTU/H | Two Auxiliary Boilers. BACT for NOx and CO only. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND CLEAN FUEL. | 3.2 | LB/H | each unit | 4.8 | T/YR | each unit | 0.08 | LB/MMBTU | each unit
TX-0408 | INDIAN ROCK GATHERING COMPANY LP | INDIAN ROCK GATHERING COMPANY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-11-22 | 2002 | NATURAL GAS PROCESSING FACILITY | AUXILIARY BOILER, (2) | 13.31 | NATURAL GAS | 6 | MMBTU/H | BOILERS ARE UNCONTROLLED BECAUSE BOILER DUTY IS <40 MMBTU/H. | Nitrogen Oxides (NOx) | N |  | 0.59 | LB/H | EACH | 2.58 | T/YR | EACH | 0.098 | LB/MMBTU |  | UNCONTROLLED BECAUSE BOILER IS LESS THAN 40 MMBTU/H.
VA-0243 | STANLEY FURNITURE |  | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-12-01 | 2002 | WOOD HOUSEHOLD FURNITURE MFG. | BOILER, NAT GAS & OIL | 13.31 | NATURAL GAS | 26.5 | MMBTU/H | KEWANEE NATURAL GAS/DISTILLATE OIL BOILER. THROUGHPUT 26.5 MMBTU/HR - 450,000 GAL #2 OIL. ADDITIONAL SCC, 10200502. FOR ALL POLLUTANTS, NO CONTROLS, EMISSION LIMITS IN T/YR ONLY | Nitrogen Oxides (NOx) | N | EMISSION LIMITS IN T/YR ONLY | 12.8 | T/YR | [6 empty] | NOT AVAILABLE
TX-0392 | LUCITE BEAUMONT | INEOS ACRYLICS, INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-09 | 2002 | SULFURIC ACID REGENERATION FACILITY | NO.1 PRE-HEATER | 13.31 | NATURAL GAS |  |  |  | Nitrogen Oxides (NOx) | N |  | 5.6 | LB/H |  | 53.9 | T/YR |  | 0.12 | LB/MMBTU
TX-0392 | LUCITE BEAUMONT | INEOS ACRYLICS, INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-09 | 2002 | SULFURIC ACID REGENERATION FACILITY | NO. 2 PRE-HEATER | 13.31 | NATURAL GAS |  |  |  | Nitrogen Oxides (NOx) | N |  | 3.8 | LB/H |  | 16.4 | T/YR |  | 0.08 | LB/MMBTU
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | HEAT TRANSFER FLUID HEATER, H202 | 13.31 | NATURAL GAS | 31 | MMBTU/H |  | Nitrogen Oxides (NOx) | N | NONE INDICATED | 3.08 | LB/H |  | 13.48 | T/YR |  | 0.1 | LB/MMBTU | CALCULATED USING THROUGHPUT
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | HEAT TRANSFER FLUID HEATER, H2202 | 13.31 | NATURAL GAS | 31 | MMBTU/H |  | Nitrogen Oxides (NOx) | N | NONE INDICATED | 3.08 | LB/H |  | 13.48 | T/YR |  | 0.1 | LB/MMBTU | CALCULATED USING THROUGHPUT
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | (2) STEAM BOILERS, X-426A AND X-426B | 13.31 | NATURAL GAS | 15.8 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 2.05 | LB/H | EACH | 9 | T/YR | EACH | 0.13 | LB/MMBTU
IA-0062 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT (IPL) | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-12-20 | 2002 | PERMITS WERE AMENDED ON 6/26/03. RBLC ID IA-0062 WAS CORRECTED AS MOST OF THE CHANGES WERE MINOR (BASED ON OPERATIONAL & DESIGN CHANGES BEING MADE AS PLANT IS CONSTRUCTED). THE NEW DEW POINT HEATER HAS BEEN GIVEN A NEW RBLC ID. | GAS HEATER, (2) | 13.31 | NATURAL GAS | 16.4 | MMBTU/H | Natural Gas fired Heaters, 16.4 MMBTU/HR capacity for each. Operating hours reduced from 8760 hours to 6000 hours each. | Nitrogen Dioxide (NO2) | P | DLN | 0.049 | LB/MMBTU |  |  |  |  | 0.049 | LB/MMBTU |  | SCR cost $35k
IA-0062 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT (IPL) | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-12-20 | 2002 | PERMITS WERE AMENDED ON 6/26/03. RBLC ID IA-0062 WAS CORRECTED AS MOST OF THE CHANGES WERE MINOR (BASED ON OPERATIONAL & DESIGN CHANGES BEING MADE AS PLANT IS CONSTRUCTED). THE NEW DEW POINT HEATER HAS BEEN GIVEN A NEW RBLC ID. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 68 | MMBTU/H | Limited to 6000 hours of operation per year. | Nitrogen Dioxide (NO2) | P | DLN | 0.049 | LB/MMBTU |  |  |  |  | 0.049 | LB/MMBTU |  | Boiler came with DLN therefore a cost/ton was not done.
IN-0116 | PSEG LAWRENCEBURG ENERGY CO., INC. | PSEG LAWRENCEBURG ENERGY CO., INC. | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2002-12-23 | 2002 | POWER PLANT | HEATER, STARTUP GAS, NATURAL GAS | 13.31 | NATURAL GAS | 2.4 | MMBTU/H | Startup gas heater. Natural gas usage shall not exceed 5.3 MMSCF/ 12 mo period rolled on monthly basis | Nitrogen Oxides (NOx) | N |  | 0.14 | LB/MMBTU |  |  |  |  | 0.14 | LB/MMBTU
TX-0389 | BAYTOWN CARBON BLACK PLANT | DEGUSSA ENGINEERED CARBONS, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-31 | 2002 |  | BACK-UP BOILER | 13.31 | NATURAL GAS | 13.4 | MMBUT/H |  | Nitrogen Oxides (NOx) | N |  | 1.4 | LB/H |  | 6.12 | T/YR
WA-0291 | WALLULA POWER PLANT | WALLULA GENERATION, LLC | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2003-01-03 | 2003 | WALLULA GENERATION, LLC, PROPOSES TO CONSTRUCT AND OPERATE A 1,300 MW COMBINED CYCLE ELECTRIC POWER PLANT. THE PROJECT WILL CONSIST OF TWO INDEPENDENT POWER BLOCKS WITH CRITICAL BACK-UP SYSTEMS TO MAINTAIN OVERALL PLANT RELIABILITY AND AVAILABILITY. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 55.3 | MMBTU/H | Operational limit of 4,000 hr per year | Nitrogen Oxides (NOx) | N | LNB PLUS FGR | 30 | PPMDV @ 3% O2 | 3 hr ave | 12.7 | LB/H | 3 hr ave | 0.23 | LB/MMBTU
PA-0216 | J & L SPECIALTY STEEL, INC. | J & L SPECIALTY STEEL, INC. | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2003-01-13 | 2003 | THIS PA/REVIEW MEMO IS VERY LONG AND INVOLVED AND SHOULD BE CONSULTED FOR ANY CLARIFICATION ON ISSUES. | BOILER, DRAP LINE | 13.31 | NATURAL GAS | 33.5 | MMBTU/H | Installation of ultra-low Nox burner on the drap line | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNER | 30 | PPM @ 3% O2 |  |  |  |  | 0.04 | LB/MMBTU | Calculated using F-Factor
OH-0295 | GMC TRUCK AND BUS, MORAINE ASSEMBLY PLANT | GENERAL MOTORS CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-01-14 | 2003 | LIGHT DUTY TRUCKS AND AUTOMOBILE PRODUCTION, ASSEMBLY PLANT | NATURAL GAS USAGE | 13.31 | NATURAL GAS | 1700 | MMCF/rolling 12-mo | THE INCREASE IN NATURAL GAS USAGE CAUSED THIS PERMIT TO BE PSD FOR NOX. COMBINED NATURAL GAS USAGE FOR: ELPO SAND, GUIDE COAT, BODY SAND, BODY WIPE, TOPCOAT SYSTEM, TOPCOAT ABATEMENT, FINAL REPAIR, DEADNER, BUILDING HEAT. | Nitrogen Oxides (NOx) | N |  | 135.58 | T/YR | [6 empty] | NOT AVAILABLE
IA-0064 | ROQUETTE AMERICA | ROQUETTE AMERICA | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2003-01-31 | 2003 |  | DEW POINT HEATER | 13.31 | NATURAL GAS | 1.6 | MMBTU/H | natural gas only, operates 8760 h/yr | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICES | 0.15 | LB/MMBTU |  | 0.24 | LB/H |  | 0.15 | LB/MMBTU
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HOT OIL HEATER, EPN6 | 13.31 | NAT GAS | 12 | MMBTU/H |  | Nitrogen Oxides (NOx) | N | NONE INDICATED | 1.41 | LB/H |  | 5.15 | T/YR |  | 0.118 | LB/MMBTU | SEE NOTE | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | GLYCOL REBOILER, EPN11 | 13.31 | NAT GAS | 2.5 | MMBTU/H |  | Nitrogen Oxides (NOx) | N | NONE INDICATED | 0.29 | LB/H |  | 1.07 | T/YR |  | 0.116 | LB/MMBTU | SEE NOTE | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HOT OIL HEATER, EPN26 | 13.31 | NAT GAS | 32.5 | MMBTU/H |  | Nitrogen Oxides (NOx) | N | NONE INDICATED | 1.95 | LB/H |  | 8.54 | T/YR |  | 0.06 | LB/MMBTU | CALCULATED, SEE NOTES | EMISSION LIMIT IN STANDARDIZED UNITS WAS CALCULATED BY DIVIDING THE HOURLY LIMIT BY THE THROUGHPUT.
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HP TEG FIREBOX, EPN30 | 13.31 | NAT GAS | 3 | MMBTU/H |  | Nitrogen Oxides (NOx) | N | NONE INDICATED | 0.29 | LB/H |  | 1.29 | T/YR |  | 0.0967 | LB/MMBTU | SEE NOTE | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
IA-0063 | WISDOM GENERATION STATION | CORN BELT POWER COOPERATIVE | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2003-02-05 | 2003 |  | HEATER , NATURAL GAS | 13.31 | NATURAL GAS | 5.38 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | DLN | 0.095 | LB/MMBTU |  |  |  |  | 0.095 | LB/MMBTU
OR-0040 | KLAMATH GENERATION, LLC | KLAMATH GENERATION, LLC | OR | OREGON DEPT OF ENVIRONMENTAL QUALITY | 2003-03-12 | 2003 | POWER GENERATION FACILITY | BOILER, AUXILIARY, NATURAL GAS | 13.31 | NATURAL GAS | 50000 | LB/H | Throughput is lb/h of steam. Boiler provides steam for standby and startup conditions. | Nitrogen Oxides (NOx) | N |  | 30 | PPMVD @ 3% O2 | 3-H AVG | [5 empty] | NOT AVAILABLE
OK-0090 | DUKE ENERGY STEPHENS, LLC STEPHENS ENERGY | DUKE ENERGY | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2003-03-21 | 2003 | MERCHANT POWER PLANT - NOMINAL TOTAL OF 620 MW. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW-NOX BURNERS | 0.05 | LB/MMBTU |  |  |  |  | 0.05 | LB/MMBTU
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 | 2003 |  | BOILER NO. 1 | 13.31 | NATURAL GAS | 43.2 | MMBTU/H | One of two boilers | Nitrogen Dioxide (NO2) | B | FLUE GAS RECIRCULATION WITH LOW NOX BURNERS. CONTINUOUS EMISSION MONITORING SYSTEM. GOOD COMBUSTION PRACTICES. | 6.17 | LB/H | each unit |  |  |  | 0.14 | LB/MMBTU |  | one of two units
GA-0098 | RINCON POWER PLANT | GENPOWER RINCON LLC | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2003-03-24 | 2003 | ELECTRIC GENERATING FACILITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 83 | MMBTU/H | THE BOILER IS LIMITED TO 1,000 H/YR OF OPERATION. | Nitrogen Oxides (NOx) | N |  | 0.055 | LB/MMBTU |  |  |  |  | 0.055 | LB/MMBTU
WA-0316 | NORTHWEST PIPELINE CORP.-MT VERNON COMPRESSOR | NORTHWEST PIPELINE CORP. | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2003-03-27 | 2003 | NATURAL GAS TRANSMISSION STATION | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 4.19 | MMBTU/H | Sellers C100 heater/boiler | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICE | 34 | PPMDV @ 3% O2 | 24 h avg | 4 | LB/D |  | 0.04 | LB/MMBTU | calculated | Additional limit: .66 t/yr
OH-0276 | CHARTER STEEL | CHARTER MANUFACTURING CO., INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-04-14 | 2003 | NEW MELT SHOP AT EXISTING FACILITY, INCLUDES NEW: ELECTRIC ARC FURNACE; LADLE METALLURGY FURNACE; VACUUM OXYGEN DEGASSER (VOD); VOC BOILER; CONTINUOUS CASTING MACHINES; 3 SILOS; 6 LADLE PREHEATERS; CUT-OFF-TORCH; 3 TUNDISH PREHEATERS; PROCESS SPACE HEATER | BOILER FOR VACUUM OXYGEN DEGASSER VESSEL | 13.31 | NATURAL GAS | 25 | MMBTU/H | VACUUM OXYGEN DEGASSER VESSEL BOILER, WITH LOW NOX BURNER | Nitrogen Oxides (NOx) | A | LOW NOX BURNER | 2.45 | LB/H | FROM NATURAL GAS COMBUSTION | 10.7 | T/YR | FROM NATURAL GAS COMBUSTION |  |  | NOT AVAILABLE
GA-0105 | MCINTOSH COMBINED CYCLE FACILITY | SAVANNAH ELECTRIC AND POWER CO | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2003-04-17 | 2003 | ELECTRIC GENERATING FACILITY | FUEL GAS HEATER | 13.31 | NATURAL GAS | 5 | MMBTU/H |  | Nitrogen Oxides (NOx) | N |  | 99 | PPM @ 15% O2 |  |  |  |  | 0.37 | LB/MMBTU | CALCULATED
GA-0107 | TALBOT ENERGY FACILITY | OGLETHORPE POWER CORPORATION | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2003-06-09 | 2003 | ELECTRIC GENERATING FACILITY | FUEL GAS PREHEATERS, (3) | 13.31 | NATURAL GAS | 5 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | DRY LOW NOX BURNERS | 30 | PPM @ 15% O2 |  |  |  |  | 0.11 | LB/MMBTU | CALCULATED
IA-0068 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT - EMERY GENERATING STATI | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2003-06-26 | 2003 | IPL CHANGED NAMES FROM THE POWER IOWA ENERGY CENTER (PIEC) TO THE EMERY GENERATING STATION. | GAS HEATER | 13.31 | NATURAL GAS | 9 | MMBTU/H | One natural gas dew point heater is added. | Nitrogen Oxides (NOx) | A | DLN | 0.049 | LB/MMBTU |  | 1.93 | T/YR |  | 0.049 | LB/MMBTU
TX-0458 | JACK COUNTY POWER PLANT | DUKE ENERGY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-07-22 | 2003 | DUKE ENERGY JACK, L.P. IS CONSTRUCTING A 620 MW COMBINED CYCLE POWER PLANT. TWO COMBUSTION TURBINES WILL EACH PROVIDE APPROXIMATELY 170 MW OF ELECTRICITY. A 550 MMBTU/HR DUCT BURNER ON EACH TURBINE EXHAUST STREAM WILL ADD SUPPLEMENTAL HEAT TO THE HEAT REC | AUXILIARY BOILER | 13.31 | NATURAL GAS | 36 | mmbtu/h |  | Nitrogen Oxides (NOx) | N |  | 1.3 | LB/H |  | 3.9 | T/YR |  | 0.036111 | LB/MMBTU
OH-0254 | DUKE ENERGY WASHINGTON COUNTY LLC | DUKE ENERGY NORTH AMERICA | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-08-14 | 2003 | TWO 170 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE | BOILER | 13.31 | NATURAL GAS | 30.6 | MMBTU/H | THE MAXIMUM ANNUAL FUEL HEAT INPUT SHALL NOT EXCEED 128,000 MMBTU/ROLLING 12-MONTHS | Nitrogen Oxides (NOx) | N |  | 1.08 | LB/H |  | 2.3 | T/ROLLING 12-MONTHS |  | 0.035 | LB/MMBTU
AZ-0049 | LA PAZ GENERATING FACILITY | ALLEGHENY ENERGY SUPPLY LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2003-09-04 | 2003 | NATURAL GAS FIRED, COMBINED CYCLE GENERATING STATION | AUXILIARY BOILER FOR GE TURBINE | 13.31 | NATURAL GAS | 41 | MMBTU/H | THIS BOILER IS TO BE USED IF THE GE TURBINE SETUP IS SELECTED. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.027 | LB/MMBTU |  |  |  |  | 0.027 | LB/MMBTU
AZ-0049 | LA PAZ GENERATING FACILITY | ALLEGHENY ENERGY SUPPLY LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2003-09-04 | 2003 | NATURAL GAS FIRED, COMBINED CYCLE GENERATING STATION | AUXILIARY BOILER FOR SIEMENS TURBINES | 13.31 | NATURAL GAS | 55.34 | MMBTU/H | THIS BOILER IS FOR USE WHEN THE SIEMENS TURBINE SYSTEM IS SELECTED. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.036 | LB/MMBTU |  |  |  |  | 0.036 | LB/MMBTU
MI-0355 | ABBOTT LABORATORIES, STURGIS PLANT | ABBOTT LABORATORIES, ROSS PRODUCTS DIVISION | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 2003-09-16 | 2003 | NUTRITIONAL PRODUCTS MANUFACTURER. | BOILER, GAS-FIRED | 13.31 | NATURAL GAS | 98.51 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION. | 0.08 | LB/MMBTU |  |  |  |  | 0.08 | LB/MMBTU |  | Limit is based on combustion of natural gas. Limit for burning #2 fuel oil is 0.14 lb/MMBtu
IN-0108 | NUCOR STEEL | NUCOR STEEL | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2003-11-21 | 2003 | STEEL MINI MILL | BOILER, NATURAL GAS, (2) | 13.31 | NATURAL GAS | 34 | MMBTU/H | Throughput for each. Propane is backup fuel. These boilers supply steam to the entire cold mill area of the plant. Subject to NSPS Subpart Dc | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS, NATURAL GAS | 0.035 | LB/MMBTU |  |  |  |  | 0.035 | LB/MMBTU
MN-0054 | MANKATO ENERGY CENTER |  | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2003-12-04 | 2003 | COMBINED CYCLE GAS TURBINE ELECTRIC POWER PLANT. TWO IDENTICAL GE FRAME F7A GAS TURBINES EACH WITH HRSG W/DUCT BURNERS FEEDING STEAM TO COMMON STEAM TURBINES. PRIMARY FUEL IS NG, NO. 2 VERY LOW SULFUR DISTILLATE OIL FOR BACKUP. ALSO, AUX. BOILER, DIESEL E | BOILER, COMMERCIAL | 13.31 | NATURAL GAS | 70 | MMBTU/H | NATURAL GAS ONLY | Nitrogen Oxides (NOx) | P | DRY LOW NOX AND FLUE GAS RECIRCULATION | 0.036 | LB/MMBTU |  |  |  |  | 0.036 | LB/MMBTU
OR-0039 | COB ENERGY FACILITY, LLC | Peoples Energy Resources | OR | OREGON DEPT OF ENVIRONMENTAL QUALITY | 2003-12-30 | 2003 | POWER GENERATION FACILITY | BOILERS, AUXILIARY, NATURAL GAS, (2) | 13.31 | NATURAL GAS | 80 | MMBTU/H | Throughput for each. Provide auxiliary steam for standby and startup conditions. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 0.035 | LB/MMBTU | 3-h avg |  |  |  | 0.035 | LB/MMBTU |  | Limit does not apply during startup and shut down.
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S50/B50, 60 MMBTU/H | 13.31 | NATURAL GAS | 60 | MMBTU/H | NATURAL GAS / PROPANE | Nitrogen Oxides (NOx) | P | LOW NOX BURNER | 0.04 | LB/MMBTU |  |  |  |  | 0.04 | LB/MMBTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S51/B51, 80 MMBTU/H | 13.31 | NATURAL GAS | 80 | MMBTU/H | NAT. GAS / PROPANE | Nitrogen Oxides (NOx) | P | NAT. GAS / PROPANE, LOW NOX BURNER | 0.04 | LB/MMBTU |  |  |  |  | 0.04 | LB/MMTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S52/B52, 11 MMBTU/H | 13.31 | NATURAL GAS | 11 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | NATURAL GAS / PROPANE; LOW NOX BURNER | 0.04 | LB/MMBTU |  |  |  |  | 0.04 | LB/MMBTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S53 / B53, 34 MMBTU/H | 13.31 | NATURAL GAS | 34 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | NATURAL GAS / PROPANE; LOW NOX BURNER | 0.04 | LB/MMBTU |  |  |  |  | 0.04 | LB/MMBTU
OK-0097 | QUAD GRAPHICS OKC FAC | QUAD GRAPHICS INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2004-02-03 | 2004 | COMMERCIAL PRINTING | BOILERS, NATURAL GAS, STEAM GENERATORS | 13.31 | NATURAL GAS | 600 | HP | Throughput for each boiler. Boilers produce steam for solvent recovery. Natural gas is primary fuel, propane used for emergencies, limited to 336 h/yr, each boiler. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS, CLEAN FUEL, AND FLUE GAS RECIRCULATION | 0.035 | LB/MMBTU |  |  |  |  | 0.035 | LB/MMBTU |  | Limit while burning propane: 0.15 lb/mmbtu (propane limited to < 336 h/yr each)
OK-0097 | QUAD GRAPHICS OKC FAC | QUAD GRAPHICS INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2004-02-03 | 2004 | COMMERCIAL PRINTING | HEATERS/OXIDIZERS | 13.31 | NATURAL GAS | 16 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | MAINTENANCE/OPERATION PER MANUFACTURE'S SPECIFICATION, AND EXCLUSIVELY FIRING COMMERCIAL NATURAL GAS OR PROPANE. | 2.48 | LB/H |  | 5.23 | T/YR |  | 0.155 | LB/MMBTU | calculated
AR-0076 | U.S. ARMY, PINE BLUFF ARSENAL | U.S. ARMY, PINE BLUFF ARSENAL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-02-17 | 2004 | PINE BLUFF ARSENAL IS THE ARMY'S ONLY CHEMICAL ARSENAL AND THE ONLY INSTALLATION WITH BOTH MANUFACTURING AND DEPOT FUNCTIONS. OPERATIONAL FUNCTIONS INCLUDE: AMMUNITION OPERATIONS; CHEMICAL AND BIOLOGICAL DEFENSE OPERATIONS; PRODUCT AND PROCESS DEVELOPMENT | BOILER, PROCESS STEAM, (2) SN-PBCDF-03, -04 | 13.31 | NATURAL GAS | 0.03 | MMDSCF/H | THROUGH PUT FOR EACH. ADDITIONAL THROUGHPUT: 28.4 MMBTU/H (EACH). PROCESS STEAM BOILER SERVES BRINE REDUCTION AREA EQUIPMENT. | Nitrogen Oxides (NOx) | P | LOW-NOX BURNERS WITHOUT FLUE GAS RECIRCULATION. | 1.5 | LB/H | EACH |  |  |  | 0.0528 | LB/MMBTU | CALCULATED | ESTIMATED CAPITAL COSTS RANGE FROM $ 7500 TO $ 25000 FOR EACH BOILER.
AR-0076 | U.S. ARMY, PINE BLUFF ARSENAL | U.S. ARMY, PINE BLUFF ARSENAL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-02-17 | 2004 | PINE BLUFF ARSENAL IS THE ARMY'S ONLY CHEMICAL ARSENAL AND THE ONLY INSTALLATION WITH BOTH MANUFACTURING AND DEPOT FUNCTIONS. OPERATIONAL FUNCTIONS INCLUDE: AMMUNITION OPERATIONS; CHEMICAL AND BIOLOGICAL DEFENSE OPERATIONS; PRODUCT AND PROCESS DEVELOPMENT | BOILER, HOT WATER, (2) SN-PBCDF-05, -06 | 13.31 | NATURAL GAS | 0.01 | MMDSCF/H | ADDITIONAL THROUGHPUT: 11.7 MMBTU/H, THROUGHPUT FOR EACH. | Nitrogen Oxides (NOx) | P | LOW-NOX BURNERS WITHOUT FLUE GAS RECIRCULATION. | 0.6 | LB/H | EACH |  |  |  | 0.051 | LB/MMBTU | CALCULATED | ESTIMATED CAPITAL COSTS RANGE FROM $ 7500 TO $ 25000 FOR EACH BOILER.
AR-0076 | U.S. ARMY, PINE BLUFF ARSENAL | U.S. ARMY, PINE BLUFF ARSENAL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-02-17 | 2004 | PINE BLUFF ARSENAL IS THE ARMY'S ONLY CHEMICAL ARSENAL AND THE ONLY INSTALLATION WITH BOTH MANUFACTURING AND DEPOT FUNCTIONS. OPERATIONAL FUNCTIONS INCLUDE: AMMUNITION OPERATIONS; CHEMICAL AND BIOLOGICAL DEFENSE OPERATIONS; PRODUCT AND PROCESS DEVELOPMENT | BOILER, LABORATORY SN-PBCDF-16 | 13.31 | NATURAL GAS | 1.4 | mmbtu/h |  | Nitrogen Oxides (NOx) | P | LOW-NOX BURNERS WITHOUT FLUE GAS RECIRCULATION. | 0.2 | LB/H |  |  |  |  | 0.143 | LB/MMBTU | CALCULATED | ESTIMATED CAPITAL COSTS RANGE FROM $ 7500 TO $ 25000 FOR EACH BOILER.
AL-0191 | HYUNDAI MOTOR MANUFACTURING OF ALABAMA, LLC | HYUNDAI MOTOR MANUFACTURING OF ALABAMA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2004-03-23 | 2004 | AUTOMOBILE MANUFACTURING PLANT | BOILERS, NATURAL GAS, (3) | 13.31 | NATURAL GAS | 50 | MMBTU/H | BACT for NOx, PM, and CO | Nitrogen Oxides (NOx) | P | NATURAL GAS ONLY; LOW NOX BURNERS | 1.75 | LB/H |  | 0.035 | LB/MMBTU |  | 0.035 | LB/MMBTU
ID-0015 | J R SIMPLOT COMPANY - DON SIDING PLANT | J R SIMPLOT COMPANY | ID | IDAHO DEPT OF ENVIRONMENTAL QUALITY | 2004-04-05 | 2004 | THE DON SIDING PLANT IS A PHOSPHATE FERTILIZER MANUFACTURING FACILITY. EMISSION UNITS REVIEWED FOR RACT INCLUDE: 300 SULFURIC ACID PLANT, 400 SULFURIC ACID PLANT, PHOSPHORIC ACID PLANT, RECLAIM COOLING TOWERS, GRANULATION I, GRANULATION II, GRANULATION II | BOILER, 64 MMBTU/H | 13.31 | NATURAL GAS | 64 | MMBTU/H | BABCOCK & WILCOX BOILER | Nitrogen Oxides (NOx) | P | LOW-NOX BURNER | 2.88 | LB/H |  | 12.63 | T/YR |  | 0.045 | LB/MMBTU | CALCULATED, NOT PERMIT LIMIT | NATURAL GAS USAGE LIMITED TO 559 MMCF/YR
NV-0037 | COPPER MOUNTAIN POWER | SEMPRA ENERGY RESOURCES | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2004-05-14 | 2004 | A 600 MW COMBINED CYCLE ELECTRICAL GENERATION FACILITY CONSISTING OF TWO COMBUSTION TURBINE GENERATORS WITH HEAT RECOVERY STEAM GENERATORS, ONE STEAM TURBINE GENERATOR, AND ONE AUXILIARY BOILER. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 60 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNER (WITH EITHER INTERNAL OR EXTERNAL FLUE GAS RECIRCULATION) | 0.035 | LB/MMBTU |  | 9.6 | TONS/YR |  | 0.035 | LB/MMBTU
WV-0021 | OHIO RIVER PLANT | CABOT CORPORATION | WV | WEST VIRGINIA AIR POLLUTION CONTROL COMM | 2004-06-09 | 2004 | AN EXISTING 3-UNIT, 4-REACTOR CARBON BLACK PRODUCTION FACILITY. TRADITIONALLY, HAS FLARED OR COMBUSTED ALL TAIL GAS. | BOILER, NATURAL GAS, 39.00 MMBTU | 13.31 | NATURAL GAS | 365 | MMSCF/YR | Boiler has MDHI of 39.00 mmbtu and combusts natural gas only. | Nitrogen Oxides (NOx) | A | LOW-NOX BURNERS/FLUE-GAS RECIRCULATION | 2.08 | PPH |  | 9.13 | T/YR |  | 0.05 | LB/MMBTU
CO-0058 | CHEYENNE STATION | CHEYENNE PLAINS GAS PIPELINE COMPANY | CO | COLORADO DEPT OF HEALTH - AIR POLL CTRL | 2004-06-12 | 2004 | COMPRESSOR STATION | HEATERS | 13.31 | NATURAL GAS | 45 | MMBTU/H | TWO HOT OIL HEATERS RATED AT 45 MMBTU/HR AND ONE UTILITY HEATER RATED AT 16 MMBTU/HR. THE HEATERS ARE INCLUDED IN PERMIT 03WE0913. | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.035 | LB/MMBTU | 1-HR AVERAGE |  |  |  | 0.035 | LB/MMBTU
WI-0223 | LOUISIANA-PACIFIC HAYWARD | LOUISIANA-PACIFIC CORPORATION | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-06-17 | 2004 | OSB MILL | THERMAL OIL HEATER, GTS ENERGY, S31, B31 | 13.31 | NATURAL GAS | 32 | MMBTU/H | STACK S31; BOILER B31 - GTS ENERGY THERMAL OIL HEATER RATED AT 32.0 MILLION BTU PER HOUR WHEN BURNING NATURAL GAS AND 30.0 MILLION BTU PER HOUR WHEN BURNING DISTILLATE FUEL OIL | Nitrogen Oxides (NOx) | P | USE OF NATURAL GAS / DISTILLATE OIL, W/ RESTRICTION ON OIL USAGE | 4.24 | LB/H |  |  |  |  | 0.13 | LB/MMBTU | CALCULATED, NOT PERMIT LIMIT
WI-0223 | LOUISIANA-PACIFIC HAYWARD | LOUISIANA-PACIFIC CORPORATION | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-06-17 | 2004 | OSB MILL | THERMAL OIL HEATER, GTS ENERGY, S32, B32 | 13.31 | NATURAL GAS | 32 | MMBTU/H | STACK S32; BOILER B32 - GTS ENERGY THERMAL OIL HEATER RATED AT 32.0 MILLION BTU PER HOUR WHEN BURNING NATURAL GAS AND 30.0 MILLION BTU PER HOUR WHEN BURNING DISTILLATE FUEL OIL. | Nitrogen Oxides (NOx) | P | USE OF NATURAL GAS / DISTILLATE OIL, W/ RESTRICTION ON OIL USAGE | 3.2 | LB/H |  |  |  |  | 0.1 | LB/MMBTU | CALCULATED, NOT PERMIT LIMIT
*NE-0023 | BEATRICE POWER STATION | NEBRASKA PUBLIC POWER DISTRICT | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2004-06-22 | 2004 | PERMIT TO CONSTRUCT: 2-NG TURBINES, 250 MW TOTAL AND ONE AUX. BOILER, 73 MMBTU/HR, OIL FIRED | AUXILIARY BOILER (NG) | 13.31 | OIL/NG | 73.3 | MMBTU/H | THIS UNIT CAN BURN UP TO 289,000 GAL/YR OF DISTILATE OIL. SEE THE PROCEESS AUXILIARY BOILER (OIL) FOR EMISSION LIMITS WHILE BURNING DISTILATE OIL. | Nitrogen Oxides (NOx) | N | OPERATION LIMITED TO 500 HOURS PER YEAR. | 0.05 | LB/MMBTU | 3 HOUR TEST AVG |  |  |  | 0.05 | LB/MMBTU | 3 HOUR TEST AVG | OPERATION LIMITED TO 500 HOURS PER YEAR. THIS UNIT CAN BURN UP TO 289,000 GAL/YR OF DISTILATE OIL. SEE THE PROCEESS AUXILIARY BOILER (OIL) FOR EMISSION LIMITS WHILE BURNING DISTILATE OIL.
NE-0026 | NUCOR STEEL DIVISION | NUCOR STEEL CORP. | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2004-06-22 | 2004 |  | NNII REHEAT FURNACE | 13.31 | NATURAL GAS | 143 | MMBTU/H |  | Nitrogen Oxides (NOx) | A | ULTRA-LOW NOX BURNERS | 0.064 | LB/MMBTU |  |  |  |  | 0.064 | LB/MMBTU
NE-0026 | NUCOR STEEL DIVISION | NUCOR STEEL CORP. | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2004-06-22 | 2004 |  | NNII BILET POST-HEATER | 13.31 | NATURAL GAS | 6.8 | MMBTU/H |  | Nitrogen Oxides (NOx) | A | ULTRA-LOW NOX BURNERS | 0.147 | LB/MMBTU |  |  |  |  | 0.147 | LB/MMBTU
AR-0077 | BLUEWATER PROJECT | STEELCORR, INC. | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-07-22 | 2004 | THE FACILITY IS A NEW SPECIALTY STEEL MILL PRODUCING VARIOUS HOT ROLLED, COLD ROLLED AND GALVANIZED PRODUCTS FOR VARIOUS END USE MARKETS. AFIN: 47-00541 | BOILERS | 13.31 | NATURAL GAS | 22 | MMBTU/H | ENTRY INCLUDES TWO BOILERS. THE 22 MMBTU/H PICKLE LINE BOILER, 51 MMBTU/H VACUUM DEGASSER BOILERS. | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS | 0.08 | LB/MMBTU |  |  |  |  | 0.08 | LB/MMBTU
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | 2004 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, NATURAL GAS (1) | 13.31 | NATURAL GAS | 40 | MMBTU/H | AUXILIARY BOILER. | Nitrogen Dioxide (NO2) | P | LOW NOX BURNER; FGR. | 0.04 | LB/MMBTU | 3 HOUR AVERAGE |  |  |  | 0.04 | LB/MMBTU
WI-0226 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE (WPS) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-08-27 | 2004 | ELECTRIC UTILITY | NATURAL GAS FIRED BOILER | 13.31 | NATURAL GAS | 46.2 | MMBTU/H | NOT PSD | Nitrogen Oxides (NOx) | P | BURNER DESIGN, NATURAL GAS FUELED | 1.67 | LB/H | 3,300 HR / ROLLING 12 MO. |  |  |  | 0.036 | LB/MMBTU |  | NATURAL GAS FIRED, 46.2 MMBTU/HR BOILER 1.22 LBS NOX / HR @ 37.1 MMBTU/HR (0.033 LBS/MMBTU)
WI-0227 | PORT WASHINGTON GENERATING STATION | WE ENERGIES (WEPCO) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-13 | 2004 | ELECTRIC GENERATION | NATURAL GAS FIRED AUXILLIARY BOILER | 13.31 | NATURAL GAS | 97.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | NATURAL GAS FUEL, COMBUSTION OPTIMIZATION (BASED ON CAPACITY FACTOR DURING OZONE SEASON EXCEEDING 20%) | 13.7 | LB/H |  |  |  |  | 0.141 | LB/MMBTU | CALCULATED | IF CAPACITY FACTOR DURING THE OZONE SEASON EXCEEDS 20%, THE FACILITY SHALL CONDUCT A COMBUSTION OPTIIMIZATION (IN ACCORDANCE WITH CH. NR 439, NOX RACT). NOT SUBJECT TO PSD BACT, AS THE INCREASE WAS OFFSET BY ADDITIONAL REDUCTIONS FROM THE COMBUSTION TURBI
WI-0227 | PORT WASHINGTON GENERATING STATION | WE ENERGIES (WEPCO) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-13 | 2004 | ELECTRIC GENERATION | GAS HEATER (P06, S06) | 13.31 | NATURAL GAS | 10 | MMBTU/H | GAS CONDITIONING HEATER | Nitrogen Oxides (NOx) | P | NATURAL GAS FUEL | 0.1 | LBS/MMBTU |  | 0.36 | LB/H |  | 0.1 | LBS/MMBTU
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | B63, S63; B64, S64 - NATURAL GAS STATION HEATER 1 AND 2 | 13.31 | NATURAL GAS | 0.75 | MMBTU/H | EMISSION LIMITS ARE THOSE FOR EACH UNIT. | Nitrogen Oxides (NOx) | P | NATURAL GAS | 0.073 | LB/H |  |  |  |  | 0.097333 | LBS/MMBTU | NOT AVAILABLE | (LIMIT IS FOR EACH UNIT)
NV-0042 | CAPITAL CABINET CORPORATION | CAPITAL CABINET CORPORATION | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2004-11-05 | 2004 | A WOOD CABINETS AND COUNTER TOPS MANUFACTURING PLANT | FUEL COMBUSTION | 13.31 | NATURAL GAS | 8.8 | MMBTU/H | THE PROCESS EQUIPMENT CONSISTS OF SIX (6) FUEL COMBUSTION UNITS, THREE ARE MAKE-UP AIR HEATERS, EACH RATED AT 2.592 MMBTU/HR, TWO ARE FURNACES, EACH RATED AT 0.15 MMBTU/HR, ONE IS WATER HEATER RATED AT 0.722 MMBTU/HR. | Nitrogen Oxides (NOx) | P | USE OF NATURAL GAS AS THE ONLY FUEL FOR ALL THE COMBUSTION UNITS | 0.5 | T/MO | PER CALENDAR MONTH | 3.81 | T/YR | PER ROLLING 12-MONTH PERIOD. |  |  |  | THESE ARE FACILITY-WIDE EMISSION LIMITS. FOR COMBUSTION UNITS B03, B04, AND B08, EACH HAS AN ANNUAL EMISSION LIMIT OF 1.12 TONS PER YEAR.
AL-0212 | HYUNDAI MOTOR MANUFACTURING ALABAMA, LLC | HYUNDAI MOTOR MANUFACTURING ALABAMA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2004-11-22 | 2004 | AUTOMOBILE MANUFACTURING PLANT | BOILER, NATURAL GAS (2) | 13.31 | NATURAL GAS | 24.5 | mmbtu/h | THROUGHPUT FOR EACH BOILER. PREVIOUS CONSTRUCTION PERMIT ISSUED (10/02) FOR THREE 50.0 MMBTU/H BOILERS. THIS IS A MODIFICATION | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS | 0.35 | LB/MMBTU |  |  |  |  | 0.35 | LB/MMBTU
AZ-0047 | WELLTON MOHAWK GENERATING STATION | DOME VALLEY ENERGY PARTNERS | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2004-12-01 | 2004 | COMBINED CYCLE GAS-FIRED ELECTRICITY GENERATING STATION | AUXILIARY BOILER | 13.31 | NATURAL GAS | 38 | MMBTU/H |  | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS | 0.37 | LB/MMBTU | BASED ON HIGHER HEATING VALUE OF FUEL |  |  |  | 0.37 | LB/MMBTU
OH-0252 | DUKE ENERGY HANGING ROCK ENERGY FACILITY | DUKE ENERGY HANGING ROCK, LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2004-12-28 | 2004 | FOUR NATURAL GAS (NG) FIRED COMBUSTION TURBINES, WITH DUCT BURNERS; COMBINED CYCLE, EACH 172 MW | BOILERS (2) | 13.31 | NATURAL GAS | 30.6 | MMBTU/H | LIMITS ARE FOR EACH BOILER INDIVIDUALLY. THE MAXIMUM FUEL HEAT INPUT SHALL NOT EXCEED 91,500 MMBTU/ROLLING 12-MONTHS FOR EACH BOILER. | Nitrogen Oxides (NOx) | N |  | 1.07 | LB/H | EACH BOILER | 1.6 | T/ROLLING 12-MONTHS | EACH BOILER | 0.035 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
WA-0301 | BP CHERRY POINT REFINERY | BRITISH PETROLEUM | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2005-04-20 | 2005 | BRITISH PETROLEUM (BP), FORMERLY KNOWN AS ARCO PRODUCTS COMPANY OPERATES A REFINERY AT CHERRY POINT NEAR BLAINE, WASHINGTON. THE REFINERY IS LOCATED IN A RURAL SETTING NEAR BLAINE AND BIRCH BAY WASHINGTON. THE SURROUNDING LAND USE IS ZONED HEAVY IMPACT IN | PROCESS HEATER, IHT | 13.31 | NATURAL GAS | 13 | MMBTU/H | Isom hydrotreater (IHT) process heater | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 0.1 | LB/MMBTU | 7% O2, 24 hr ave | 0.455 | LB/H | 24 hr ave | 0.1 | LB/MMBTU
LA-0192 | CRESCENT CITY POWER | CRESENT CITY POWER, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-06-06 | 2005 | NEW 600 MW NATURAL GAS-FIRED COMBINED CYCLE POWER PLANT | FUEL GAS HEATERS (3) | 13.31 |  | 19 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND GOOD COMBUSTION PRACTICES | 1.81 | LB/H | HOURLY MAXIMUM | 0.68 | T/YR | *SEE NOTES. ANNUAL MAXIMUM | 0.095 | LB/MMBTU | ANNUAL AVERAGE | *TPY LIMIT FOR ALL 3 HEATERS. AGGREGATE HEAT INPUT IS LIMITED TO 14,250 MM BTU/YR. ONLY 2 OF THE 3 HEATERS ARE ALLOWED TO OPERATE AT ANY GIVEN TIME.
LA-0203 | OAKDALE OSB PLANT | MARTCO LIMITED PARTNERSHIP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-06-13 | 2005 | PSD FOR A NEW ORIENTED STRAND BOARD (OSB) MANUFACTURING FACILITY CAPABLE OF PRODUCING 900,000 MSF 3/8 INCH OSB PER YEAR. | AUXILIARY THERMAL OIL HEATER | 13.31 | NATURAL GAS | 66.5 | MMBTU/H | OPERATING TIME = 500 HR/YR. | Nitrogen Oxides (NOx) | P | USE OF NATURAL GAS AS FUEL AND GOOD COMBUSTION PRACTICES | 7.82 | LB/H | HOURLY MAXIMUM |  |  |  | 0.118 | LB/MMBTU | CALCULATED BY CATC
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-07-27 | 2005 | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | CRACKING FURNACES A-D | 13.31 |  | 90 | MMBTU/H EA. |  | Nitrogen Oxides (NOx) | B | LOW NOX BURNERS AND SELECTIVE CATALYTIC REDUCTION (SCR) | 0.009 | LB/MMBTU |  |  |  |  | 0.009 | LB/MMBTU | THREE ONE-HOUR TEST AVERAGE
MD-0035 | DOMINION | DOMINION COVE POINT LNG, L.P. | MD | MARYLAND DEPARTMENT OF THE ENVIRONMENT | 2005-08-12 | 2005 | LNG FACILITY | VAPORIZATION HEATER | 13.31 | NATURAL GAS |  |  | SEVEN VAPORIZATION HEATERS; RATED HEAT INPUT IS 88.4 MMBTU/H FOR EACH UNIT; EMISSION LIMITS APPLY TO EACH UNIT | Nitrogen Oxides (NOx) | A | ULNB | 0.012 | LB/MMBTU |  | 9 | PPMVD |  | 0.012 | LB/MMBTU
MD-0035 | DOMINION | DOMINION COVE POINT LNG, L.P. | MD | MARYLAND DEPARTMENT OF THE ENVIRONMENT | 2005-08-12 | 2005 | LNG FACILITY | EMERGENCY VENT HEATER | 13.31 | NATURAL GAS |  |  | ONE 1.3 MMBTU/HR EMERGENCY VENT HEATER | Nitrogen Oxides (NOx) | A | LNB | 0.036 | LB/MMBTU | 3-HOUR AVERAGE |  |  |  | 0.036 | LB/MMBTU
AK-0062 | BADAMI DEVELOPMENT FACILITY | BP EXPLORATION ALASKA | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2005-08-19 | 2005 | OIL AND GAS PROCESSING FACILITY | NATCO PRODUCTION HEATER | 13.31 | NATURAL GAS | 34 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS / FLUE GAS RECIRCULATION | 0.095 | LB/MMBTU |  |  |  |  | 0.095 | LB/MMBTU | *SEE NOTES | LOW NOX BURNERS / FLUE GAS RECIRCULATION
AK-0062 | BADAMI DEVELOPMENT FACILITY | BP EXPLORATION ALASKA | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2005-08-19 | 2005 | OIL AND GAS PROCESSING FACILITY | NATCO TEG REBOILER | 13.31 | NATURAL GAS | 1.34 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | CONVENTIONAL BURNER TECHNOLOGY | 0.08 | LB/MMBTU |  |  |  |  | 0.08 | LB/MMBTU | *SEE NOTES | CONVENTIONAL BURNER TECHNOLOGY
CA-1127 | GENENTECH, INC. | GENENTECH, INC. | CA | BAY AREA AQMD, CA | 2005-09-27 | 2005 |  | BOILER: >= 50 MMBTU/H | 13.31 | NATURAL GAS | 97 | MMBTU/H | EQUIP: WATERTUBE, MFR: NEBRASKA BOILER, INC., TYPE: STEAM BOILER, MODEL: NS-E-64-ST-CA-HM-AL, FUNC EQUIP: PROVIDE STEAM AND HOT WATER., FUEL_TYPE: MAY INSTALL DIESEL OIL BACKUP IN FUTURE., SCHEDULE: CONTINUOUS, H/D: 24, D/W: 7, W/Y: 52, NOTES: THREE IDENT | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS: NATCOM P-97-LOG-35-2127 | 9 | PPMVD @ 3% O2 | THREE 30-MIN SAMP PERIODS AV
MD-0036 | DOMINION | DOMINION COVE POINT LNG, L.P. | MD | MARYLAND DEPARTMENT OF THE ENVIRONMENT | 2006-03-10 | 2006 | LNG FACILITY | FUEL GAS PROCESS HEATER | 13.31 | NATURAL GAS |  |  | ENGINEERING TECH NO. IDHLE 1.0; 0.93 MMBTU/HR | Nitrogen Dioxide (NO2) | B | DRY LNB AND GOOD COMBUSTION PRACTICES | 17 | PPMVD | 3-HOUR AVERAGE | [6 empty] | 17 PPMVD (CORRECTED TO 3% O2)
MD-0036 | DOMINION | DOMINION COVE POINT LNG, L.P. | MD | MARYLAND DEPARTMENT OF THE ENVIRONMENT | 2006-03-10 | 2006 | LNG FACILITY | FUEL GAS PROCESS HEATER | 13.31 | NATURAL GAS |  |  | ENGINEERING TECH NO. IDHLE 1.0; 0.93 MMBTU/HR | Nitrogen Oxides (NOx) | B | GOOD COMBUSTION PRACTICES AND DRY LNB | 17 | PPMVD | 3-HOUR AVERAGE | [6 empty] | 17 PPMVD (CORRECTED TO 3% O2)
CA-1128 | COTTAGE HEALTH CARE - PUEBLO STREET | COTTAGE HEALTH CARE - PUEBLO STREET | CA | SANTA BARBARA COUNTY APCD, CA | 2006-05-16 | 2006 |  | BOILER: 5 TO < 33.5 MMBTU/H | 13.31 | NATURAL GAS | 25 | MMBTU/H (75 MMBTU/H TOTAL) | EQUIP: THREE 25 MMBTU/H STEAM BOILERS WITH FUEL OIL (AMBER 363) BACKUP, MFR: CLEAVER-BROOKS, TYPE: STEAM BOILER, MODEL: 4WI700-600-150ST, FUNC EQUIP: PROVIDES HEAT TO A NEW HOSPITAL, FUEL_TYPE: BACKUP WITH AMBER 363 (BACT) UP TO 192 HRS/YR, SCHEDULE: CONT | Nitrogen Oxides (NOx) | A | ULTRA-LOW NOX BURNER | 9 | PPMV AT 3% O2 | 6-MIN AV
*NV-0046 | GOODSPRINGS COMPRESSOR STATION | KERN RIVER GAS TRANSMISSION COMPANY | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2006-05-16 | 2006 | THE FACILITY IS A COMPRESSOR STATION ON AN INTER-STATE PIPELINE FOR TRANSPORTING NATURAL GAS. THE FACILITY IS A MAJOR STATIONARY SOURCE FOR NITROGEN OXIDES IN A NON-ATTAINMENT AREA FOR OZONE AIR QUALITY. | COMMERCIAL/INSTITUTIONAL BOILER | 13.31 | NATURAL GAS | 3.85 | MMBTU/H | THE UNIT'S MODEL IDENTIFICATION IS PEERLESS 724 FDA WU. | Nitrogen Oxides (NOx) | P | GOOD COMBUSTION PRACTICE | 0.101 | LB/MMBTU |  | 1.69 | T/YR |  | 0.101 | LB/MMBTU
NV-0044 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S ENTERTAINMENT | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2007-01-04 | 2007 | THE FACILITY IS A NEW MAJOR STATIONARY SOURCE FOR NITROGEN OXIDES AS A RESULT OF CONSOLIDATING SIX LARGE HOTEL/CASINO RESORTS, WHICH ARE HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. | COMMERCIAL/INSTITUTIONAL-SIZE BOILERS | 13.31 | NATURAL GAS | 35.4 | MMBTU/H | THE BACT DETERMINATIONS REPORTED HERIN ARE SPECIFICALLY FOR THE TWO HURST BOILERS INSTALLED AT CAESAR'S PALACE. EACH OF THEM HAS A RATED HEAT INPUT OF 35.4 MMBTU/HR. THE PERMITTING ACTION ALSO APPROVED THE INSTALLATION OF A NUMBER OF SMALL BOILERS, ALL OF | Nitrogen Oxides (NOx) | B | LOW-NOX BURNER AND FLUE GAS RECIRCULATION | 0.035 | LB/MMBTU |  | 29 | PPMVD | 3% OXYGEN | 0.035 | LB/MMBTU |  | PPMVD" STANDS FOR PARTS PER MILLION BY VOLUME ON A DRY BASIS. THE DATA PERTAIN TO EITHER ONE OF THE HURST BOILERS | WHICH RATED HEAT INPUT IS 35.4 MMBTU/H."
*NC-0115 | NC COMMUNICATION TECH |  | NC | NORTH CAROLINA DIV OF ENV MGMT | 2007-01-06 | 2007 |  | DRYER OR OVEN, DIRECT OR INDIRECT | 13.31 | NATURAL GAS | 5.4 | MMBTU/H | ANY OTHER INFORMATION THAT WILL HELP US TO BETTER UNDERSTAND | Nitrogen Oxides (NOx) | A | LOW NOX -BURNER | 18 | PPMVD@3%O2
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | 2007 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NATURAL GAS | 13.31 | NATURAL GAS | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. WITH #2 OIL BACKUP TWO SET OF LIMITS, THIS ONE FOR NATURAL GAS | Nitrogen Oxides (NOx) | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 0.72 | LB/H |  | 3.5 | T/YR |  | 0.035 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
*AL-0231 | NUCOR DECATUR LLC | NUCOR CORPORATION | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-06-12 | 2007 | THE FACILITY PRODUCES STEEL COILS PRIMARILY FROM STEEL SCRAP USING THE ELECTRIC ARC FURNACE (EAF) PROCESS. | VACUUM DEGASSER BOILER | 13.31 | NATURAL GAS | 95 | MMBTU/H |  | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 0.035 | LB/MMBTU |  | 3.33 | LB/H |  | 0.035 | LB/MMBTU
*AL-0231 | NUCOR DECATUR LLC | NUCOR CORPORATION | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-06-12 | 2007 | THE FACILITY PRODUCES STEEL COILS PRIMARILY FROM STEEL SCRAP USING THE ELECTRIC ARC FURNACE (EAF) PROCESS. | GALVANIZING LINE FURNACE | 13.31 | NATURAL GAS | 98.7 | MMBTU/H |  | Nitrogen Oxides (NOx) | A | SCR | 0.067 | LB/MMBTU |  | 6.6 | LB/H |  | 0.067 | LB/MMBTU
IA-0088 | ADM CORN PROCESSING - CEDAR RAPIDS | ARCHER DANIELS MIDLAND | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-06-29 | 2007 | CONSISTS OF THREE DISTINCT OPERATIONS: CORN WET MILL, CORN DRY MILL AND BOILERHOUSE | INDIRECT-FIRED DDGS DRYER | 13.31 | NATURAL GAS | 93.7 | MMBTU/H | PROJECT INCLUDES THE INSTALLATION OF EIGHT IDENTICAL DDGS DRYERS. PERMITS 07-A-546-P, 547, 548, 549, 550, 557, 558 AND 559. THE COMBUSTION CHAMBER AND THE FEED CHAMBER ARE SEPERATED BY A HEAT EXCHANGER. THE DRYERS CAN FIRE NATURAL GAS, BIOGAS FROM THE WWT | Nitrogen Oxides (NOx) | A | LOW NOX BURNERS WITH FLUE GAS RECIRCULATION | 0.04 | LB/MMBTU | AVERAGE OF 3 TEST RUNS |  |  |  | 0.04 | LB/MMBTU
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED BATCH ANNEALING FURNACE (535) | 13.31 | NATURAL GAS | 99 | MMBTU/H | THIS PROCESS IS COVERED UNDER 503-0095-X005. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS | 0.11 | LB/MMBTU |  | 10.89 | LB/H |  | 0.11 | LB/MMBTU
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED PASSIVE ANNEALING FURNACE (LO41) | 13.31 | NATURAL GAS | 27.2 | MMBTU/H | THIS PROCESS IS COVERED UNDER 503-0095-X013. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS (ULNB) WITH EXHAUST GAS RECIRCULATION (EGR) | 0.11 | LB/MMBTU |  | 2.99 | LB/H |  | 0.11 | LB/MMBTU
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED PASSIVE ANNEALING FURNACE (LO41) | 13.31 | NATURAL GAS | 27.2 | MMBTU/H | THIS PROCESS IS COVERED UNDER 503-0095-X013. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Nitrogen Oxides (NOx) | P | ULTRA LOW NOX BURNERS (ULNB) WITH EXHAUST GAS RECIRCULATION | 0.11 | LB/MMBTU |  | 2.99 | LB/H |  | 0.11 | LB/MMBTU
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED BATCH ANNEALING FURNACES (LA63, LA64) | 13.31 | NATURAL GAS | 33.4 | MMBTU each | THIS PROCESS IS COVERED UNDER 503-0095-X014. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Nitrogen Oxides (NOx) | P | UNLB WITH EGR | 0.11 | LB/MMBTU |  | 3.68 | LB/H |  | 0.11 | LB/MMBTU
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | 3 NATURAL GAS-FIRED BOILERS WITH ULNB & EGR (537-539) | 13.31 | NATURAL GAS | 64.9 | MMBtu each | THIS PROCESS IS COVERED UNDER 503-0095-X026. | Nitrogen Oxides (NOx) | P | ULNB & EGR | 0.035 | LB/MMBTU |  | 2.27 | LB/H |  | 0.035 | LB/MMBTU
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 8 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 50 | MMBTU/H | THE NUMBER 8 PAPER MACHINE CONSISTS OF THREE SOURCES: THE NATURAL GAS FIRED BURNERS, THE PAPER MACHINE, AND THE DUST SYSTEM. STACK TESTING FOR CO AND NOX. | Particulate Matter (PM) | P | CLEAN FUEL | 0.164 | LB/MMBTU |  | 0 |  |  | 0.164 | LB/MMBTU
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 5 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 21 | MMBTU/H | THE BURNERS FOR THE NUMBER 5 PAPER MACHINE HAVE BEEN UPGRADED. | Particulate Matter (PM) | P | CLEAN FUEL | 0.0164 | LB/MMBTU |  | 0 |  |  | 0.0164 | LB/MMBTU
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 6 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 58.4 | MMBTU/H | THE BURNERS FOR THE NUMBER 6 PAPER MACHINE HAVE BEEN UPGRADED. | Particulate Matter (PM) | P | CLEAN FUEL | 0.0164 | LB/MMBTU |  | 0 |  |  | 0.0164 | LB/MMBTU
KY-0068 | TOYOTA MOTOR MANUFACTURING, USA, INC | TOYOTA MOTOR MANUFACTURING, USA, INC | KY | KENTUCKY DEP, DIV FOR AIR QUALITY | 1997-05-29 | 1997 | MODIFICATION OF AN AUTOMOBILE ASSEMBLY PLANT (THIRD REVISION OF PERMIT) | BOILER (NATURAL GAS) | 13.31 | NATURAL GAS | 96 | MMBTU/H | A SEPARATELY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING FUEL OIL (BACKUP FUEL). WHEN FIRING NATURAL GAS, ANNUAL OPERATING HOURS SHALL NOT EXCEED 6132 H/YR. | Particulate Matter (PM) | A | FABRIC FILTER | 0.1 | LB/MMBTU |  |  |  |  | 0.1 | LB/MMBTU |  | THE OUTLET PARTICULATE CONCENTRATION FROM EACH FABRIC FILTER CONTROL DEVICE SHALL NOT EXCEED 0.003 GR PER ACF.
AL-0139 | ANNISTON ARMY DEPOT | U.S. ARMY - ANNISTON ARMY DEPOT | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-06-19 | 1997 |  | BOILER, NATURAL GAS FIRED, 2 | 13.31 | NATURAL GAS | 13.4 | MMBTU/H |  | Particulate Matter (PM) | P | CLEAN FUEL. | 0.0076 | LB/MMBTU |  |  |  |  | 0.0076 | LB/MMBTU
AL-0140 | ANNISTON ARMY DEPOT | U.S. ARMY - ANNISTON ARMY DEPOT | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-06-19 | 1997 |  | BOILER, NATURAL GAS FIRED, 2 | 13.31 | NATURAL GAS | 11.7 | MMBTU/H |  | Particulate Matter (PM) | P | CLEAN FUEL | 0.0076 | LB/MMBTU |  |  |  |  | 0.0076 | LB/MMBTU
WI-0188 | GOLDEN BOOKS PUBLISHING COMPANY INC. | GOLDEN BOOKS PUBLISHING COMPANY INC. | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 1997-06-24 | 1997 | PRINTING FACILITY | SPACE HEAT & COMBUSTION SOURCES, (P01 S01) | 13.31 | NATURAL GAS | 93 | MMBTU/H | SECOND FUEL: PROPANE | Particulate Matter (PM) | P | SECTION NR 415.05 (2) WIS.ADM.CODE. EMISSION LIMIT IS 0.15 LB/MMBTU OR 13.95 LB/H. IN ORDER TO PROTECT THE PM AMBIENT AIR QUALITY STANDARDS THE LIMIT IS SET AT 1.25 LB/H | 1.25 | LB/H |  |  |  |  | 0.013 | LB/MMBTU
WY-0034 | SOLVAY SODA ASH JOINT VENTURE TRONA MINE/SODA ASH | SOLVAY SODA ASH JOINT VENTURE TRONA MINE/SODA ASH | WY | WYOMING AIR QUAL DIV, DEPT OF ENV QUAL | 1998-02-06 | 1998 |  | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 100 | MMBTU/H | HEATING MINE VENTILATION AIR | Particulate Matter (PM) | N | MINIMAL PARTICULATE EMISSIONS AND LOW EMITTING FUEL | 5 | LB/MMBTU |  | 0
IA-0048 | CARGILL INC - SIOUX CITY | CARGILL INC - SIOUX CITY | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1998-06-01 | 1998 | SOYBEAN OIL MILL | BOILER, BACKUP | 13.31 |  | 77 | MMBTU/H | PERMIT NUMBER FOR THIS PROCESS IS 86-A-036-S1. permit for PM/PM10 and NOx only | Particulate Matter (PM) | N |  | 0.7 | LB/H |  | 3 | LB/MMCF |  | 0.009 | LB/MMBTU |  | 500 H/YR RESTRICTION - THE ONLY REVISION MADE TO THE EXISTING PERMIT.
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | 1998 | VEGETABLE OIL PLANT | BOILER, NEBRASKA, NAT GAS | 13.31 | NATURAL GAS | 28 | MMBTU/H | See separate process for backup fuel (No. 2 oil) requirements. | Particulate Matter (PM) | N |  | 2.4 | LB/H |  | 0.1 | LB/MMBTU |  | 0.1 | LB/MMBTU
WI-0161 | AARROW CAST | AARROW CAST | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 1998-10-01 | 1998 |  | CORE WASH OVEN, S07 | 13.3 | NATURAL GAS | 10 | MMBTU/H | Limit required for PM and VE only | Particulate Matter (PM) | P | BACT FOR THIS PROCESS IS THE COMBUSTION OF NATURAL GAS. | 0.15 | LB/MMBTU |  |  |  |  | 0.15 | LB/MMBTU
GA-0080 | RAYONIER, INC.- SWAINSBORO | RAYONIER, INC. - SWAINSBORO | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 1998-11-05 | 1998 | LUMBER MILL | OIL HEATER OH-1 | 13.31 | NATURAL GAS | 75 | MMBTU/H | HOT OIL HEATER FIRES NATURAL GAS WITH THE CAPABILITY OF FIRING NO. 2 FUEL OIL. | Particulate Matter (PM) | P | FUEL LIMITATIONS, SEE POLLUTANT NOTES. |  |  | SEE POLLUTANT NOTES | [6 empty] | NOT TO EMIT GASES WITH PARTICULATE CONTENT EXCEEDING RATE CALCULATED THUS: E=0.5*(10/R) ^0.5, WHERE E=ALLOWABLE EMISSION RATE IN LB/MMBTU, AND R= HEAT INPUT IN MMBTU/H
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | WASTE HEAT RECOVERY, UNIT 10 | 13.31 | NATURAL GAS | 52.8 | MMBTU/H | MAXIMUM OPERATION DURING COMMISSIONING PERIOD: 1848 H MAXIMUM OPERATION AFTER COMMISSIONING PERIOD: 1000 H UNDER NORMAL LONG-TERM OPERATIONS, THE WASTE HEAT RECOVERY SUPPLEMENTAL BURNER WILL NOT BE OPERATED. OPERATION OF THIS BURNER IS UNDER AN ALTERNATIV | Particulate Matter (PM) | P | GOOD OPERATION PRACTICES. | 0.05 | GR/DSCF | AVERAGED OVER 3 HOURS |  |  |  | 0.0072 | LB/MMBTU | CALCULATED- SEE BELOW | BACT IS TO COMPLY WITH STATE STANDARDS 18 AAC 50.055. EMISSIONS IN LB/MMBTU WERE CALCULATED USING THE FOLLOWING CONVERSION FACTORS: 1 DSCF NATURAL GAS = 1000 BTU AND 1 GR = .000143 LB.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | GLYCOL REBOILER, UNIT 13 | 13.31 | NATURAL GAS | 5 | MMBTU/H | MAXIMUM OPERATION DURING COMMISSIONING PERIOD: 1848 H. MAXIMUM OPERATION AFTER COMMISSIONING PERIOD: 8760 H/YR. | Particulate Matter (PM) | N |  | 0.05 | GR/DSCF | AV OVER 3 H |  |  |  | 0.0072 | LB/MMBTU | CALCULATED- SEE NOTE | BACT IS TO COMPLY WITH STATE STANDARD 18 AAC 50.055. EMISSIONS IN LB/MMBTU WERE CALCULATED USING THE FOLLOWING CONVERSION FACTORS: 1000 BTU = 1 DSCF NATURAL GAS AND 0.000143 LB = 1 GR.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | GLYCOL SKID HEATER (NATURAL GAS), UNIT NO. 14 | 13.31 | NATURAL GAS | 1.05 | MMBTU/H | SECOND FUEL FOR GLYCOL SKID HEATER IS DIESEL- LISTED SEPARATELY. MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. | Particulate Matter (PM) | N | NONE INDICATED. | 0.05 | GR/DSCF |  |  |  |  | 0.0072 | LB/MMBTU | CALCULATED- SEE NOTES | BACT IS TO COMPLY WITH STATE STANDARD 18 AAC 50.055. EMISSIONS IN LB/MMBTU CONVERTED USING FOLLOWING CONVERSION FACTORS; 1 DSCF NATURAL GAS = 1000 BTU, AND 1 GR = 0.000143 LB.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | SPACE HEATER, WAREHOUSE, UNIT NO. 15, 16 | 13.31 | NATURAL GAS | 0.5 | MMBTU/H | MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. | Particulate Matter (PM) | P | GOOD OPERATION PRACTICES | 0.05 | GR/DSCF |  |  |  |  | 0.0072 | LB/MMBTU | CALCULATED, SEE NOTES | BACT IS TO COMPLY WITH STATE STANDARD 18 AAC 50.055. EMISSIONS IN LB/MMBTU WERE CALCULATED USING THE FOLLOWING CONVERSION FACTORS: 1 DSCF NATURAL GAS = 1000 BTU, AND 0.000143 LB = 1 GR.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | SPACE HEATER, WAREHOUSE, UNIT NO. 17 | 13.31 | NATURAL GAS | 0.63 | MMBTU/H | MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. | Particulate Matter (PM) | P | GOOD OPERATION PRACTICES. | 0.05 | GR/DSCF |  |  |  |  | 0.0072 | LB/MMBTU | CALCULATED- SEE NOTES | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055. EMISSIONS IN LB/MMBTU WERE CALCULATED USING THE FOLLOWING CONVERSION FACTORS: 1 DSCF NATURAL GAS = 1000 BTU, AND 0.000143 LB = 1 GR.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | SPACE HEATER, WAREHOUSE, UNIT NO. 18 | 13.31 | NATURAL GAS | 1.06 | MMBTU/H | MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. | Particulate Matter (PM) | P | GOOD OPERATIONS PRACTICES. | 0.05 | GR/DSCF | AVERAGED OVER 3 H |  |  |  | 0.0072 | LB/MMBTU | CALCULATED- SEE NOTE | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055. EMISSIONS IN LB/MMBTU WERE CALCULATED USING THE FOLLOWING CONVERSION FACTORS; 1 DSCF NATURAL GAS = 1000 BTU, AND 1 GR = 0.000143.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | RIG BOILER (NATURAL GAS), UNIT 206, 207 | 13.31 | NATURAL GAS | 6.3 | MMBTU/H | PERMIT LISTS UNIT 206 AND 207 WITH NATURAL GAS AND DIESEL, LISTED SEPARATELY IN DATABASE. TYPICAL OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 924 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. DURING PRE- SEALFIT PERIOD AND COMMI | Particulate Matter (PM) | P | GOOD OPERATIONS PRACTICES | 0.05 | GR/DSCF | AV OVER 3 H |  |  |  | 0.0072 | LB/MMBTU | CONVERTED- SEE NOTES | EMISSIONS IN LB/MMBTU WERE CONVERTED USING THE FOLLOWING CONVERSION FACTORS: 1 DSCF NATURAL GAS = 1000 BTU, AND 0.000143 LB = 1 GR. BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATER (NATURAL GAS), UNIT 208, 209 | 13.31 | NATURAL GAS | 3.5 | MMBTU/H | UNITS 208 AND 209 ARE LISTED IN PERMIT AS BURNING BOTH NATURAL GAS AND DIESEL FUEL. THESE ARE LISTED SEPARATELY IN DATABASE. DURING PRE-SEALIFT PERIOD AND COMMISSIONING PERIOD, UNITS MAY BE OPERATED WITH NATURAL GAS OR DIESEL FOR THE SAME AMOUNT OF TIME. | Particulate Matter (PM) | P | GOOD OPERATIONS PRACTICES | 0.05 | GR/DSCF | AVERAGED OVER 3 H |  |  |  | 0.0072 | LB/MMBTU | CALCULATED- SEE NOTES | EMISSIONS IN LB/MMBTU WERE CALCULATED USING THE FOLLOWING CONVERSION FACTORS: 1 DSCF NATURAL GAS = 1000 BTU, AND 0.000143 LB = 1 GR. BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATER (NATURAL GAS), UNIT 210 | 13.31 | NATURAL GAS | 4.2 | MMBTU/H | THE SOURCE INVENTORY TABLE IN THE PERMIT LISTED ONLY DIESEL, BUT GAVE OPERATIONAL HOURS TYPICAL FOR BOTH NAT GAS AND DIESEL (SIMILAR TO OTHER SOURCES). FOOTNOTE STATED THAT UNIT 210 BURNS NATURAL GAS AND DIESEL, THEREFORE IT WAS ASSUMED THAT NAT GAS WAS E | Particulate Matter (PM) | P | GOOD OPERATIONS PRACTICES. | 0.05 | GR/DSCF | AV OVER 3 H |  |  |  | 0.0072 | LB/MMBTU | CALCULATED- SEE NOTES | EMISSIONS IN LB/MMBTU CALCULATED USING THE FOLLOWING CONVERSION FACTORS: 1 DSCF NATURAL GAS = 1000 BTU, AND 1 GR = 0.000143 LB. BACT IS CONSIDRED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
MA-0029 | SITHE MYSTIC DEVELOPMENT LLC | SITHE MYSTIC DEVELOPMENT LLC | MA | MASSACHUSETTS DIV OF AIR QUAL CONTROL | 1999-09-29 | 1999 | COMBINED CYCLE ELECTRIC GENERATING FACILITY | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 96 | MMBTU/H |  | Particulate Matter (PM) | P | NATURAL GAS FUEL | 0.7 | LB/H |  |  |  |  | 0.007 | LB/MMBTU
CA-0919 | COCA COLA | COCA COLA | CA | SOUTH COAST AQMD, CA | 1999-11-23 | 1999 |  | BOILER, FIRE TUBE | 13.31 | NATURAL GAS | 31.5 | MMBTU/H | ARB RECORD # A310-947-00 SCOTCH MARINE CUSTOM FIRE-TUBE BOILER USED TO PROVIDE STEAM FOR SANITATION. BACT LIMITS ARE APPLIED TO NOX AND CO LEVELS. NO BACT LIMITS WERE APPLIED TO PM, ROG, AND SOX. DEFAULT EMISSION FACTORS ARE THE BASIS OF THE PM, ROG AND S | Particulate Matter (PM) | N | NO BACT LIMITS WERE APPLIED TO PM. DEFAULT EMISSION FACTORS ARE THE BASIS OF THE PM LEVEL LISTED HERE. | 0.0071 | LB/MMBTU |  |  |  |  | 0.0071 | LB/MMBTU
AK-0053 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFI | CRUDE HEATER, CF-H-31003A | 13.31 | FUEL GAS | 65.6 | MMBTU/H | PERMIT INFORMATION LISTS FUEL TYPE AS FUEL GAS" BUT TECHNICAL DOCUMENTS INDICATE THAT FUEL IS NATURAL GAS. SCC AND PROCESS CODES WERE CHOSEN FOR NATURAL GAS." | Particulate Matter (PM) | P | GOOD OPERATIONAL PRACTICES. COMPLY WITH VE EMISSION LIMITS AS A SURROGATE FOR PM LIMITS. | 14 | LB/MMSCF |  | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H, LIQUID FUEL | 10 | % OPACITY | FOR NO MORE THAN 3MIN/H, NATURAL GAS
AK-0053 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFI | CRUDE HEATER, CF-H-31003B | 13.31 | FUEL GAS | 65.6 | MMBTU/H | PERMIT INFORMATION INDICATES FUEL TYPE IS FUEL GAS" BUT TECHNICAL INFORMATION INDICATES FUEL GAS IS NATURAL GAS. SCC AND PROCESS CODES WERE CHOSEN FOR NATURAL GAS. UNIT IS DESCRIBED AS BORN." | Particulate Matter (PM) | P | GOOD OPERATIONAL PRACTICES. COMPLY WITH VE EMISSION LIMITS AS A SURROGATE FOR PM EMISSION LIMITS. | 14 | LB/MMSCF |  | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H, LIQUID FUEL | 10 | % OPACITY | FOR NO MORE THAN 3MIN/H, NATURAL GAS
TX-0274 | SOLAR GAS TURBINE COGEN. | AMERIPOL SYNPOL CORP. | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-04-03 | 2000 | AMERIPOL PROPOSES TO CONSTRUCT A COGENERATION FACILITY, TURBINE WITH DUCT BURNER FIRED HEAT RECOVERY STEAM GENERATOR (HRSG) AND AN AUXILLIARY BOILER. THE TURBINE IS A 4.4 MW (DESIGN CAPACITY AT ISO CONDITIONS, BASE LOAD) NATURAL GAS FIRED SOLAR TURBINE, M | AUXILIARY BOILER | 13.31 | NATURAL GAS | 54.01 | MMBTU/H | WILL BE OPERATED 175 H/YR ONLY DURING PERIODS OF CTG DOWNTIME. | Particulate Matter (PM) | P | FUEL SPECIFICATIONS OF NO MORE THAN 2.5 GRAINS TOTAL SULFUR PER 100 DRY STANDARD CUBIC FEET ON A SHORT-TERM BASIS AND 0.5 GRAIN TOTAL SULFUR PER 100 DSCF ON A ROLLING 12-MONTH AVERAGE BASIS. | 0.4 | LB/H |  | 0.04 | T/YR |  | 0.007 | LB/MMBTU | CONVERTED USING THROUGHPUT | POLLUTANT DESCRIBED AS PM/PM10. OPACITY LIMIT OF 5%, AVERAGED OVER A 6-MINUTE PERIOD.
MA-0027 | CABOT POWER CORPORATION | CABOT POWER CORPORATION | MA | MASSACHUSETTS DIV OF AIR QUAL CONTROL | 2000-05-07 | 2000 | COMBINED CYCLE ELECTRIC GENERATING FACILITY. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 26.6 | MMBTU/H | PROCESS RESTRICTED TO 500 HOURS PER YEAR (12,881,000 SCF NATURAL GAS) | Particulate Matter (PM) | P | NATURAL GAS FUEL | 0.3 | LB/H |  |  |  |  | 0.01 | LB/MMBTU
AK-0045 | NORTH COOK INLET UNIT | PHILLIPS PETROLEUM COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-06-06 | 2000 | THIS PERMIT ALLOWS PHILLIPS TO INSTALL TWO SOLAR TAURUS 60 T-7300 TURBINES RATED AT 6740 HP AT ISO CONDITIONS. THE TURBINES ARE SUBJECT TO PSD REVIEW FOR NOX AND PM10. | GLYCOL HEATER NOS. 1, 2, AND 3 | 13.31 | NATURAL GAS | 8.36 | MMBTU/H | THREE PROCESS UNITS ARE INCLUDED IN THIS ENTRY. THE OWNER REQUESTED TO LIMIT THE SULFUR CONTENT OF GASEOUS AND LIQUID FUELS TO 200-PPM HYDROGEN SULFIDE AND 0.25% SULFUR BY WEIGHT TO AVOID A PSD PRE-CONSTRUCTION REVIEW OF EXISTING EQUIPMENT. THE OWNER WILL | Particulate Matter (PM) | N | NONE INDICATED | 0.05 | GR/DSCF | 3 H AV, EACH | 0.06 | LB/H |  | 0.0071 | LB/MMBTU | EACH, CALCULATED, SEE NOTES | BASIS OF DETERMINATION IS 18 AAC 50.055(B)(1). THE OWNER REQUESTED TO LIMIT THE SULFUR CONTENT OF GASEOUS AND LIQUID FUELS TO 200-PPM HYDROGEN SULFIDE AND 0.25% SULFUR BY WEIGHT TO AVOID A PSD PRE-CONSTRUCTION REVIEW OF EXISTING EQUIPMENT. THE OWNER WILL
AK-0045 | NORTH COOK INLET UNIT | PHILLIPS PETROLEUM COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-06-06 | 2000 | THIS PERMIT ALLOWS PHILLIPS TO INSTALL TWO SOLAR TAURUS 60 T-7300 TURBINES RATED AT 6740 HP AT ISO CONDITIONS. THE TURBINES ARE SUBJECT TO PSD REVIEW FOR NOX AND PM10. | DRILLING BOILER NO. 1 | 13.31 | NATURAL GAS | 100 | HP | THE OWNER REQUESTED TO LIMIT THE SULFUR CONTENT OF GASEOUS AND LIQUID FUELS TO 200-PPM HYDROGEN SULFIDE AND 0.25% SULFUR BY WEIGHT AND LIMITED HOURS OF OPERATION TO 1080 PER 12 MO PERIOD TO AVOID A PSD PRE-CONSTRUCTION REVIEW OF EXISTING EQUIPMENT. | Particulate Matter (PM) | N | NONE INDICATED | 0.05 | GR/DSCF | 3 H AV | 0.034 | LB/H |  | 0.0071 | LB/MMBTU | CALCULATED, SEE NOTES | BASIS OF DETERMINATION - 18 AAC 50.055(B)(1). THE HOURLY EMISSION LIMIT WAS CONVERTED INTO STANDARDIZED UNITS BY DIVIDING IT BY THE THROUGHPUT.
WI-0181 | CHARTER STEEL | CHARTER STEEL | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2000-08-02 | 2000 | STEEL MILL | BOILER | 13.31 | NATURAL GAS | 10 | MMBTU/H | THIS BOILER IS SUBJECT TO NSPS | Particulate Matter (PM) | P | BACT FOR PM IS DETERMINED TO BE GOOD COMBUSTION CONTROL & THE USE OF NAT. GAS TO FUEL THE BOILER | 0.016 | LB/MMBTU |  |  |  |  | 0.016 | LB/MMBTU
WI-0181 | CHARTER STEEL | CHARTER STEEL | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2000-08-02 | 2000 | STEEL MILL | SPACE HEATERS | 13.31 |  | 5 | MMBTU/H | SPACE HEATERS' THROUGHPUT IS NO MORE THAN 5 MMBTU/H EACH. | Particulate Matter (PM) | P | BACT FOR PM IS DETERMINED TO BE GOOD COMBUSTION AND USE OF NATURAL GAS TO FUEL THE SPACE HEATERS AND SIMILAR COMBUSTION APPLIANCES | 0.016 | LB/MMBTU |  |  |  |  | 0.016 | LB/MMBTU
MN-0039 | MINNESOTA CORN PROCESSORS | MINNESOTA CORN PROCESSORS | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2000-08-08 | 2000 | WET CORN MILLING, PRODUCTION OF CORN PRODUCTS | CARBON FURNACE - FRUCTOSE OR CORN SYRUP | 13.31 | NATURAL GAS | 5.2 | MMBTU/H | COMPLIANCE VERIFIED (STACK TESTING) 01/11/2001. SOX, CO, NOX AND VOC LIMITS SET IN EARLIER DETERMINATIONS. | Particulate Matter (PM) | A | VENTURI SCRUBBER | 0.7 | LB/H |  |  |  |  | 0.13 | LB/MMBTU
AL-0217 | BIRMINGHAM SLAG | HOLCIM, INC. | AL | JEFFERSON COUNTY DEPT OF HEALTH, AL | 2000-11-02 | 2000 | THE PLANT PRODUCES GRANCEM, A SPECIAL CEMENT MANUFACTURED FROM GROUND GRANULATED BLAST FURNACE SLAG, A BYPRODUCT OF THE STEEL-MAKING PROCESS. | NATURAL GAS FIRED FLASH DRYER | 13.31 | NATURAL GAS | 80 | MMBTU/H |  | Particulate Matter (PM) | A | BAGHOUSE | 4.03 | LB/H |  |  |  |  | 0.05 | LB/MMBTU
AL-0178 | ANNISTON ARMY DEPOT | US ARMY - Anniston Army Depot | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-01-05 | 2001 | CHEMICAL WEAPONS INCINERATOR | TWO (2) 13.4 MMBTU/H BOILERS | 13.31 | NATURAL GAS | 13.4 | MMBTU/H | LP Backup | Particulate Matter (PM) | N |  | 0.0076 | LB/MMBTU |  | 0.16 | LB/H |  | 0.0076 | LB/MMBTU
AL-0178 | ANNISTON ARMY DEPOT | US ARMY - Anniston Army Depot | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-01-05 | 2001 | CHEMICAL WEAPONS INCINERATOR | TWO (2) 11.7 MMBTU/H BOILERS | 13.31 | NATURAL GAS | 11.7 | MMBTU/H | LP Backup | Particulate Matter (PM) | N |  | 0.0076 | LB/MMBTU |  | 0.11 | LB/H |  | 0.0076 | LB/MMBTU
SC-0061 | COLUMBIA ENERGY LLC | COLUMBIA ENERGY LLC | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 2001-04-09 | 2001 | ELECTRIC COGENERATION POWER PLANT SUPPLYING STEAM AND ENERGY, A EASTMAN CHEMICAL CO. | HOT WATER HEATERS (2) | 13.31 | NATURAL GAS | 11 | MMBTU/H | USED FOR PREHEATING THE NATURAL GAS PRIOR TO SUPPLY TO THE COMBUSTION TURBINES, SUBJECT TO SUBPART Dc - STANDARDS OF PERFORMANCE FOR SMALL INDUSTRIAL-COMMERCIAL-INSTITUTIONAL STEAM GENERATING UNITS | Particulate Matter (PM) | P | CLEAN BURNING FUEL | 0.6 | LB/MMBTU |  |  |  |  | 0.6 | LB/MMBTU
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-5302A AND H-5302B | 13.31 | NATURAL GAS | 35 | MMBTU/H EA | 35 MMBTU/H MAXIMUM RATE/CAPACITY EA, 30 MMBTU/H NOMINAL CAPACITY EA. | Particulate Matter (PM) | N |  | 0.05 | GR/DSCF | 3 H AVERAGE, STANDARD CONDITIONS |  |  |  | 0.0071 | LB/MMBTU | CALCULATED | EMISSIONS PROVIDED IN LB/MMBTU WERE CALCULATED BY CONVERTING GR TO LB USING THE CONVERSION FACTOR OF 0.00014285714 AND BY CONVERTING DSCF TO MMBTU USING THE NATURAL GAS EQUIVALENT CONVERSION FACTOR OF 0.001.
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-4510A AND H-4510B | 13.31 | NAT GAS | 14.4 | MMBTU/H EACH |  | Particulate Matter (PM) | N |  | 0.05 | GR/DSCF | 3 H AV, STANDARD CONDITIONS |  |  |  | 0.0071 | LB/MMBTU | CALCULATED | EMISSIONS PROVIDED IN LB/MMBTU WERE CALCULATED BY CONVERTING GR TO LB USING THE CONVERSION FACTOR OF 0.00014285714 AND BY CONVERTING DSCF TO MMBTU USING THE NATURAL GAS HEAT VALUE (CONVERSION FACTOR) OF 0.001.
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-5701A AND H-5701B | 13.31 | NAT GAS | 29 | MMBTU/H EACH | 29 MMBTU/H MAXIMUM RATE/CAPACITY EA, 22.7 MMBTU/H NOMINAL CAPACITY EA. HEATERS BURN BOTH NATURAL GAS AND DIESEL FUELS. OPERATING RESTRICTION OF NO MORE THAN 200 H DURING ANY 12 CONSECUTIVE MOS, COMBINED, WHILE FIRING FUEL OIL. OPERATING RESTRICTION OF COM | Particulate Matter (PM) | N |  | 0.05 | GR/DSCF | 3 H AV, STANDARD CONDITIONS |  |  |  | 0.0071 | LB/MMBTU | CALCULATED | EMISSIONS PROVIDED IN LB/MMBTU WERE CALCULATED BY CONVERTING GR TO LB USING THE CONVERSION FACTOR OF 0.00014285714 AND BY CONVERTING DSCF TO MMBTU USING THE NATURAL GAS EQUIVALENT CONVERSION FACTOR OF 0.001.
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | 2001 | ELECTRICITY GENERATION | FUEL GAS HEATER | 13.31 | NATURAL GAS | 16 | MMBTU/H | FUEL GAS HEATER PRE-HEATS THE PIPELINE NATURAL GAS FUEL ENTERING THE COMBUSTION TURBINE UNITS AT 70 DEGREES F | Particulate Matter (PM) | N | NONE- PM EMISSIONS ALREADY VERY LOW | 0.12 | LB/H |  | 0.433 | T/YR |  | 0.0271 | LB/MMBTU
PR-0007 | COGENERATION PLANT (AES-PRCP) | AES PUERTO RICO | PR | PUERTO RICO ENV QUALITY BOARD, AIR PROGRAM | 2001-10-29 | 2001 | COGENERATION UNIT | LIMESTONE DRYER | 13.31 | PROPANE | 13 | MMBTU/H | LIMESTONE DRYER INCLUDES A CRUSHER. HEATED AIR BOTH CLASSIFIES THE GROUND LIMESTONE AND DRIES THE MATERIAL. UNIT IS LIMITED TO A 505 CAPACITY FACTOR CALCULATED BASED ON 4380 H/CALENDAR YR. COMBUSTION CONTROLS WILL BE USED TO MINIMIZE AIR EMISSIONS. | Particulate Matter (PM) | A | BAGHOUSE | 1.24 | LB/H |  |  |  |  | 0.095 | LB/MMBTU
CA-1109 | SUPERIOR INDUSTRIES INTERNATIONAL | SUPERIOR INDUSTRIES INTERNATIONAL | CA | SOUTH COAST AQMD, CA | 2001-10-30 | 2001 |  | METAL HEATING FURNACE | 13.31 | NATURAL GAS | 12.6 | MMBTU/H | EQUIP: NO AIR PREHEAT, MFR: THERMAL PROCESS, TYPE: REVERBERATORY, FUNC EQUIP: ALUMINUM MELTING, FUEL_TYPE: PROPANE, SCHEDULE: CONTINUOUS, H/D: 24, D/W: 7, W/Y: 50 NOTES: THIS IS A RECLAIM FACILITY. THE FACILITY REQUESTED PERMIT MODIFICATIONS FOR FOUR ALUM | Particulate Matter (PM) | N |  | 0.1 | GR/SCF |  |  |  |  | 0.1 | GR/SCF
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | 2001 | SOYBEAN EXTRACTION PLANT | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. There is a separate process entry for this boiler when firing fuel oil. | Particulate Matter (PM) | N |  | 0.46 | LB/H |  | 2.06 | T/YR |  | 0.005 | LB/MMBTU |  | USING NATURAL GAS WITH BACKUP NO.2 FUEL OIL. EMISSIONS BASED ON MFG. TESTED RATE FOR NATURAL GAS 0.005 LB PE/MMBTU.
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | 2001 | SOYBEAN EXTRACTION PLANT | DRYER, SOY PROTEIN CONCENTRATE - COMBUSTION | 13.31 | NATURAL GAS | 37 | MMBTU/H | Baghouse with 100% capture. Process is in 2 parts - dryer - combustion, and dryer - pm. | Particulate Matter (PM) | A | BAGHOUSE WITH 100% CAPTURE | 0.11 | LB/H |  | 0.48 | T/YR |  | 0.003 | LB/MMBTU |  | BAGHOUSE WITH MANUFACTURER'S GUARANTEED GRAIN LOADING OF 0.0025 GRAIN/DSCF AND AIR FLOW RATE USED TO DEMONSTRATE COMPLIANCE. IF REQUIRED BY REGULATING AGENCY, METHOD 5 AND/OR 9 MAY BE USED TO DEMONSTRATE COMPLIANCE.
IN-0097 | CARGILL, INC | CARGILL, INC | IN | INDIANA, OTHER | 2001-12-03 | 2001 | GRAIN ELEVATOR AND SOYBEAN OIL EXTRACTION AND PROTEIN RICH PRODUCTS. | BOILERS 1 & 2 | 13.31 | NATURAL GAS | 75 | MMBTU/H | CEMS, WHEN BURNING RESIDUAL OIL. LIMITS ON NO.2, 3 & 4 FUEL OIL USAGES FOR SO2 AND NOX. | Particulate Matter (PM) | N |  | 7.6 | LB/MMSCF NATURAL GAS | PM AND PM10, FROM AP-42 |  |  |  | 0.007 | LB/MMBTU | 7.6 LB/MMSCF | PM EMISSIONS ARE FROM THE STANDARD IN AP-42.
IN-0095 | ALLEGHENY ENERGY SUPPLY CO. LLC | ALLEGHENY ENERGY SUPPLY CO. LLC (ACADIA BAY ENERGY | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-12-07 | 2001 | ELECTRIC POWER GENERATING STATION | AUXILLIARY BOILER | 13.31 | NATURAL GAS | 21 | MMBTU/H |  | Particulate Matter (PM) | P | NATURAL GAS AS SOLE FUEL | 0.0075 | LB/MMBTU |  |  |  |  | 0.0075 | LB/MMBTU
AR-0049 | GEORGIA PACIFIC - CROSSETT PAPER | GEORGIA PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-12-14 | 2001 | KRAFT PAPER MILL. | BURNER EXHAUST A, TAD (SN-85A) | 13.31 | NATURAL GAS | 90 | MMBTU/H | Source has not been installed yet. BACT for PM, VOC, CO and NOx. Initial & 3 yr periodic testing required for CO & NOx. | Particulate Matter (PM) | P | USE OF NATURAL GAS FUEL. | 0.0217 | LB/MMBTU |  |  |  |  | 0.0217 | LB/MMBTU
AR-0049 | GEORGIA PACIFIC - CROSSETT PAPER | GEORGIA PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-12-14 | 2001 | KRAFT PAPER MILL. | BURNER EXHAUST B, TAD | 13.31 | NATURAL GAS | 50 | MMBTU/H | Source not yet installed. BACT for PM, CO, NOx, VOC. Initial & 3 -yr periodic testing is required for NOx & CO. | Particulate Matter (PM) | P | NATURAL GAS FUEL USAGE ONLY (CLEAN FUEL). | 0.0217 | LB/MMBTU |  |  |  |  | 0.0217 | LB/MMBTU
AR-0049 | GEORGIA PACIFIC - CROSSETT PAPER | GEORGIA PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-12-14 | 2001 | KRAFT PAPER MILL. | BURNER, YANKEE | 13.31 | NATURAL GAS | 21 | MMBTU/H | Source is not installed yet. Initial & 3 year periodic testing required for CO & NOx using methods 10 & 7E respectively. BACT for PM, VOC, CO and NOx. | Particulate Matter (PM) | P | NATURAL GAS AS FUEL. | 0.0164 | LB/MMBTU |  | 1.5 | T/YR |  | 0.0164 | LB/MMBTU
LA-0174 | PORT HUDSON OPERATIONS | GEORGIA-PACIFIC CORPORATION | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-01-25 | 2002 | PULP MILL | POWER BOILER NO. 2 | 13.31 | NAT GAS | 65.5 | MMBTU/H | EMISSION POINT NO. 6. | Particulate Matter (PM) | P | FIRED BY NATURAL GAS | 3.33 | LB/H |  | 2.2 | T/YR |  | 0.05 | LB/MMBTU
KY-0087 | QUEBECOR WORLD FRANKLIN | QUEBECOR WORLD FRANKLIN | KY | KENTUCKY DEP, DIV FOR AIR QUALITY | 2002-07-12 | 2002 | ROTOGRAVURE PRINTING PLANT | BOILER, NATURAL GAS, #4 | 13.31 | NATURAL GAS | 33.5 | MMBTU/H | Boiler is a Cleaver Brooks indirect heat exchanger, using natural gas as primary fuel and no. 2 fuel oil as standby fuel. | Particulate Matter (PM) | N |  | 0.308 | LB/MMBTU |  |  |  |  | 0.308 | LB/MMBTU
IA-0060 | HAWKEYE GENERATING, LLC | ENTERGY | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-07-23 | 2002 | ENTERGY IS INSTALLING TWO GE 7FA (170MW) NATURAL GAS FIRED TURBINES. THEY ARE REQUIRED TO INSTALL SCR FOR CONTROL OF NOX (3 PPMVD, 3 HOUR AVG. TIME) AND CATALYTIC OXIDATION FOR THE CONTROL OF CO (5 PPMVD, 3 HOUR AVG. TIME) FOR COMBINED CYCLE OPERATION. SI | AUXILIARY BOILER (48.5 MMBTU/H) | 13.31 | NATUAL GAS | 48.69 | MILLION CF/YR |  | Particulate Matter (PM) | B | GCP | 0.007 | LB/MMBTU |  |  |  |  | 0.007 | LB/MMBTU
VA-0261 | CPV CUNNINGHAM CREEK | COMPETITIVE POWER VENTURE | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-09-06 | 2002 | TURBINES USED TO PRODUCE ELECTRICITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 80 | MMBTU/H | one auxiliary boiler | Particulate Matter (PM) | P | GOOD COMBUSTION PRACTICES. | 0.58 | LB/H |  | 0.87 | T/YR |  | 0.007 | LB/MMBTU
GA-0101 | MURRAY ENERGY FACILITY | DUKE ENERGY MURRAY LLC | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2002-10-23 | 2002 | ELECTRIC GENERATING FACILITY | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 31.4 | MMBTU/H | HOURS OF OPERATION NOT TO EXCEED 6,000 H/YR. | Particulate Matter (PM) | P | GOOD COMBUSTION PRACTICE, CLEAN FUEL | 0.01 | LB/MMBTU |  |  |  |  | 0.01 | LB/MMBTU
VA-0243 | STANLEY FURNITURE |  | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-12-01 | 2002 | WOOD HOUSEHOLD FURNITURE MFG. | BOILER, NAT GAS & OIL | 13.31 | NATURAL GAS | 26.5 | MMBTU/H | KEWANEE NATURAL GAS/DISTILLATE OIL BOILER. THROUGHPUT 26.5 MMBTU/HR - 450,000 GAL #2 OIL. ADDITIONAL SCC, 10200502. FOR ALL POLLUTANTS, NO CONTROLS, EMISSION LIMITS IN T/YR ONLY | Particulate Matter (PM) | N | EMISSION LIMITS IN T/YR ONLY | 1.1 | T/YR | [6 empty] | NOT AVAILABLE
TX-0392 | LUCITE BEAUMONT | INEOS ACRYLICS, INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-09 | 2002 | SULFURIC ACID REGENERATION FACILITY | NO.1 PRE-HEATER | 13.31 | NATURAL GAS |  |  |  | Particulate Matter (PM) | N |  | 0.04 | LB/H |  | 0.18 | T/YR
IA-0062 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT (IPL) | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-12-20 | 2002 | PERMITS WERE AMENDED ON 6/26/03. RBLC ID IA-0062 WAS CORRECTED AS MOST OF THE CHANGES WERE MINOR (BASED ON OPERATIONAL & DESIGN CHANGES BEING MADE AS PLANT IS CONSTRUCTED). THE NEW DEW POINT HEATER HAS BEEN GIVEN A NEW RBLC ID. | GAS HEATER, (2) | 13.31 | NATURAL GAS | 16.4 | MMBTU/H | Natural Gas fired Heaters, 16.4 MMBTU/HR capacity for each. Operating hours reduced from 8760 hours to 6000 hours each. | Particulate Matter (PM) | P | LOW ASH FUEL | 0.0075 | LB/MMBTU |  |  |  |  | 0.0075 | LB/MMBTU
IA-0062 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT (IPL) | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-12-20 | 2002 | PERMITS WERE AMENDED ON 6/26/03. RBLC ID IA-0062 WAS CORRECTED AS MOST OF THE CHANGES WERE MINOR (BASED ON OPERATIONAL & DESIGN CHANGES BEING MADE AS PLANT IS CONSTRUCTED). THE NEW DEW POINT HEATER HAS BEEN GIVEN A NEW RBLC ID. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 68 | MMBTU/H | Limited to 6000 hours of operation per year. | Particulate Matter (PM) | P | LOW ASH FUEL, NG | 0.0075 | LB/MMBTU |  |  |  |  | 0.0075 | LB/MMBTU
OH-0295 | GMC TRUCK AND BUS, MORAINE ASSEMBLY PLANT | GENERAL MOTORS CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-01-14 | 2003 | LIGHT DUTY TRUCKS AND AUTOMOBILE PRODUCTION, ASSEMBLY PLANT | NATURAL GAS USAGE | 13.31 | NATURAL GAS | 1700 | MMCF/rolling 12-mo | THE INCREASE IN NATURAL GAS USAGE CAUSED THIS PERMIT TO BE PSD FOR NOX. COMBINED NATURAL GAS USAGE FOR: ELPO SAND, GUIDE COAT, BODY SAND, BODY WIPE, TOPCOAT SYSTEM, TOPCOAT ABATEMENT, FINAL REPAIR, DEADNER, BUILDING HEAT. | Particulate Matter (PM) | N |  | 20 | LB/MMCF |  | 17 | T/YR |  | 0.02 | LB/MMBTU
IA-0064 | ROQUETTE AMERICA | ROQUETTE AMERICA | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2003-01-31 | 2003 |  | DEW POINT HEATER | 13.31 | NATURAL GAS | 1.6 | MMBTU/H | natural gas only, operates 8760 h/yr | Particulate Matter (PM) | P | GOOD COMBUSTION PRACTICES | 0.008 | LB/MMBTU |  | 0.012 | LB/H |  | 0.008 | LB/MMBTU
GA-0098 | RINCON POWER PLANT | GENPOWER RINCON LLC | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2003-03-24 | 2003 | ELECTRIC GENERATING FACILITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 83 | MMBTU/H | THE BOILER IS LIMITED TO 1,000 H/YR OF OPERATION. | Particulate Matter (PM) | N |  | 0.0084 | LB/MMBTU |  |  |  |  | 0.0084 | LB/MMBTU
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 | 2003 |  | BOILER NO. 1 | 13.31 | NATURAL GAS | 43.2 | MMBTU/H | One of two boilers | Particulate Matter (PM) | P | GOOD COMBUSTION PRACTICES | 0.62 | LB/H | each unit |  |  |  | 0.014 | LB/MMBTU |  | one of two boilers
AL-0202 | CORUS TUSCALOOSA | CORUS TUSCALOOSA | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2003-06-03 | 2003 | STEEL MILL | EQUALIZING FURNACE | 13.3 | NATURAL GAS | 1.8 | MMBTU/H |  | Particulate Matter (PM) | N | NATURAL GAS/GOOD COMBUSTION | 6.72 | LB/H |  | 37.33 | LB/MMCF |  | 3.73 | LB/MMBTU | calculated
IA-0068 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT - EMERY GENERATING STATI | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2003-06-26 | 2003 | IPL CHANGED NAMES FROM THE POWER IOWA ENERGY CENTER (PIEC) TO THE EMERY GENERATING STATION. | GAS HEATER | 13.31 | NATURAL GAS | 9 | MMBTU/H | One natural gas dew point heater is added. | Particulate Matter (PM) | P | LOW ASH FUEL | 0.0075 | LB/MMBTU |  | 0.29 | T/YR |  | 0.0075 | LB/MMBTU
MN-0054 | MANKATO ENERGY CENTER |  | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2003-12-04 | 2003 | COMBINED CYCLE GAS TURBINE ELECTRIC POWER PLANT. TWO IDENTICAL GE FRAME F7A GAS TURBINES EACH WITH HRSG W/DUCT BURNERS FEEDING STEAM TO COMMON STEAM TURBINES. PRIMARY FUEL IS NG, NO. 2 VERY LOW SULFUR DISTILLATE OIL FOR BACKUP. ALSO, AUX. BOILER, DIESEL E | BOILER, COMMERCIAL | 13.31 | NATURAL GAS | 70 | MMBTU/H | NATURAL GAS ONLY | Particulate Matter (PM) | N | CLEAN FUELS | 0.008 | LB/MMBTU |  |  |  |  | 0.01 | LB/MMBTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S50/B50, 60 MMBTU/H | 13.31 | NATURAL GAS | 60 | MMBTU/H | NATURAL GAS / PROPANE | Particulate Matter (PM) | P | NATURAL GAS/ PROPANE; GOOD COMBUSTION CONTROL | 0.0075 | LB/MMBTU |  | 0.45 | LB/H |  | 0.0075 | LB/MMBTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S51/B51, 80 MMBTU/H | 13.31 | NATURAL GAS | 80 | MMBTU/H | NAT. GAS / PROPANE | Particulate Matter (PM) | P | NATURAL GAS, GOOD COMBUSTION CONTROL | 0.0075 | LB/MMBTU |  | 0.6 | LB/H |  | 0.0075 | LB/MMBTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S52/B52, 11 MMBTU/H | 13.31 | NATURAL GAS | 11 | MMBTU/H |  | Particulate Matter (PM) | P | NATURAL GAS / PROPANE; GOOD COMBUSTION CONTROL | 0.0075 | LB/MMBTU |  | 0.08 | LB/H |  | 0.0075 | LB/MMBTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S53 / B53, 34 MMBTU/H | 13.31 | NATURAL GAS | 34 | MMBTU/H |  | Particulate Matter (PM) | P | NATURAL GAS / PROPANE; GOOD COMBUSTION CONTROL | 0.0075 | LB/MMBTU |  | 0.26 | LB/H |  | 0.0075 | LB/MMBTU
OK-0097 | QUAD GRAPHICS OKC FAC | QUAD GRAPHICS INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2004-02-03 | 2004 | COMMERCIAL PRINTING | HEATERS/OXIDIZERS | 13.31 | NATURAL GAS | 16 | MMBTU/H |  | Particulate Matter (PM) | P | EXCLUSIVE USE OF COMMERCIAL NATURAL GAS OR PROPANE. | 0.12 | LB/H |  | 0.39 | T/YR |  | 0.0075 | LB/MMBTU | calculated
WV-0021 | OHIO RIVER PLANT | CABOT CORPORATION | WV | WEST VIRGINIA AIR POLLUTION CONTROL COMM | 2004-06-09 | 2004 | AN EXISTING 3-UNIT, 4-REACTOR CARBON BLACK PRODUCTION FACILITY. TRADITIONALLY, HAS FLARED OR COMBUSTED ALL TAIL GAS. | BOILER, NATURAL GAS, 39.00 MMBTU | 13.31 | NATURAL GAS | 365 | MMSCF/YR | Boiler has MDHI of 39.00 mmbtu and combusts natural gas only. | Particulate Matter (PM) | N |  | 0.32 | PPH |  | 1.39 | T/YR |  | 0.008 | LB/MMBTU
WI-0223 | LOUISIANA-PACIFIC HAYWARD | LOUISIANA-PACIFIC CORPORATION | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-06-17 | 2004 | OSB MILL | THERMAL OIL HEATER, GTS ENERGY, S31, B31 | 13.31 | NATURAL GAS | 32 | MMBTU/H | STACK S31; BOILER B31 - GTS ENERGY THERMAL OIL HEATER RATED AT 32.0 MILLION BTU PER HOUR WHEN BURNING NATURAL GAS AND 30.0 MILLION BTU PER HOUR WHEN BURNING DISTILLATE FUEL OIL | Particulate Matter (PM) | P | USE OF NATURAL GAS / DISTILLATE OIL, W/ RESTRICTION ON OIL USAGE | 0.84 | LB/H |  |  |  |  | 0.15 | LB/MMBTU
WI-0223 | LOUISIANA-PACIFIC HAYWARD | LOUISIANA-PACIFIC CORPORATION | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-06-17 | 2004 | OSB MILL | THERMAL OIL HEATER, GTS ENERGY, S32, B32 | 13.31 | NATURAL GAS | 32 | MMBTU/H | STACK S32; BOILER B32 - GTS ENERGY THERMAL OIL HEATER RATED AT 32.0 MILLION BTU PER HOUR WHEN BURNING NATURAL GAS AND 30.0 MILLION BTU PER HOUR WHEN BURNING DISTILLATE FUEL OIL. | Particulate Matter (PM) | P | USE OF NATURAL GAS / DISTILLATE OIL, W/ RESTRICTION ON OIL USAGE | 1 | LB/H |  |  |  |  | 0.15 | LB/MMBTU
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | 2004 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, NATURAL GAS (1) | 13.31 | NATURAL GAS | 40 | MMBTU/H | AUXILIARY BOILER. | Particulate Matter (PM) | P | CLEAN FUEL AND GOOD COMBUSTION. | 0.008 | LB/MMBTU | 3 HOUR AVERAGE |  |  |  | 0.008 | LB/MMBTU
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | B63, S63; B64, S64 - NATURAL GAS STATION HEATER 1 AND 2 | 13.31 | NATURAL GAS | 0.75 | MMBTU/H | EMISSION LIMITS ARE THOSE FOR EACH UNIT. | Particulate Matter (PM) | P | NATURAL GAS | 0.01 | LB/H |  |  |  |  | 0.013333 | LB/MMBTU | NOT AVAILABLE | PM (INCL. M202 BACKHALF CATCH) (LIMIT IS FOR EACH UNIT)
MD-0035 | DOMINION | DOMINION COVE POINT LNG, L.P. | MD | MARYLAND DEPARTMENT OF THE ENVIRONMENT | 2005-08-12 | 2005 | LNG FACILITY | VAPORIZATION HEATER | 13.31 | NATURAL GAS |  |  | SEVEN VAPORIZATION HEATERS; RATED HEAT INPUT IS 88.4 MMBTU/H FOR EACH UNIT; EMISSION LIMITS APPLY TO EACH UNIT | Particulate Matter (PM) |  |  | 0.001 | LB/MMBTU |  |  |  |  | 0.001 | LB/MMBTU
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | 2007 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NATURAL GAS | 13.31 | NATURAL GAS | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. WITH #2 OIL BACKUP TWO SET OF LIMITS, THIS ONE FOR NATURAL GAS | Particulate Matter (PM) | N |  | 0.04 | LB/H |  | 0.27 | LB/YR |  | 0.0019 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
*AL-0231 | NUCOR DECATUR LLC | NUCOR CORPORATION | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-06-12 | 2007 | THE FACILITY PRODUCES STEEL COILS PRIMARILY FROM STEEL SCRAP USING THE ELECTRIC ARC FURNACE (EAF) PROCESS. | VACUUM DEGASSER BOILER | 13.31 | NATURAL GAS | 95 | MMBTU/H |  | Particulate Matter (PM) | N |  | 0.0076 | LB/MMBTU |  | 0.72 | LB/H |  | 0.0076 | LB/MMBTU
*AL-0231 | NUCOR DECATUR LLC | NUCOR CORPORATION | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-06-12 | 2007 | THE FACILITY PRODUCES STEEL COILS PRIMARILY FROM STEEL SCRAP USING THE ELECTRIC ARC FURNACE (EAF) PROCESS. | GALVANIZING LINE FURNACE | 13.31 | NATURAL GAS | 98.7 | MMBTU/H |  | Particulate Matter (PM) | N |  | 0.0076 | LB/MMBTU |  | 0.75 | LB/H |  | 0.0076 | LB/MMBTU
IA-0088 | ADM CORN PROCESSING - CEDAR RAPIDS | ARCHER DANIELS MIDLAND | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-06-29 | 2007 | CONSISTS OF THREE DISTINCT OPERATIONS: CORN WET MILL, CORN DRY MILL AND BOILERHOUSE | INDIRECT-FIRED DDGS DRYER | 13.31 | NATURAL GAS | 93.7 | MMBTU/H | PROJECT INCLUDES THE INSTALLATION OF EIGHT IDENTICAL DDGS DRYERS. PERMITS 07-A-546-P, 547, 548, 549, 550, 557, 558 AND 559. THE COMBUSTION CHAMBER AND THE FEED CHAMBER ARE SEPERATED BY A HEAT EXCHANGER. THE DRYERS CAN FIRE NATURAL GAS, BIOGAS FROM THE WWT | Particulate Matter (PM) | N |  | 0.015 | GR/DSCF | AVERAGE OF 3 TEST RUNS | [6 empty] | PM LIMIT INCLUDES BOTH FILTERABLE AND CONDENSABLE FRACTIONS.
IN-0108 | NUCOR STEEL | NUCOR STEEL | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2003-11-21 | 2003 | STEEL MINI MILL | BOILER, NATURAL GAS, (2) | 13.31 | NATURAL GAS | 34 | MMBTU/H | Throughput for each. Propane is backup fuel. These boilers supply steam to the entire cold mill area of the plant. Subject to NSPS Subpart Dc | Particulate Matter (PM), Filterable | P | COMPLIANCE IS BY USING NATURAL GAS | 0.0019 | LB/MMBTU |  |  |  |  | 0.0019 | LB/MMBTU |  | Filterable fraction only
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HIGH PRESSURE BOILER #2-R2 | 13.31 | FUEL OIL | 0.3 | MMBTU/H | PERMIT NO: 97-A-416 FUEL OIL < 10,674,202 GALLONS/Y PER WHOLE FACILITY SULFUR CONTENT OF FUEL OIL < 0.05 % BY WEIGHT | Particulate Matter < 10 μ (PM10) | P | LOW NOX/FGR | 0.18 | LB/H |  | 0.8 | T/YR |  | 0.6 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #3 B3 | 13.31 | NATURAL GAS | 2.3 | MMBTU/HR | BOILER BURNS NATURAL GAS OR FUEL OIL. PERMIT NO: 97-A-408 20% OPACITY PER NSPS SUBPART DC SO2 SET AT 9.46 TPY TO STAY UNDER PSD SIGNIFICANCE | Particulate Matter < 10 μ (PM10) | P | LOW NOX BURNER, FLUE GAS RECIRCULATION | 1.39 | LB/H |  | 6.07 | T/YR |  | 0.6 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #2 B2 | 13.31 | NATURAL GAS | 2.3 | MMBTU/H | 20% OPACITY BY NSPS SUBPART DC SO2 - 9.46 TPY TO STAY UNDER PSD SIGNIFICANCE | Particulate Matter < 10 μ (PM10) | P | LOW NOX BURNER, FLUE GAS RECIRC. | 1.39 | LB/H |  | 6.07 | T/YR |  | 0.6 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #1 | 13.31 | NATURAL GAS | 2.3 | MMBTU/H | FUEL IS NATURAL GAS AND FUEL OIL ONLY. PERMIT NUMBER: 97-A-377. 20 % OPACITY NSPS SUBPART BC SO2 - 9.46 TPY, SET TO STAY UNDER PSD SIGNIFICANCE LEVELS | Particulate Matter < 10 μ (PM10) | P | LOW NOX BURNER , FLUE GAS RECIRCULATION | 1.39 | LB/H |  | 6.07 | T/YR |  | 0.6 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HYDROGEN PLANT BURNER R9 | 13.31 |  |  |  | PERMIT NUMBER: 97-A-391 20% OPACITY - 1A 23.3(2)D. THIS PROCESS GENERATES HYDROGEN FROM NATURAL GAS. THE HYDROGEN IS USED FOR THE HYDROGENATION OF THE SOYBEAN OIL. | Particulate Matter < 10 μ (PM10) | N |  | 0.21 | LB/H |  | 0.9 | T/YR |  | 0.014 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HIGH PRESSURE BOILER #1 | 13.31 | NATURAL GAS | 0.3 | MMBTU/H | FUELS ARE NATURAL GAS AND #2FUEL OIL. PERMIT NUMBER 97-A-390 20% OPACITY BY NSPS SUBPART DC SO2 LIMIT 1.26 TPY TO STAY UNDER PSD SIGNIFICANCE | Particulate Matter < 10 μ (PM10) | N |  | 0.18 | LB/H |  | 0.8 | T/YR |  | 0.6 | LB/MMBTU
WI-0188 | GOLDEN BOOKS PUBLISHING COMPANY INC. | GOLDEN BOOKS PUBLISHING COMPANY INC. | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 1997-06-24 | 1997 | PRINTING FACILITY | SPACE HEAT & COMBUSTION SOURCES, (P01 S01) | 13.31 | NATURAL GAS | 93 | MMBTU/H | SECOND FUEL: PROPANE | Particulate Matter < 10 μ (PM10) | N | REGULATORY BASIS: STATE REGULATION. | 1.25 | LB/H |  |  |  |  | 0.013 | LB/MMBTU
LA-0113 | BASF CORPORATION | BASF CORPORATION | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1997-12-30 | 1997 |  | DUCT BURNER, COGEN UNIT NO. 2 | 13.31 | NATURAL GAS | 0.4 | MMLB/H STEAM |  | Particulate Matter < 10 μ (PM10) | P | GOOD DESIGN, PROPER OPERATING PRACTICES, AND USE GASEOUS FUELS | 5.4 | LB/H | [6 empty] | NOT AVAILABLE
AK-0036 | KUPARUK CENTRAL PRODUCTION FACILITY | ARCO ALASKA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1998-02-13 | 1998 |  | PROCESS HEATER | 13.31 | NATURAL GAS | 8 | MMBTU/H | OTHER COMPLIANCE: FACILITY OPERATING REPORTS. PERMIT LIMITS NOX AND H2S IN FUEL (SO2, PM10 AND VE). CO AND VOC ARE NOT INCLUDED IN THIS PERMIT. | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS | 0.05 | GR/DSCF | [6 empty] | NOT AVAILABLE
LA-0112 | GEISMAR FACILITY | AIR LIQUIDE AMERICA CORP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1998-02-13 | 1998 | AIR SEPARATION TO PRODUCE NITROGEN AND OXYGEN IN LIQUIDIZED GAS FORMS - ALSO TRANSPORT. PROJECT: NEW COGEN UNIT, NATURAL GAS FIRED FRAME 7 GE TURBINE WITH DUCT BURNER. | BOILER NO. 1 | 13.31 | NATURAL GAS | 95 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | GOOD DESIGN, PROPER OPERATING PRACTICES, AND USE CLEAN NATURAL GAS AS FUEL. | 0.95 | LB/H | HOURLY MAXIMUM | 4.16 | T/YR | ANNUAL MAXIMUM | 0.01 | LB/MMBTU | THREE ONE-HOUR TEST AVERAGE
LA-0112 | GEISMAR FACILITY | AIR LIQUIDE AMERICA CORP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 1998-02-13 | 1998 | AIR SEPARATION TO PRODUCE NITROGEN AND OXYGEN IN LIQUIDIZED GAS FORMS - ALSO TRANSPORT. PROJECT: NEW COGEN UNIT, NATURAL GAS FIRED FRAME 7 GE TURBINE WITH DUCT BURNER. | REACTIVATION HEATERS (2) | 13.31 |  | 9 | MMBTU/H | THROUGHPUT FOR EACH UNIT | Particulate Matter < 10 μ (PM10) | N |  | 0.11 | LB/H | HOURLY MAXIMUM | 0.48 | T/YR | ANNUAL MAXIMUM | 0.012 | LB/MMBTU | CALCULATED
IA-0048 | CARGILL INC - SIOUX CITY | CARGILL INC - SIOUX CITY | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1998-06-01 | 1998 | SOYBEAN OIL MILL | BOILER, BACKUP | 13.31 |  | 77 | MMBTU/H | PERMIT NUMBER FOR THIS PROCESS IS 86-A-036-S1. permit for PM/PM10 and NOx only | Particulate Matter < 10 μ (PM10) | N |  | 0.7 | LB/H |  |  |  |  | 0.009 | LB/MMBTU |  | 500 H/YR RESTRICTION - THE ONLY REVISION MADE TO THE EXISTING PERMIT.
TX-0300 | SALT CREEK GAS PLANT | MOBIL EXPLORATION & PRODUCING US INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-10-13 | 1998 | MOBIL EXPLORATION & PRODUCING US INC HAS REQUESTED AN AMENDMENT TO PERMIT NO 20660 AND A MODIFICATION TO PSD-TX-795 TO (1) INCREASE THE CO AND VOC ALLOWABLES ON THEIR COOPER-BESSEMER GMVH-12C2 ENGINES TO ALLOW THEM TO BETTER CONTROL NOX TO THE 2 G/HP-H LE | HOT OIL HEATER, EPN 26 | 13.31 | NAT GAS | 32.2 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | FUEL IS LIMITED TO PIPELINE-QUALITY, SWEET NATURAL GAS CONTAINING NO MORE THAN 5 GR S/100 DSCF | 0.06 | LB/H |  | 0.26 | T/YR |  | 0.0019 | LB/MMBTU | CALCULATED | STANDARD EMISSION LIMITS CALCULATED FROM HOURLY EMISSION LIITS AND HEATERS RATED CAPACITY.
OH-0245 | REPUBLIC TECHNOLOGIES INTERNATIONAL | REPUBLIC TECHNOLOGIES INTERNATIONAL/CANTON | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 1999-01-27 | 1999 | STEEL MILL. THIS PLANT IS PSD FOR PM, SO2, NOX, CO, AND VOC. THIS MODIFICATION IS A SIGNIFICANT INCREASE FOR NOX. | ECCENTRIC BOTTOM TAPPING LADLE PREHEATER FURNACE | 13.31 | NATURAL GAS | 14 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N |  | 0.196 | LB/H |  | 0.86 | T/YR |  | 0.014 | LB/MMBTU
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 1 (NATURAL GAS) | 13.31 | NATURAL GAS | 84.4 | MMBTU/H | MFR. IS COMBUSTION ENGINEERING. ONLY NATURAL GAS, A MIXTURE OF NO. 2 OIL AND LASALOCID OIL, AND NO. 2 OIL SHALL BE FIRED IN BOILER 1. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. AFTER APRIL 3 | Particulate Matter < 10 μ (PM10) | N |  | 1.2 | LB/H |  |  |  |  | 0.014 | LB/MMBTU
CO-0041 | AMERICAN SODA, LLP, PINEANCE FACILITY |  | CO | COLORADO DEPT OF HEALTH - AIR POLL CTRL | 1999-05-06 | 1999 |  | BOILER NO.2, TEST MINE HOT WATER (1) | 13.31 | NATURAL GAS | 51.08 | MMBTU | NATURAL GAS FIRED HOT WATER BOILER PRODUCES HIGH PRESSURE HOT WATER FOR INJECTION INTO THE WELLS. ONLY NOX, CO AND PM EMISSION LIMITS HAVE BEEN PROVIDED FOR THIS PROCESS. | Particulate Matter < 10 μ (PM10) | P | COMBUSTION CONTROL | 0.009 | LB/MMBTU |  | 0.02 | T/YR |  | 0.009 | LB/MMBTU
OK-0051 | GREEN COUNTRY ENERGY PROJECT | COGENTRIX ENERGY INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 1999-10-01 | 1999 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS |  |  |  | Particulate Matter < 10 μ (PM10) | P | USE OF LOW ASH FUEL AND EFFICIENT COMBUSTION | 0.0074 | LB/MMBTU |  |  |  |  | 0.0074 | LB/MMBTU
OK-0075 | GREEN COUNTRY ENERGY PROJECT | COGENTRIX ENERGY INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 1999-12-09 | 1999 |  | TURBINES WITH DUCT BURNERS, COMBINED CYCLE (3) | 13.31 | NATURAL GAS | 0 |  | MANUFACTURER PROVIDED NEW DATA THAT INDICATED HIGHER EMISSIONS OF PM10. | Particulate Matter < 10 μ (PM10) | P | LOW ASH FUEL AND EFFICIENT COMBUSTION | 0.012 | LB/MMBTU |  |  |  |  | 0.012 | LB/MMBTU
OK-0041 | MCCLAIN ENERGY FACILITY | NRG MCCLAIN LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2000-01-19 | 2000 | POWER PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 22 | MMBTU/H | See RBLC ID OK-0071 for updated emission limits based on increased hours of operatuion. | Particulate Matter < 10 μ (PM10) | P | CLEAN FUEL | 0.1 | T/YR | [6 empty] | Not Available
OK-0050 | ONETA GENERATING STA | CALPINE CORP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2000-01-21 | 2000 | ELECTRIC GENERATION PLANT | DUCT BURNERS (4) | 13.31 | NATURAL GAS | 328 | MMBTU/H | The emission limits indicted are for the duct burners only. Emission limits for the turbines associated with these duct burners are provided under the process Combustion Turbines | Particulate Matter < 10 μ (PM10) | P | LOW ASH FUEL - NATURAL GAS | 0.015 | LB/MMBTU |  |  |  |  | 0.015 | LB/MMBTU
TX-0309 | FORMOSA PLASTICS TEXAS | FORMOSA PLASTICS CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-02-10 | 2000 | THIS PERMIT AUTHORIZES THE OPERATION OF THE FORMOSA ETHYLENE GLYCOL PLANT & A PRODUCTION INCREASE, EQUIPMENT UPGRADES & CHANGES, ADDITIONAL FUGITIVE EMISSIONS, & AN ADDITIONAL COOLING TOWER CELL. THE APPLICANT WISHES TO CONSOLIDATE ALL FUGITIVE EMISSION P | WASTE HEAT BOILER, 70Z401 | 13.31 | NAT GAS |  |  | SHALL BE MAINTAINED AT A MINIMUM COMBUSTION CHAMBER TEMP OF 1450 F. | Particulate Matter < 10 μ (PM10) | N | NONE INDICATED | 1.13 | LB/H |  | 3.4 | T/YR |  |  |  | NOT AVAILABLE
MI-0301 | ALCHEM ALUMINUM | ALCHEM ALUMINUM, INC. | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 2000-05-02 | 2000 | SECONDARY ALUMINUM PRODUCTION. | REVERBERATORY FURNACES | 13.31 | NATURAL GAS | 42000 | LB/H | HOLDING CAPACITIES ARE 170,000 AND 250,000 POUNDS. BURNER CAPACITIES ARE 34,000,000 AND 48,000,000 BTU/H. REQ'D TESTS FOR PM, D/F, HCL, HF, CL2, VOC. ALL PERMIT LIMITS ARE BASED ON STACK TESTS OF FURNACES 1,2,7,8 AT CORPORATE'S COLDWATER MI COMPARABLE FAC | Particulate Matter < 10 μ (PM10) | B | BAGHOUSE-SEE POLLUTANT NOTES. | 0.61 | LB/T | [7 empty] | TOTAL PM10 EMISIONS FROM THE TWO FURNACES SHALL NOT EXCEED 0.61 LB/TON OF FEED/CHARGE.
MI-0301 | ALCHEM ALUMINUM | ALCHEM ALUMINUM, INC. | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 2000-05-02 | 2000 | SECONDARY ALUMINUM PRODUCTION. | FLUES | 13.31 | NATURAL GAS | 42000 | LB/H | HOLDING CAPACITIES ARE 170,000 AND 250,000 LBS. BURNER CAPACITIES ARE 34,000,000 AND 48,000,000 BTU/HR. | Particulate Matter < 10 μ (PM10) | N | COMBUSTION FLUES ARE NOT CONTROLLED | 2.11 | LB/H |  | 9.25 | T/YR |  |  | LB/MMBTU
LA-0146 | SHELL CHEMICAL COMPANY - GEISMAR PLANT | SHELL CHEMICAL COMPANY - GEISMAR PLANT | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2000-05-10 | 2000 | SHELL CHEMICAL PROPOSES TO INSTALL AN IDENTICAL SHOP 3 UNIT AND AN OLEFINS FEED PROCESSING UNIT (OFP). THE OFP UNIT WILL UTILIZE INTERNAL OLEFINS (C15/16) FROM SHOP 1, 2, AND 3. THIS UNIT WILL ALSO CONVERT THE INTERNAL OLEFINS INTO HIGH SOLUBILITY OLEFINS | C15/C16 COLUMN REBOILER FURNACE | 13.31 | NATURAL GAS | 20.75 | MMBTU/H (LHV) | EMISSION POINT 120-99 | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES AND ENGINEERING DESIGN, CLEAN BURNING FUEL | 0.15 | LB/H |  | 0.53 | T/YR |  | 0.01 | LB/MMBTU
TX-0430 | DIAMOND SHAMROCK MCKEE PLANT | DIAMOND SHAMROCK REFINING CO. | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-05-23 | 2000 | LOCATED AT 6701 FM 119, SUNRAY, TX | HEATERS, REFINERY | 13.3 | NATURAL GAS |  |  | MULTIPLE HEATERS, FIRING NATURAL GAS AND REFINERY FUEL GAS | Particulate Matter < 10 μ (PM10) | P | LOW SULFUR REFINERY FUEL GAS AND PURCHASED NATURAL GAS |  |  | SEE NOTE | [6 empty] | BACT IS CLEAN FUEL, NO EMISSION RATE LIMITS.
MN-0039 | MINNESOTA CORN PROCESSORS | MINNESOTA CORN PROCESSORS | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2000-08-08 | 2000 | WET CORN MILLING, PRODUCTION OF CORN PRODUCTS | CARBON FURNACE - FRUCTOSE OR CORN SYRUP | 13.31 | NATURAL GAS | 5.2 | MMBTU/H | COMPLIANCE VERIFIED (STACK TESTING) 01/11/2001. SOX, CO, NOX AND VOC LIMITS SET IN EARLIER DETERMINATIONS. | Particulate Matter < 10 μ (PM10) | A | VENTURI SCRUBBER | 0.7 | LB/H |  |  |  |  | 0.13 | LB/MMBTU
TX-0363 | SAINT-GOBAIN VETROTEX AMERICA | VETROTEX AMERICA | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-11-13 | 2000 | VETROTEX AMERICA (VETROTEX) OPERATES A FIBER GLASS MANUFACTURING PLANT. THE VETROTEX PLANT PRODUCES FIBERGLASS REINFORCEMENT PRODUCTS AND IS COMPRISED OF FIVE GLASS MANUFACTURING FURNACES AND ASSOCIATED EQUIPMENT. THESE REFINFORCEMENT PRODUCTS ARE USED IN | BOILER NO 3 | 13.31 | NAT GAS |  |  |  | Particulate Matter < 10 μ (PM10) | N | NONE INDICATED | 0.08 | LB/H |  | 0.36 | T/YR |  |  |  | NOT AVAILABLE
SC-0065 | BROAD RIVER INVESTORS - GAFFNEY | BROAD RIVER INVESTORS, LLC | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 2000-12-21 | 2000 | ELECTRIC GENERATION FACILITY | HOT WATER HEATERS, NAT. GAS (2) | 13.31 | NATURAL GAS | 11 | MMBTU/H (EACH) |  | Particulate Matter < 10 μ (PM10) | P | CLEAN BURNING FUEL | 0.06 | LB/H | EACH
AR-0040 | DUKE ENERGY HOT SPRINGS | DUKE ENERGY HOT SPRINGS | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2000-12-29 | 2000 | NATURAL GAS FIRED POWER PLANT | BOILERS, AUXILIARY 2 | 13.31 | NATURAL GAS | 44.1 | MMBTU/H | THROUGHPUT FOR EACH | Particulate Matter < 10 μ (PM10) | P | CLEAN FUELS, PROPER COMBUSTION. LB/HR LIMIT FOR EACH BOILER. | 0.01 | LB/MMBTU |  | 0.5 | LB/H |  | 0.01 | LB/MMBTU
NM-0042 | DEMING ENERGY FACILITY | DUKE ENERGY LUNA | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2000-12-29 | 2000 | THIS FACILITY WILL GENERATE APPROXIMATELY 640 MW (NOMINAL). IT WILL BE A COMBINED CYCLE FACILITY CONSISTING OF 2 GENERAL ELECTRIC PG7241 (FA) COMBUSTION TURBINES, 2 DUCT BURNERS, AN AUXILIARY BOILER, AND A COOLING TOWER. THE NOX FROM THE COMBUSTION TURBIN | AUX-1 AUXILARY BOILER | 13.31 | NATURAL GAS | 44.1 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS ONLY, PRE-FILTERING - LIMIT INCLUDES BOTH FRONT END AND BACK END OF SAMPLING TRAIN | 0.4 | LB/H |  |  |  |  | 0.01 | LB/MM BTU
AR-0044 | ARKANSAS STEEL ASSOCIATES | ARKANSAS STEEL ASSOCIATES | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-01-05 | 2001 | STEEL MILL. | PREHEATERS, LADLE, (3) | 13.31 | NATURAL GAS | 4 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS COMBUSTION/GOOD COMBUSTION PRACTICES. | 0.2 | LB/H | combined | 0.7 | T/YR | combined |  |  | NOT AVAILABLE
AL-0168 | GENPOWER KELLEY LLC | GENPOWER KELLEY LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-01-12 | 2001 | ELECTRIC GENERATION | BOILER | 13.31 | NATURAL GAS | 83 | MMBTU/H | BOILER OPERATION LIMITED TO 1000 HR/YR | Particulate Matter < 10 μ (PM10) | P | EFFICIENT COMBUSTION | 0.01 | LB/MMBTU |  | 0.63 | LB/H |  | 0.01 | LB/MMBTU
IN-0090 | NUCOR STEEL | NUCOR STEEL | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-01-19 | 2001 |  | LADLE PREHEATERS | 13.31 | NATURAL GAS | 15 | MMBTU/HR EACH | TUNDISH PREHEATERS 6 MMBTU/H EACH, TUNDISH NOZZLE PREHEATERS 1 MMBTU/H EACH, TUNDISH DRYERS 9 MMBTU/H, TRANSITION PIECE PREHEATERS 15 MMBTU/H | Particulate Matter < 10 μ (PM10) | P | PERMIT LIMITATION IS USE OF NATURAL GAS OR PROPANE
IN-0090 | NUCOR STEEL | NUCOR STEEL | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-01-19 | 2001 |  | TUNDISH PREHEATERS (2) | 13.31 |  | 6 | MMBTU/H | THROUGHPUT FOR EACH | Particulate Matter < 10 μ (PM10) | P | PERMIT LIMITATION IS USE OF NATURAL GAS.
AL-0169 | BLOUNT MEGAWATT FACILITY | BLOUNT COUNTY ENERGY LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-02-05 | 2001 | ELECTRIC GENERATING FACILITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 40 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES | 0.02 | LB/MMBTU |  | 0.8 | LB/H |  | 0.02 | LB/MMBTU
OH-0258 | PRO TEC COATING COMPANY | USS GALVANIZING, INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-02-15 | 2001 | STEEL FINISHING MILL: METAL COATING WITH 2 NON-INSIGNIFICANT ANNEALING FURNACES AND 4 BOILERS | BOILERS (4) | 13.31 | NATURAL GAS | 20.9 | MMBTU/H | This permit is a modification to only 2 of the 4 boilers at this facility. Permit limits the same for each of the boilers being modified. | Particulate Matter < 10 μ (PM10) | N |  | 0.04 | LB/H | each | 0.18 | T/YR | each | 0.02 | LB/MMBTU |  | Limits are for each boiler. Only 2 of the 4 boilers modified in this permit.
OH-0255 | PSEG WATERFORD ENERGY LLC | PSEG WATERFORD ENERGY LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-03-29 | 2001 | THREE 170 MW NATURAL GAS-FIRED COMBUSTION TURBINES; STAGE I SIMPLE CYCLE TO STAGE II COMBINED CYCLE | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 85.2 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N |  | 0.43 | LB/H |  | 1.87 | T/YR |  | 0.005 | LB/MMBTU
OK-0074 | KIAMICHI ENERGY FACILITY | KIOWA POWER PARTNERS LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-05-01 | 2001 | ENERGY PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 27.5 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES AND DESIGN | 0.0076 | LB/MMBTU |  |  |  |  | 0.0076 | LB/MMBTU
IN-0086 | MIRANT SUGAR CREEK, LLC | MIRANT SUGAR CREEK, LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-05-09 | 2001 |  | AUXILARY BOILER, NATURAL GAS (2) | 13.31 | NATURAL GAS | 35 | MMBTU/H | AUXILARY BOILERS ARE LIMITED TO 5,000 H/YR OF OPERATION. THROUGH PUT IS FOR EACH BOILER. | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION. LB/H LIMIT IS FOR EACH BOILER. | 0.008 | LB/MMBTU |  | 0.28 | LB/H |  | 0.008 | LB/MMBTU
OK-0046 | THUNDERBIRD POWER PLT | THUNDERBIRD GENERATION LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-05-17 | 2001 | ELECTRICAL PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 20 | MMBTU/H | CO limits are not provided in permit. | Particulate Matter < 10 μ (PM10) | P | USE OF LOW ASH FUEL | 0.0074 | LB/MMBTU |  |  |  |  | 0.0074 | LB/MMBTU
NV-0039 | CHUCK LENZIE GENERATING STATION | NEVADA POWER COMPANY | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2001-06-01 | 2001 | A NEW ELECTRIC POWER PLANT CONSISTING OF FOUR COMBUSTION TURBINE GENERATORS, FOUR HEAT RECOVERY STEAM GENERATORS EACH WITH DUCT FIRING, AND TWO STEAM TURBINE GENERATORS FOR A TOTAL NOMINAL OUTPUT OF 1170 MW. THE FACILITY IS LOCATED AT 11405 U.S. HIGHWAY 9 | AUXILIARY BOILERS | 13.31 | NATURAL GAS | 44.1 | MMBTU/H | THESE (TWO) BOILERS WILL EACH BE OPERATED A MAXIMUM OF 6,000 HOURS PER YEAR ACCORDING TO THE APPLICATION FOR ATC. | Particulate Matter < 10 μ (PM10) | P | USE OF PIPELINE-QUALITY NATURAL GAS AND GOOD COMBUSTION CONTROL | 0.4 | LB/H |  |  |  |  | 0.009 | LB/MMBTU |  | EMISSION LIMIT 1 APPLIES TO EACH AUXILIARY BOILER.
IN-0087 | DUKE ENERGY, VIGO LLC | DUKE ENERGY, VIGO LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-06-06 | 2001 |  | AUXILARY BOILER, NATURAL GAS (2) | 13.31 | NATURAL GAS | 46 | MMBTU/H | NATURAL GAS FIRED BOILERS (THROUGHPUT FOR EACH) LIMITED TO 500 H/YR OPERATION | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION. LB/H LIMIT IS FOR EACH BOILER. | 0.0075 | LB/MMBTU |  | 0.35 | LB/H |  | 0.0075 | LB/MMBTU
AL-0190 | GE PLASTICS | GE PLASTICS | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-07-13 | 2001 | SYNTHETIC ORGANIC CHEMICAL MANUFACTURER THAT PRODUCES POLYCARBONATE RESIN PELLETS | FURNACE, HOT OIL, 10 MMBTU/H | 13.31 | NATURAL GAS | 10 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES | 0.1 | LB/H |  | 0.01 | LB/MMBTU |  | 0.01 | LB/MMBTU
AL-0190 | GE PLASTICS | GE PLASTICS | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-07-13 | 2001 | SYNTHETIC ORGANIC CHEMICAL MANUFACTURER THAT PRODUCES POLYCARBONATE RESIN PELLETS | FURNACE, HOT OIL, 20 MMBTU/H | 13.31 | NATURAL GAS | 20 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES | 0.1 | LB/H |  | 0.005 | LB/MMBTU |  | 0.005 | LB/MMBTU
OH-0263 | FREMONT ENERGY CENTER, LLC | CALPINE CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-08-09 | 2001 | TWO 180 MW COMBINED CYCLE TURBINES (2 HRSGS),USING SELECTIVE CATALYTIC REDUCTION (SCR) AND OXIDATION CATALYST | AUXILIARY BOILER | 13.31 | NATURAL GAS | 80 | MMBTU/H | Auxiliary boiler, natural gas-fired, 80 mmBtu/hr | Particulate Matter < 10 μ (PM10) | N |  | 0.41 | LB/H |  | 1.8 | T/YR |  | 0.0051 | LB / MMBTU
OK-0044 | SMITH POCOLA ENERGY PROJECT | SMITH COGENERATION OK INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-16 | 2001 | ELEC. POWER GENERATION | AUXILIARY BOILERS, (2) | 13.31 | NATURAL GAS | 48 | MMBTU/H | THROUGHPUT FOR EACH | Particulate Matter < 10 μ (PM10) | P | USE OF LOW ASH FUEL AND EFFICIENT COMBUSTION | 0.72 | LB/H | combined | 3.13 | T/YR | combined | 0.0076 | LB/MMBTU
OK-0054 | QUAD GRAPHICS OKC FACILITY | QUAD GRAPHICS INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-21 | 2001 | PRINT SHOP | BOILERS | 13.31 | NATURAL GAS | 62.77 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS FUEL, GOOD COMBUSTION PRACTICE | 0.63 | LB/H |  | 2.76 | T/YR
OK-0054 | QUAD GRAPHICS OKC FACILITY | QUAD GRAPHICS INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-21 | 2001 | PRINT SHOP | HEATERS/OXIDIZERS | 13.31 | NATURAL GAS | 16 | MMBTU/H | THESE UNITS INCLUDE HEATERS FOR INK DRYING AND OXIDIZERS ASSOCIATED WITH CONTROLLING EMISSIONS. EMISSION LIMITS ARE FOR PRODUCTS OF COMBUSTION. | Particulate Matter < 10 μ (PM10) | P | FUEL LIMITS AND MAINTENANCE PER MANUFACTURERS SPECS | 0.12 | LB/H | per Unit | 0.39 | T/YR | per Unit |  |  | Not Available
MD-0033 | KELSON RIDGE | FREE STATE ELECTRIC, LLC | MD | MARYLAND, OTHER | 2001-09-27 | 2001 | FACILITY WAS LICENSED; PROJECT WAS THEN CANCELLED BY APPLICANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 40 | MMBTU/H | EMISSIONS LIMITS APPLY TO EACH BOILER | Particulate Matter < 10 μ (PM10) | B | EXCLUSIVE USE OF NATURAL GAS, ADVANCED DRY LOW-NOX BURNERS; GOOD COMBUSTION CONTROLS ANNUAL FUEL USE LIMIT |  |  | SEE NOTE | [6 empty] | HEAT INPUT TO THE AUXILIARY BOILERS (2) SHALL BE LIMITED TO 210,240 MMBTU FOR ANY CONSECUTIVE 12-MONTH PERIOD
AL-0179 | TENASKA TALLADEGA GENERATING STATION | TENASKA ALABAMA IV PARTNERS, LP | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-10-03 | 2001 | NATURAL GAS/DISTILLATE OIL FIRED COMBINED CYCLE ELECTRIC GENERATING FACILITY. | 30 MMBTU/HR AUXILIARY BOILER | 13.31 | NATURAL GAS | 30 | MMBTU/H | Operation limited to 1000 h/yr. | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS AS EXCLUSIVE FUEL | 0.005 | LB/MMBTU |  | 0.2 | LB/H |  | 0.005 | LB/MMBTU
IN-0110 | COGENTRIX LAWRENCE CO., LLC | COGENTRIX LAWRENCE CO., LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-10-05 | 2001 | POWER PLANT | BOILER, AUXILIARY, NATURAL GAS | 13.31 | NATURAL GAS | 35 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | CLEAN FUEL, GOOD COMBUSTION PRACTICES | 0.02 | LB/MMBTU |  | 0.7 | LB/H |  | 0.02 | LB/MMBTU
OH-0265 | DRESDEN ENERGY LLC | Dresden Energy | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-10-16 | 2001 | TWO 171.7 MW NATURAL GAS AND FUEL OIL- FIRED COMBUSTION TURBINES, COMBINED CYCLE; 49 MMBTU/HR NATURAL GAS FIRED BOILER; 2,250,000 GALLON FIXED ROOF STORAGE TANK FOR #2 FUEL OIL. | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 49 | MMBTU/H | Boiler is restricted to 800 hour of operation per a rolling 12 months. | Particulate Matter < 10 μ (PM10) | N |  | 0.38 | LB/H |  | 0.15 | T/YR |  | 0.0077 | LB/MMBTU | calculated | Boiler is restricted to 800 hours or operation per a rolling 12 months.
OK-0043 | WEBERS FALLS ENERGY FACILITY | ENERGETIX | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-10-22 | 2001 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 30 | MMBTU/H | BOILER OPERATIONS LIMITED TO 3,000 HOURS/YEAR. | Particulate Matter < 10 μ (PM10) | P | USE OF LOW ASH FUEL & EFFICIENT COMBUSTION | 0.01 | LB/MMBTU |  |  |  |  | 0.01 | LB/MMBTU
AL-0181 | DUKE ENERGY AUTAUGA, LLC | DUKE ENERGY AUTAUGA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-10-23 | 2001 | COMBINED CYCLE ELECTRIC GENERATING PLANT. | 31.4 MMBTU/HR NATURAL GAS FIRED BOILER | 13.31 | NATURAL GAS | 31.4 | MMBTU/H | Operation limited to 2500 hrs/yr. | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS IS EXCLUSIVE FUEL. | 0.009 | LB/MMBTU |  | 0.31 | LB/H |  | 0.0098726 | LB/MMBTU
*WA-0292 | SATSOP COMBUSTION TURBINE PROJECT | GRAYS HARBOR ENERGY LLC | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2001-10-23 | 2001 | GE F7 TURBINE BASED COMBINED CYCLE NATURAL GAS ONLY FUELED COMBUSTION TURBINE INCLUDES COOLING TOWER AND EMERGENCY ICE GENERATOR AND FIRE WATER ENGINES | AUXILIARY BOILER | 13.31 | NAT GAS | 29.3 | MMBTU/H | 29.3 MMBTU/H IS THE DESIGN HEAT INPUT RATE FOR THE BOILER, AS PROVIDED BY THE STATE CONTACT PERSON. | Particulate Matter < 10 μ (PM10) | N |  | 7 | LB/D | FILTERABLE + CONDENSIBLE, ANNUAL AVG | [5 empty] | NOT AVAILABLE
OK-0071 | MCCLAIN ENERGY FACILITY | NRG MCCLAIN LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-10-25 | 2001 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | USE OF LOW ASH FUELS | 0.009 | LB/MMBTU |  |  |  |  | 0.009 | LB/MMBTU
TX-0378 | LA PORTE POLYPROPYLENE PLANT | ATOFINA PETROCHEMICALS INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-11-05 | 2001 | ATOFINA PROPOSES TO INSTALL A 60 MMBTU/H PACKAGE BOILER TO PROVIDE NEEDED STEAM CAPACITY. THE BURNER WILL MEET ESAD LIMIT OF 0.015 LB NOX/MMBTU FOR HOUSTON/GALVESTON. UPON STARTUP OF EPN ES-206, THE 40 MMBTU/H TEMPORARY BOILER (EPN TEMPBOILER) SHALL BE RE | PACKAGE BOILER BO-4 | 13.31 | NAT GAS | 60 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N | NONE INDICATED | 0.48 | LB/H |  | 2.11 | T/YR |  | 0.008 | LB/MMBTU | CALCULATED
IN-0097 | CARGILL, INC | CARGILL, INC | IN | INDIANA, OTHER | 2001-12-03 | 2001 | GRAIN ELEVATOR AND SOYBEAN OIL EXTRACTION AND PROTEIN RICH PRODUCTS. | BOILERS 1 & 2 | 13.31 | NATURAL GAS | 75 | MMBTU/H | CEMS, WHEN BURNING RESIDUAL OIL. LIMITS ON NO.2, 3 & 4 FUEL OIL USAGES FOR SO2 AND NOX. | Particulate Matter < 10 μ (PM10) | N |  | 794.13 | LB/MMCF NG | [6 empty] | NOT AVAILABLE
AL-0180 | DUKE ENERGY DALE, LLC | DUKE ENERGY DALE, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-12-11 | 2001 | NATURAL GAS FIRED COMBINED CYCLE ELECTRIC GENERATING PLANT. | 35 MMBTU/HR NAT. GAS FIRED AUXILIARY BOILER | 13.31 | NATURAL GAS | 35 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS AS EXCLUSIVE FUEL. | 0.009 | LB/MMBTU |  | 0.31 | LB/H |  | 0.0088571 | LB/MMBTU
*PA-0210 | DART CONTAINER CORP OF PA | DART CONTAINER CORP OF PA | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2001-12-14 | 2001 | NEW BOILERS ARE SUBJECT TO 40 CFR, PART 60, SUBPART DC AND BAT AND 25 PA CODE , CHAPTER 123. | BOILER, (2) | 13.31 | NATURAL GAS | 33.5 | MMBTU/H | CLEAVER BROOKS BOILERS. Boilers subject to NSPS/BAT/SIP | Particulate Matter < 10 μ (PM10) | N |  | 0.4 | LB/MMBTU |  |  |  |  | 0.4 | LB/MMBTU
OH-0257 | JACKSON COUNTY POWER, LLC | JACKSON COUNTY POWER, LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-12-27 | 2001 | FOUR 305 MW NATURAL-GAS FIRED COMBUSTION TURBINES, COMBINED CYCLE, WITH DLN AND SCR | AUXILIARY BOILER | 13.31 | NATURAL GAS | 76 | MMBTU/H | Limited to 3000 hours of operation per rolling 12 month period. | Particulate Matter < 10 μ (PM10) | N |  | 1.52 | LB/H |  | 2.28 | T/YR |  | 0.02 | LB/MMBTU
NC-0094 | GENPOWER EARLEYS, LLC | GENPOWER EARLEYS, LLC | NC | NORTH CAROLINA DIV OF ENV MGMT | 2002-01-09 | 2002 | POWER GENERATING FACILITY | BOILER, AUXILIARY, NATURAL GAS | 13.31 | NATURAL GAS | 83 | MMBTU/H | Auxiliary boiler supplies steam for start up, and maintain operating temperatures for HSRGs and steam turbine when the CTs are off line. Boiler is allowed to operate < 1000 h/yr. | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION AND DESIGN | 0.62 | LB/H |  |  |  |  | 0.0075 | LB/MMBTU | calculated
LA-0174 | PORT HUDSON OPERATIONS | GEORGIA-PACIFIC CORPORATION | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-01-25 | 2002 | PULP MILL | POWER BOILER NO. 2 | 13.31 | NAT GAS | 65.5 | MMBTU/H | EMISSION POINT NO. 6. | Particulate Matter < 10 μ (PM10) | P | FIRED BY NATURAL GAS | 3.33 | LB/H |  | 2.2 | T/YR |  | 0.05 | LB/MMBTU
OK-0056 | HORSESHOE ENERGY PROJECT | MUSTANG POWER LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-02-12 | 2002 | POWER PLANT | AUXILIARY BOILERS | 13.31 | NATURAL GAS | 0 |  |  | Particulate Matter < 10 μ (PM10) | P | LOW ASH FUEL (NATURAL GAS) | 0.0076 | LB/MMBTU |  |  |  |  | 0.0076 | LB/MMBTU
TX-0388 | SAND HILL ENERGY CENTER | AUSTIN ELECTRIC UTILITY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-02-12 | 2002 | ELECTRIC POWER GENERATOR CONSISTING OF NATURAL GAS-FIRED COMBUSTION TURBINE WITH HRSG. | INLET AIR HEATERS (3) | 13.31 |  |  |  |  | Particulate Matter < 10 μ (PM10) | N |  | 0.04 | LB/H |  | 0.02 | T/YR
LA-0120 | GEISMAR PLANT | SHELL CHEMICAL LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-02-26 | 2002 | RE-EVALUATION OF BACT FOR OLEFIN AND ALCOHOL PROJECT. THIS PROJECT WAS APPROVED EARLIER UNDER PSD PERMIT NO. PSD-LA-647 (M-1) DATED JUNE 26, 2001. THE CURRENT PERMIT IS FOR THE MODIFICATION OF REGENERATIVE FURNACE, EMISSION POINT 620-99, TO INCLUDE PREMIX | REGENERATOR FURNACE #620-99 | 13.31 | NATURAL GAS | 3.3 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES | 0.02 | LB/H |  | 0.07 | T/YR |  | 0.01 | LB/MMBTU
LA-0120 | GEISMAR PLANT | SHELL CHEMICAL LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-02-26 | 2002 | RE-EVALUATION OF BACT FOR OLEFIN AND ALCOHOL PROJECT. THIS PROJECT WAS APPROVED EARLIER UNDER PSD PERMIT NO. PSD-LA-647 (M-1) DATED JUNE 26, 2001. THE CURRENT PERMIT IS FOR THE MODIFICATION OF REGENERATIVE FURNACE, EMISSION POINT 620-99, TO INCLUDE PREMIX | SYLTHERM FURNACE, #321-99 | 13.31 | NATURAL GAS | 53 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES | 0.38 | LB/H |  | 1.35 | T/YR |  | 0.01 | LB/MMBTU
LA-0120 | GEISMAR PLANT | SHELL CHEMICAL LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-02-26 | 2002 | RE-EVALUATION OF BACT FOR OLEFIN AND ALCOHOL PROJECT. THIS PROJECT WAS APPROVED EARLIER UNDER PSD PERMIT NO. PSD-LA-647 (M-1) DATED JUNE 26, 2001. THE CURRENT PERMIT IS FOR THE MODIFICATION OF REGENERATIVE FURNACE, EMISSION POINT 620-99, TO INCLUDE PREMIX | HOT OIL FURNACE, #621-99 | 13.31 | NATURAL GAS | 20 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES | 0.15 | LB/H |  | 0.51 | T/YR |  | 0.01 | LB/MMBTU
AR-0051 | DUKE ENERGY-JACKSON FACILITY | DUKE ENERGY | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-04-01 | 2002 | 620 MW NATURAL GAS TURBINE ELECTRIC UTILITY PLANT. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | GOOD OPERATING PRACTICE | 0.01 | LB/MMBTU |  |  |  |  | 0.01 | LB/MMBTU
TN-0153 | WILLIAMS REFINING & MARKETING, L.L.C. | WILLIAMS REFINING & MARKETING, L.L.C. | TN | MEMPHIS AND SHELBY CO HEALTH DEPT, TN | 2002-04-03 | 2002 | PETROLEUM REFINERY | BOILER, NO. 9 | 13.31 | NATURAL GAS | 95 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0075 | LB/MMBTU |  |  |  |  | 0.0075 | LB/MMBTU
TN-0153 | WILLIAMS REFINING & MARKETING, L.L.C. | WILLIAMS REFINING & MARKETING, L.L.C. | TN | MEMPHIS AND SHELBY CO HEALTH DEPT, TN | 2002-04-03 | 2002 | PETROLEUM REFINERY | CCR STABILIZATION REBOILER | 13.31 | NATURAL GAS | 54 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N |  | 0.005 | LB/MMBTU |  |  |  |  | 0.005 | LB/MMBTU
IA-0058 | GREATER DES MOINES ENERGY CENTER | MIDAMERICAN ENERGY | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-04-10 | 2002 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 68 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0076 | LB/MMBTU |  | 2.27 | T/YR |  | 0.0076 | LB/MMBTU
OK-0072 | REDBUD POWER PLT | REDBUD ENERGY LP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-05-06 | 2002 | ELECTRICAL GENERATOR | AUXILIARY BOILER | 13.31 | NATURAL GAS | 93 | MMBUT/H |  | Particulate Matter < 10 μ (PM10) | P | USE OF NATURAL GAS/LOW ASH FUEL AND EFFICIENT COMBUSTION | 0.0053 | LB/MMBTU |  |  |  |  | 0.0053 | LB/MMBTU
OH-0264 | NORTON ENERGY STORAGE, LLC | NORTON ENERGY | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-05-23 | 2002 | NINE 300 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE WITH DLN AND SCR; TEN 11.45 MMBTU/H NATURAL GAS-FIRED FUEL SUPPLY HEATERS/BOILERS; SEVEN 12.84 MMBTU/H NATURAL GAS-FIRED RECUPERATOR PRE HEATERS/BOILERS | RECUPERATOR PRE-HEATERS (9) | 13.31 | NATURAL GAS | 12.84 | MMBTU/H | Each boiler is limited to 100 hour of operation per rolling 12 months. | Particulate Matter < 10 μ (PM10) | N |  | 0.098 | LB/H |  | 0.005 | T/YR |  | 0.008 | LB/MMBTU |  | Limits are for each boiler. Each boiler is retricted to 100 hours of operation.
OH-0264 | NORTON ENERGY STORAGE, LLC | NORTON ENERGY | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-05-23 | 2002 | NINE 300 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE WITH DLN AND SCR; TEN 11.45 MMBTU/H NATURAL GAS-FIRED FUEL SUPPLY HEATERS/BOILERS; SEVEN 12.84 MMBTU/H NATURAL GAS-FIRED RECUPERATOR PRE HEATERS/BOILERS | FUEL SUPPLY HEATERS (9) | 13.31 | NATURAL GAS | 11.45 | MMBTU/H | Each fuel supply heater is limited to a maximum annual cumulative fuel heat input of 47,630 mmBtu per rolling 12 months. | Particulate Matter < 10 μ (PM10) | N |  | 0.087 | LB/H |  | 0.18 | T/YR |  | 0.008 | LB/MMBTU |  | Limits are for each heater.
OK-0070 | GENOVA OK I POWER PROJECT | GENOVA OKLAHOMA LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-06-13 | 2002 | COMBINED CYCLE POWER PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | LOW ASH FUEL AND EFFICIENT COMBUSTION | 0.01 | LB/MMBTU |  |  |  |  | 0.01 | LB/MMBTU
NM-0044 | CLOVIS ENERGY FACILITY | DUKE ENERGY CURRY LLC | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2002-06-27 | 2002 | THIS IS A 1,200 MW COMBINED CYCLE MERCHANT POWER PLANT. | AUXILIARY BOILERS (AUX-1 AND AUX-2) | 13.31 | NATURAL GAS | 33 | MMBTU/H | Emission limits are for each (Aux-1 and Aux-2) Auxiliary Boiler. | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS ONLY, GOOD COMBUSTION PRACTICE | 0.3 | LB/H |  |  |  |  | 0.009 | LB/MMBTU | calculated
AL-0185 | BARTON SHOALS ENERGY | BARTON SHOALS ENERGY, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2002-07-12 | 2002 | ELECTRIC GENERATION - NATURAL GAS FIRED COMBINED CYCLE | TWO (2) 40 MMBTU/H AUXILIARY BOILERS | 13.31 | NATURAL GAS | 40 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS ONLY | 0.0075 | LB/MMBTU |  | 0.3 | LB/H |  | 0.007 | LB/MMBTU
IA-0060 | HAWKEYE GENERATING, LLC | ENTERGY | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-07-23 | 2002 | ENTERGY IS INSTALLING TWO GE 7FA (170MW) NATURAL GAS FIRED TURBINES. THEY ARE REQUIRED TO INSTALL SCR FOR CONTROL OF NOX (3 PPMVD, 3 HOUR AVG. TIME) AND CATALYTIC OXIDATION FOR THE CONTROL OF CO (5 PPMVD, 3 HOUR AVG. TIME) FOR COMBINED CYCLE OPERATION. SI | AUXILIARY BOILER (48.5 MMBTU/H) | 13.31 | NATUAL GAS | 48.69 | MILLION CF/YR |  | Particulate Matter < 10 μ (PM10) | B | GCP | 0.007 | LB/MMBTU |  |  |  |  | 0.012 | LB/MMBTU
AR-0070 | GENOVA ARKANSAS I, LLC | GENOVA ARKANSAS I, LLC | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-08-23 | 2002 | COMBINED CYCLE POWER PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICE | 0.012 | LB/MMBTU |  |  |  |  | 0.012 | LB/MMBTU
VA-0261 | CPV CUNNINGHAM CREEK | COMPETITIVE POWER VENTURE | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-09-06 | 2002 | TURBINES USED TO PRODUCE ELECTRICITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 80 | MMBTU/H | one auxiliary boiler | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES. | 0.58 | LB/H |  | 0.87 | T/YR |  | 0.007 | LB/MMBTU
OH-0248 | LAWRENCE ENERGY | CALPINE CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-09-24 | 2002 | THREE 180 MW GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE, WITH DLN, SCR AND OXIDATION CATALYST | BOILER | 13.31 | NATURAL GAS | 99 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N |  | 0.76 | LB/H |  | 0.0076 | LB/MMBTU |  | 0.0076 | LB/MMBTU |  | Limits are for each boiler. Additional limit: 10% Opacity as a 6 minute average.
AL-0192 | HONDA MANUFACTURING OF ALABAMA, LLC | HONDA MANUFACTURING OF ALABAMA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2002-10-18 | 2002 | AUTOMOBILE MANUFACTURING PLANT | BOILERS, NATURAL GAS, (3) | 13.31 | NATURAL GAS | 30 | MMBTU/H | throughput for each boiler. BACT for CO, NOx, PM10, and VE | Particulate Matter < 10 μ (PM10) | P | CLEAN FUEL, GOOD COMBUSTION | 0.228 | LB/H |  | 0.0076 | LB/MMBTU |  | 0.0076 | LB/MMBTU
WI-0195 | SENA NIAGARA MILL | STORA ENSO NORTH AMERICA | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2002-10-18 | 2002 |  | PROCESS HEATER, PAPER MACHINE P51 | 13.31 | NATURAL GAS | 34.4 | MMBTU/H | Throughput is total for natural gas IR and flotation dryers. | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS AS FUEL | 0.023 | LB/MMBTU |  |  |  |  | 0.023 | LB/MMBTU
NJ-0062 | CONSOLIDATE EDISON DEVELOPMENT (CED) | CONSOLIDATED EDISON DVPMT.- LAKEWOOD GEN. FACILITY | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2002-10-22 | 2002 | POWER GENERATION | FUEL GAS HEATERS (3 UNITS) | 13.31 | NATURAL GAS | 4.62 | MMBTU/H | INSTALLATION OF 3 NEW FUEL GAS HEATERS@ 4.62 MMBTU/HR EACH. FUEL: NATURAL GAS. | Particulate Matter < 10 μ (PM10) | N | THE USE OF NATURAL GAS IS CONSIDERED THE MOST EFFECTIVE MEANS FOR CONTROLLING PM-10 EMISSIONS. | 0.05 | LB/H |  | 0.011 | LB/MMBTU |  | 0.011 | LB/MMBTU
VA-0255 | VA POWER - POSSUM POINT | Virginia Power | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-11-18 | 2002 | THIE PERMIT WAS AMENDED AND APPROVED ON 11/18/2002 FROM THE PERMIT THAT WAS DATED 10/05/2001. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 99 | MMBTU/H | 2 Auxiliary boilers. | Particulate Matter < 10 μ (PM10) | P | CLEAN FUEL AND GOOD COMBUSTION PRACTICES. | 0.7 | LB/H | EACH UNIT | 3.7 | T/YR | COMBINED UNITS | 0.007 | LB/MMBTU | EACH UNIT
TX-0408 | INDIAN ROCK GATHERING COMPANY LP | INDIAN ROCK GATHERING COMPANY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-11-22 | 2002 | NATURAL GAS PROCESSING FACILITY | AUXILIARY BOILER, (2) | 13.31 | NATURAL GAS | 6 | MMBTU/H | BOILERS ARE UNCONTROLLED BECAUSE BOILER DUTY IS <40 MMBTU/H. | Particulate Matter < 10 μ (PM10) | N |  | 0.05 | LB/H | EACH | 0.2 | T/YR | EACH | 0.0083 | LB/MMBTU |  | UNCONTROLLED BECAUSE BOILER IS LESS THAN 40 MMBTU/H.
VA-0243 | STANLEY FURNITURE |  | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-12-01 | 2002 | WOOD HOUSEHOLD FURNITURE MFG. | BOILER, NAT GAS & OIL | 13.31 | NATURAL GAS | 26.5 | MMBTU/H | KEWANEE NATURAL GAS/DISTILLATE OIL BOILER. THROUGHPUT 26.5 MMBTU/HR - 450,000 GAL #2 OIL. ADDITIONAL SCC, 10200502. FOR ALL POLLUTANTS, NO CONTROLS, EMISSION LIMITS IN T/YR ONLY | Particulate Matter < 10 μ (PM10) | N | NO CONTROLS LISTED. EMISSION LIMITS IN T/YR ONLY | 0.9 | T/YR | [6 empty] | NOT AVAILABLE
TX-0392 | LUCITE BEAUMONT | INEOS ACRYLICS, INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-09 | 2002 | SULFURIC ACID REGENERATION FACILITY | NO. 2 PRE-HEATER | 13.31 | NATURAL GAS |  |  |  | Particulate Matter < 10 μ (PM10) | N |  | 0.04 | LB/H |  | 0.18 | T/YR
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | HEAT TRANSFER FLUID HEATER, H202 | 13.31 | NATURAL GAS | 31 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N | NONE INDICATED | 0.23 | LB/H |  | 1.02 | T/YR |  | 0.01 | LB/MMBTU | CALCULATED USING THROUGHPUT
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | HEAT TRANSFER FLUID HEATER, H2202 | 13.31 | NATURAL GAS | 31 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N | NONE INDICATED | 0.23 | LB/H |  | 1.02 | T/YR |  | 0.007 | LB/MMBTU | CALCULATED USING THROUGHPUT
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | (2) STEAM BOILERS, X-426A AND X-426B | 13.31 | NATURAL GAS | 15.8 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N | NONE INDICATED | 0.12 | LB/H | EACH | 0.53 | T/YR | EACH | 0.008 | LB/MMBTU | EACH, CALCULATED USING THROUGHPUT
IA-0062 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT (IPL) | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-12-20 | 2002 | PERMITS WERE AMENDED ON 6/26/03. RBLC ID IA-0062 WAS CORRECTED AS MOST OF THE CHANGES WERE MINOR (BASED ON OPERATIONAL & DESIGN CHANGES BEING MADE AS PLANT IS CONSTRUCTED). THE NEW DEW POINT HEATER HAS BEEN GIVEN A NEW RBLC ID. | GAS HEATER, (2) | 13.31 | NATURAL GAS | 16.4 | MMBTU/H | Natural Gas fired Heaters, 16.4 MMBTU/HR capacity for each. Operating hours reduced from 8760 hours to 6000 hours each. | Particulate Matter < 10 μ (PM10) | P | LOW ASH FUEL | 0.0075 | LB/MMBTU |  |  |  |  | 0.0075 | LB/MMBTU
IA-0062 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT (IPL) | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-12-20 | 2002 | PERMITS WERE AMENDED ON 6/26/03. RBLC ID IA-0062 WAS CORRECTED AS MOST OF THE CHANGES WERE MINOR (BASED ON OPERATIONAL & DESIGN CHANGES BEING MADE AS PLANT IS CONSTRUCTED). THE NEW DEW POINT HEATER HAS BEEN GIVEN A NEW RBLC ID. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 68 | MMBTU/H | Limited to 6000 hours of operation per year. | Particulate Matter < 10 μ (PM10) | P | LOW ASH FUEL, NG | 0.0075 | LB/MMBTU |  |  |  |  | 0.0075 | LB/MMBTU
TX-0389 | BAYTOWN CARBON BLACK PLANT | DEGUSSA ENGINEERED CARBONS, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-31 | 2002 |  | BACK-UP BOILER | 13.31 | NATURAL GAS | 13.4 | MMBUT/H |  | Particulate Matter < 10 μ (PM10) | N |  | 0.1 | LB/H |  | 0.44 | T/YR |  | 0.0074627 | LB/MMBTU
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HOT OIL HEATER, EPN6 | 13.31 | NAT GAS | 12 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N | NONE INDICATED | 0.11 | LB/H |  | 0.4 | T/YR |  | 0.0092 | LB/MMBTU | CALCULATED, SEE NOTES | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | GLYCOL REBOILER, EPN11 | 13.31 | NAT GAS | 2.5 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N | NONE INDICATED | 0.02 | LB/H |  | 0.08 | T/YR |  | 0.008 | LB/MMBTU |  | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HOT OIL HEATER, EPN26 | 13.31 | NAT GAS | 32.5 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N | NONE INDICATED | 0.29 | LB/H |  | 1.06 | T/YR |  | 0.009 | LB/MMBTU | SEE NOTE | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HP TEG FIREBOX, EPN30 | 13.31 | NAT GAS | 3 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N | NONE INDICATED | 0.02 | LB/H |  | 0.1 | T/YR |  | 0.006 | LB/MMBTU |  | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
LA-0193 | STYRENE MONOMER PLANT | COS-MAR COMPANY | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2003-02-11 | 2003 | PLANT PRODUCES STYRENE MONOMER THROUGH THE ALKYLATION OF BENZENE AND ETHYLENE TO ETHYLBENZENE, FOLLOWED BY DEHYDROGENATION OF ETHYLBENZENE TO STYRENE. PROJECT EXPANDS STYRENE MONOMER CAPACITY FROM 1.9 TO 2.55 BILLION POUNDS PER YEAR. | REGENERATION GAS HEATER HS-2102 | 13.31 |  | 14.4 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | USE OF CLEAN BURNING FUELS (NATURAL GAS) | 0.11 | LB/H | HOURLY MAXIMUM |  |  |  | 0.01 | LB/MMBTU | ANNUAL AVERAGE | ANNUAL PM10 EMISSIONS FROM THE FOLLOWING SOURCES ARE CAPPED AT 108.3 TPY: 145-02-A, 145-02-B, 145-02-C, 145-02-D, 145-02-E, 145-02-F, 145-02-G, 145-02-H, 145-02-I, 145-02-J, 145-02-K, 145-02-L, 145-02-M, 145-02-N, 145-02-O, & 145-02-P.
LA-0193 | STYRENE MONOMER PLANT | COS-MAR COMPANY | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2003-02-11 | 2003 | PLANT PRODUCES STYRENE MONOMER THROUGH THE ALKYLATION OF BENZENE AND ETHYLENE TO ETHYLBENZENE, FOLLOWED BY DEHYDROGENATION OF ETHYLBENZENE TO STYRENE. PROJECT EXPANDS STYRENE MONOMER CAPACITY FROM 1.9 TO 2.55 BILLION POUNDS PER YEAR. | PEB RECOVERY COLUMN HEATER HS-2105 | 13.31 |  | 25.2 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | USE OF CLEAN BURNING FUELS (NATURAL GAS) | 0.19 | LB/H | HOURLY MAXIMUM |  |  |  | 0.01 | LB/MMBTU | ANNUAL AVERAGE | ANNUAL PM10 EMISSIONS FROM THE FOLLOWING SOURCES ARE CAPPED AT 108.3 TPY: 145-02-A, 145-02-B, 145-02-C, 145-02-D, 145-02-E, 145-02-F, 145-02-G, 145-02-H, 145-02-I, 145-02-J, 145-02-K, 145-02-L, 145-02-M, 145-02-N, 145-02-O, & 145-02-P.
OR-0040 | KLAMATH GENERATION, LLC | KLAMATH GENERATION, LLC | OR | OREGON DEPT OF ENVIRONMENTAL QUALITY | 2003-03-12 | 2003 | POWER GENERATION FACILITY | BOILER, AUXILIARY, NATURAL GAS | 13.31 | NATURAL GAS | 50000 | LB/H | Throughput is lb/h of steam. Boiler provides steam for standby and startup conditions. | Particulate Matter < 10 μ (PM10) | N |  | 0.0042 | LB/MMBTU |  |  |  |  | 0.0042 | LB/MMBTU
OK-0090 | DUKE ENERGY STEPHENS, LLC STEPHENS ENERGY | DUKE ENERGY | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2003-03-21 | 2003 | MERCHANT POWER PLANT - NOMINAL TOTAL OF 620 MW. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | USE OF LOW ASH FUEL AND EFFICIENT COMBUSTION | 0.01 | LB/MMBTU |  |  |  |  | 0.01 | LB/MMBTU
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 | 2003 |  | BOILER NO. 1 | 13.31 | NATURAL GAS | 43.2 | MMBTU/H | One of two boilers | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES | 0.32 | LB/H | each unit |  |  |  | 0.007 | LB/MMBTU |  | one of two units.
OH-0276 | CHARTER STEEL | CHARTER MANUFACTURING CO., INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-04-14 | 2003 | NEW MELT SHOP AT EXISTING FACILITY, INCLUDES NEW: ELECTRIC ARC FURNACE; LADLE METALLURGY FURNACE; VACUUM OXYGEN DEGASSER (VOD); VOC BOILER; CONTINUOUS CASTING MACHINES; 3 SILOS; 6 LADLE PREHEATERS; CUT-OFF-TORCH; 3 TUNDISH PREHEATERS; PROCESS SPACE HEATER | BOILER FOR VACUUM OXYGEN DEGASSER VESSEL | 13.31 | NATURAL GAS | 25 | MMBTU/H | VACUUM OXYGEN DEGASSER VESSEL BOILER, WITH LOW NOX BURNER | Particulate Matter < 10 μ (PM10) | N |  | 0.19 | LB/H | FROM NATURAL GAS COMBUSTION | 0.83 | T/YR | FROM NATURAL GAS COMBUSTION |  |  | NOT AVAILABLE
IA-0068 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT - EMERY GENERATING STATI | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2003-06-26 | 2003 | IPL CHANGED NAMES FROM THE POWER IOWA ENERGY CENTER (PIEC) TO THE EMERY GENERATING STATION. | GAS HEATER | 13.31 | NATURAL GAS | 9 | MMBTU/H | One natural gas dew point heater is added. | Particulate Matter < 10 μ (PM10) | P | LOW ASH FUEL, NATURAL GAS | 0.0075 | LB/MMBTU |  | 0.29 | T/YR |  | 0.0075 | LB/MMBTU
TX-0458 | JACK COUNTY POWER PLANT | DUKE ENERGY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-07-22 | 2003 | DUKE ENERGY JACK, L.P. IS CONSTRUCTING A 620 MW COMBINED CYCLE POWER PLANT. TWO COMBUSTION TURBINES WILL EACH PROVIDE APPROXIMATELY 170 MW OF ELECTRICITY. A 550 MMBTU/HR DUCT BURNER ON EACH TURBINE EXHAUST STREAM WILL ADD SUPPLEMENTAL HEAT TO THE HEAT REC | AUXILIARY BOILER | 13.31 | NATURAL GAS | 36 | mmbtu/h |  | Particulate Matter < 10 μ (PM10) | N |  | 0.4 | LB/H |  | 1.1 | T/YR |  | 0.011111 | LB/MMBTU
OH-0254 | DUKE ENERGY WASHINGTON COUNTY LLC | DUKE ENERGY NORTH AMERICA | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-08-14 | 2003 | TWO 170 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE | BOILER | 13.31 | NATURAL GAS | 30.6 | MMBTU/H | THE MAXIMUM ANNUAL FUEL HEAT INPUT SHALL NOT EXCEED 128,000 MMBTU/ROLLING 12-MONTHS | Particulate Matter < 10 μ (PM10) | N |  | 0.31 | LB/H |  | 0.64 | T/ROLLING 12-MONTHS |  | 0.01 | LB/MMBTU
AZ-0049 | LA PAZ GENERATING FACILITY | ALLEGHENY ENERGY SUPPLY LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2003-09-04 | 2003 | NATURAL GAS FIRED, COMBINED CYCLE GENERATING STATION | AUXILIARY BOILER FOR GE TURBINE | 13.31 | NATURAL GAS | 41 | MMBTU/H | THIS BOILER IS TO BE USED IF THE GE TURBINE SETUP IS SELECTED. | Particulate Matter < 10 μ (PM10) | N |  | 0.015 | LB/MMBTU |  |  |  |  | 0.015 | LB/MMBTU
AZ-0049 | LA PAZ GENERATING FACILITY | ALLEGHENY ENERGY SUPPLY LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2003-09-04 | 2003 | NATURAL GAS FIRED, COMBINED CYCLE GENERATING STATION | AUXILIARY BOILER FOR SIEMENS TURBINES | 13.31 | NATURAL GAS | 55.34 | MMBTU/H | THIS BOILER IS FOR USE WHEN THE SIEMENS TURBINE SYSTEM IS SELECTED. | Particulate Matter < 10 μ (PM10) | N |  | 0.015 | LB/MMBTU |  |  |  |  | 0.015 | LB/MMBTU
IN-0108 | NUCOR STEEL | NUCOR STEEL | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2003-11-21 | 2003 | STEEL MINI MILL | BOILER, NATURAL GAS, (2) | 13.31 | NATURAL GAS | 34 | MMBTU/H | Throughput for each. Propane is backup fuel. These boilers supply steam to the entire cold mill area of the plant. Subject to NSPS Subpart Dc | Particulate Matter < 10 μ (PM10) | P | COMPLIANCE BY USING NATURAL GAS | 0.0076 | LB/MMBTU |  |  |  |  | 0.0076 | LB/MMBTU
MN-0054 | MANKATO ENERGY CENTER |  | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2003-12-04 | 2003 | COMBINED CYCLE GAS TURBINE ELECTRIC POWER PLANT. TWO IDENTICAL GE FRAME F7A GAS TURBINES EACH WITH HRSG W/DUCT BURNERS FEEDING STEAM TO COMMON STEAM TURBINES. PRIMARY FUEL IS NG, NO. 2 VERY LOW SULFUR DISTILLATE OIL FOR BACKUP. ALSO, AUX. BOILER, DIESEL E | BOILER, COMMERCIAL | 13.31 | NATURAL GAS | 70 | MMBTU/H | NATURAL GAS ONLY | Particulate Matter < 10 μ (PM10) | N | CLEAN FUELS | 0.008 | LB/MMBTU |  |  |  |  | 0.01 | LB/MMBTU
OK-0097 | QUAD GRAPHICS OKC FAC | QUAD GRAPHICS INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2004-02-03 | 2004 | COMMERCIAL PRINTING | BOILERS, NATURAL GAS, STEAM GENERATORS | 13.31 | NATURAL GAS | 600 | HP | Throughput for each boiler. Boilers produce steam for solvent recovery. Natural gas is primary fuel, propane used for emergencies, limited to 336 h/yr, each boiler. | Particulate Matter < 10 μ (PM10) | P | CLEAN FUELS | 0.63 | LB/H |  | 2.76 | T/YR |  | 0.023 | LB/MMBTU | calculated
AR-0076 | U.S. ARMY, PINE BLUFF ARSENAL | U.S. ARMY, PINE BLUFF ARSENAL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-02-17 | 2004 | PINE BLUFF ARSENAL IS THE ARMY'S ONLY CHEMICAL ARSENAL AND THE ONLY INSTALLATION WITH BOTH MANUFACTURING AND DEPOT FUNCTIONS. OPERATIONAL FUNCTIONS INCLUDE: AMMUNITION OPERATIONS; CHEMICAL AND BIOLOGICAL DEFENSE OPERATIONS; PRODUCT AND PROCESS DEVELOPMENT | BOILER, PROCESS STEAM, (2) SN-PBCDF-03, -04 | 13.31 | NATURAL GAS | 0.03 | MMDSCF/H | THROUGH PUT FOR EACH. ADDITIONAL THROUGHPUT: 28.4 MMBTU/H (EACH). PROCESS STEAM BOILER SERVES BRINE REDUCTION AREA EQUIPMENT. | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS ONLY. | 0.3 | LB/H | EACH |  |  |  | 0.0106 | LB/MMBTU | CALCULATED
AR-0076 | U.S. ARMY, PINE BLUFF ARSENAL | U.S. ARMY, PINE BLUFF ARSENAL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-02-17 | 2004 | PINE BLUFF ARSENAL IS THE ARMY'S ONLY CHEMICAL ARSENAL AND THE ONLY INSTALLATION WITH BOTH MANUFACTURING AND DEPOT FUNCTIONS. OPERATIONAL FUNCTIONS INCLUDE: AMMUNITION OPERATIONS; CHEMICAL AND BIOLOGICAL DEFENSE OPERATIONS; PRODUCT AND PROCESS DEVELOPMENT | BOILER, HOT WATER, (2) SN-PBCDF-05, -06 | 13.31 | NATURAL GAS | 0.01 | MMDSCF/H | ADDITIONAL THROUGHPUT: 11.7 MMBTU/H, THROUGHPUT FOR EACH. | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS ONLY. | 0.1 | LB/H | EACH |  |  |  | 0.0085 | LB/MMBTU | CALCULATED
AR-0076 | U.S. ARMY, PINE BLUFF ARSENAL | U.S. ARMY, PINE BLUFF ARSENAL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-02-17 | 2004 | PINE BLUFF ARSENAL IS THE ARMY'S ONLY CHEMICAL ARSENAL AND THE ONLY INSTALLATION WITH BOTH MANUFACTURING AND DEPOT FUNCTIONS. OPERATIONAL FUNCTIONS INCLUDE: AMMUNITION OPERATIONS; CHEMICAL AND BIOLOGICAL DEFENSE OPERATIONS; PRODUCT AND PROCESS DEVELOPMENT | BOILER, LABORATORY SN-PBCDF-16 | 13.31 | NATURAL GAS | 1.4 | mmbtu/h |  | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS ONLY. | 0.1 | LB/H |  |  |  |  | 0.071 | LB/MMBTU | CALCULATED
AL-0191 | HYUNDAI MOTOR MANUFACTURING OF ALABAMA, LLC | HYUNDAI MOTOR MANUFACTURING OF ALABAMA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2004-03-23 | 2004 | AUTOMOBILE MANUFACTURING PLANT | BOILERS, NATURAL GAS, (3) | 13.31 | NATURAL GAS | 50 | MMBTU/H | BACT for NOx, PM, and CO | Particulate Matter < 10 μ (PM10) | P | CLEAN FUEL | 0.38 | LB/H |  | 0.0075 | LB/MMBTU |  | 0.0075 | LB/MMBTU
NV-0037 | COPPER MOUNTAIN POWER | SEMPRA ENERGY RESOURCES | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2004-05-14 | 2004 | A 600 MW COMBINED CYCLE ELECTRICAL GENERATION FACILITY CONSISTING OF TWO COMBUSTION TURBINE GENERATORS WITH HEAT RECOVERY STEAM GENERATORS, ONE STEAM TURBINE GENERATOR, AND ONE AUXILIARY BOILER. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 60 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | RESTRICTION OF OPERATION TO NATURAL GAS | 0.5 | LB/H |  |  |  |  | 0.0083333 | LB/MMBTU | NOT AVAILABLE
AR-0086 | NUCOR-YAMATO STEEL COMPANY, BLYTHEVILLE MILL | NUCOR-YAMATO STEEL COMPANY | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-06-11 | 2004 |  | VTD BOILER | 13.31 | NATURAL GAS | 50 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICE | 0.4 | LB/H |  | 1.7 | T/YR |  | 0.0075 | LB/MMBTU
AR-0077 | BLUEWATER PROJECT | STEELCORR, INC. | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-07-22 | 2004 | THE FACILITY IS A NEW SPECIALTY STEEL MILL PRODUCING VARIOUS HOT ROLLED, COLD ROLLED AND GALVANIZED PRODUCTS FOR VARIOUS END USE MARKETS. AFIN: 47-00541 | BOILERS | 13.31 | NATURAL GAS | 22 | MMBTU/H | ENTRY INCLUDES TWO BOILERS. THE 22 MMBTU/H PICKLE LINE BOILER, 51 MMBTU/H VACUUM DEGASSER BOILERS. | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS COMBUSTION ONLY | 0.0076 | LB/MMBTU |  |  |  |  | 0.0076 | LB/MMBTU
WI-0226 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE (WPS) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-08-27 | 2004 | ELECTRIC UTILITY | NATURAL GAS FIRED BOILER | 13.31 | NATURAL GAS | 46.2 | MMBTU/H | NOT PSD | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS | 0.8 | LB/H |  |  |  |  | 0.017316 | LB/MMBTU |  | BOTH PM / PM10 EMISSIONS OF 0.132 LBS/HR @ 37.1 MMBTU/HR (0.0036 LBS/MMBTU)
WI-0227 | PORT WASHINGTON GENERATING STATION | WE ENERGIES (WEPCO) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-13 | 2004 | ELECTRIC GENERATION | NATURAL GAS FIRED AUXILLIARY BOILER | 13.31 | NATURAL GAS | 97.1 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS FUEL, GOOD COMBUSTION PRACTICES | 0.74 | LB/H |  |  |  |  | 0.0076 | LB/MMBTU | CALCULATED | BOTH PM / PM10
WI-0227 | PORT WASHINGTON GENERATING STATION | WE ENERGIES (WEPCO) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-13 | 2004 | ELECTRIC GENERATION | GAS HEATER (P06, S06) | 13.31 | NATURAL GAS | 10 | MMBTU/H | GAS CONDITIONING HEATER | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS FUEL | 0.08 | LB/H |  |  |  |  | 0.008 | LB/MMBTU | CALCULATED | BOTH PM / PM10
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | B63, S63; B64, S64 - NATURAL GAS STATION HEATER 1 AND 2 | 13.31 | NATURAL GAS | 0.75 | MMBTU/H | EMISSION LIMITS ARE THOSE FOR EACH UNIT. | Particulate Matter < 10 μ (PM10) | P | NATURAL GAS FUEL | 0.006 | LB/H | [6 empty] | NOT AVAILABLE | (LIMIT IS FOR EACH UNIT)
AZ-0047 | WELLTON MOHAWK GENERATING STATION | DOME VALLEY ENERGY PARTNERS | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2004-12-01 | 2004 | COMBINED CYCLE GAS-FIRED ELECTRICITY GENERATING STATION | AUXILIARY BOILER | 13.31 | NATURAL GAS | 38 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | N |  | 0.0033 | LB/MMBTU | BASED ON HIGHER HEATING VALUE OF FUEL |  |  |  | 0.0033 | LB/MMBTU
OH-0252 | DUKE ENERGY HANGING ROCK ENERGY FACILITY | DUKE ENERGY HANGING ROCK, LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2004-12-28 | 2004 | FOUR NATURAL GAS (NG) FIRED COMBUSTION TURBINES, WITH DUCT BURNERS; COMBINED CYCLE, EACH 172 MW | BOILERS (2) | 13.31 | NATURAL GAS | 30.6 | MMBTU/H | LIMITS ARE FOR EACH BOILER INDIVIDUALLY. THE MAXIMUM FUEL HEAT INPUT SHALL NOT EXCEED 91,500 MMBTU/ROLLING 12-MONTHS FOR EACH BOILER. | Particulate Matter < 10 μ (PM10) | N |  | 0.31 | LB/H | EACH BOILER | 0.46 | T/ROLLING 12-MONTHS | EACH BOILER | 0.01 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER
LA-0192 | CRESCENT CITY POWER | CRESENT CITY POWER, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-06-06 | 2005 | NEW 600 MW NATURAL GAS-FIRED COMBINED CYCLE POWER PLANT | FUEL GAS HEATERS (3) | 13.31 |  | 19 | MMBTU/H |  | Particulate Matter < 10 μ (PM10) | P | USE OF LOW SULFUR PIPELINE NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.14 | LB/H | HOURLY MAXIMUM | 0.05 | T/YR | *SEE NOTES. ANNUAL MAXIMUM | 0.007 | LB/MMBTU | ANNUAL AVERAGE | *TPY LIMIT FOR ALL 3 HEATERS. AGGREGATE HEAT INPUT IS LIMITED TO 14,250 MM BTU/YR. ONLY 2 OF THE 3 HEATERS ARE ALLOWED TO OPERATE AT ANY GIVEN TIME.
LA-0203 | OAKDALE OSB PLANT | MARTCO LIMITED PARTNERSHIP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-06-13 | 2005 | PSD FOR A NEW ORIENTED STRAND BOARD (OSB) MANUFACTURING FACILITY CAPABLE OF PRODUCING 900,000 MSF 3/8 INCH OSB PER YEAR. | AUXILIARY THERMAL OIL HEATER | 13.31 | NATURAL GAS | 66.5 | MMBTU/H | OPERATING TIME = 500 HR/YR. | Particulate Matter < 10 μ (PM10) | P | USE OF NATURAL GAS AS FUEL AND GOOD COMBUSTION PRACTICES | 0.59 | LB/H | HOURLY MAXIMUM |  |  |  | 0.009 | LB/MMBTU | CALCULATED BY CATC
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-07-27 | 2005 | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | CRACKING FURNACES A-D | 13.31 |  | 90 | MMBTU/H EA. |  | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICES AND USE OF NATURAL GAS AS FUEL | 0.007 | LB/MMBTU |  |  |  |  | 0.007 | LB/MMBTU | THREE ONE-HOUR TEST AVERAGE
MD-0036 | DOMINION | DOMINION COVE POINT LNG, L.P. | MD | MARYLAND DEPARTMENT OF THE ENVIRONMENT | 2006-03-10 | 2006 | LNG FACILITY | FUEL GAS PROCESS HEATER | 13.31 | NATURAL GAS |  |  | ENGINEERING TECH NO. IDHLE 1.0; 0.93 MMBTU/HR | Particulate Matter < 10 μ (PM10) | P | USE OF LNG QUALITY, LOW SULFUR NATURAL GAS | 0.0074 | LB/MMBTU | 3-HOUR AVERAGE | [6 empty] | PM10 - FILERABLE AND CONDENSIBLE
*NV-0046 | GOODSPRINGS COMPRESSOR STATION | KERN RIVER GAS TRANSMISSION COMPANY | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2006-05-16 | 2006 | THE FACILITY IS A COMPRESSOR STATION ON AN INTER-STATE PIPELINE FOR TRANSPORTING NATURAL GAS. THE FACILITY IS A MAJOR STATIONARY SOURCE FOR NITROGEN OXIDES IN A NON-ATTAINMENT AREA FOR OZONE AIR QUALITY. | COMMERCIAL/INSTITUTIONAL BOILER | 13.31 | NATURAL GAS | 3.85 | MMBTU/H | THE UNIT'S MODEL IDENTIFICATION IS PEERLESS 724 FDA WU. | Particulate Matter < 10 μ (PM10) | P | GOOD COMBUSTION PRACTICE | 0.0078 | LB/MMBTU |  | 0.13 | T/YR |  | 0.0078 | LB/MMBTU
NV-0044 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S ENTERTAINMENT | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2007-01-04 | 2007 | THE FACILITY IS A NEW MAJOR STATIONARY SOURCE FOR NITROGEN OXIDES AS A RESULT OF CONSOLIDATING SIX LARGE HOTEL/CASINO RESORTS, WHICH ARE HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. | COMMERCIAL/INSTITUTIONAL-SIZE BOILERS | 13.31 | NATURAL GAS | 35.4 | MMBTU/H | THE BACT DETERMINATIONS REPORTED HERIN ARE SPECIFICALLY FOR THE TWO HURST BOILERS INSTALLED AT CAESAR'S PALACE. EACH OF THEM HAS A RATED HEAT INPUT OF 35.4 MMBTU/HR. THE PERMITTING ACTION ALSO APPROVED THE INSTALLATION OF A NUMBER OF SMALL BOILERS, ALL OF | Particulate Matter < 10 μ (PM10) | P | USE OF NATURAL GAS AS THE ONLY FUEL | 0.0075 | LB/MMBTU |  | 0.26 | LB/H |  | 0.0075 | LB/MMBTU |  | THE DATA PERTAIN TO EITHER ONE OF THE HURST BOILERS, WHICH RATED HEAT INPUT IS 35.4 MMBTU/H.
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | 2007 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NATURAL GAS | 13.31 | NATURAL GAS | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. WITH #2 OIL BACKUP TWO SET OF LIMITS, THIS ONE FOR NATURAL GAS | Particulate Matter < 10 μ (PM10) | N |  | 0.15 | LB/H |  | 0.78 | T/YR |  | 0.0075 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
IA-0088 | ADM CORN PROCESSING - CEDAR RAPIDS | ARCHER DANIELS MIDLAND | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-06-29 | 2007 | CONSISTS OF THREE DISTINCT OPERATIONS: CORN WET MILL, CORN DRY MILL AND BOILERHOUSE | INDIRECT-FIRED DDGS DRYER | 13.31 | NATURAL GAS | 93.7 | MMBTU/H | PROJECT INCLUDES THE INSTALLATION OF EIGHT IDENTICAL DDGS DRYERS. PERMITS 07-A-546-P, 547, 548, 549, 550, 557, 558 AND 559. THE COMBUSTION CHAMBER AND THE FEED CHAMBER ARE SEPERATED BY A HEAT EXCHANGER. THE DRYERS CAN FIRE NATURAL GAS, BIOGAS FROM THE WWT | Particulate Matter < 10 μ (PM10) | N |  | 0.015 | GR/DSCF | AVERAGE OF 3 TEST RUNS
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED BATCH ANNEALING FURNACE (535) | 13.31 | NATURAL GAS | 99 | MMBTU/H | THIS PROCESS IS COVERED UNDER 503-0095-X005. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Particulate Matter < 10 μ (PM10) | N |  | 0.0076 | LB/MMBTU |  | 0.75 | LB/H
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED PASSIVE ANNEALING FURNACE (LO41) | 13.31 | NATURAL GAS | 27.2 | MMBTU/H | THIS PROCESS IS COVERED UNDER 503-0095-X013. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Particulate Matter < 10 μ (PM10) | N |  | 0.0076 | LB/MMBTU |  | 0.21 | LB/H
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED BATCH ANNEALING FURNACES (LA63, LA64) | 13.31 | NATURAL GAS | 33.4 | MMBTU each | THIS PROCESS IS COVERED UNDER 503-0095-X014. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Particulate Matter < 10 μ (PM10) | N |  | 0.0076 | LB/MMBTU |  | 6.25 | LB/H
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | 3 NATURAL GAS-FIRED BOILERS WITH ULNB & EGR (537-539) | 13.31 | NATURAL GAS | 64.9 | MMBtu each | THIS PROCESS IS COVERED UNDER 503-0095-X026. | Particulate Matter < 10 μ (PM10) | N |  | 0.0076 | LB/MMBTU |  | 0.5 | LB/H
*NE-0043 | NATUREWORKS, LLC |  | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2007-10-01 | 2007 | POLYMER PRODUCTION FACILITY | HOT OIL HEATER | 13.31 |  |  |  |  | Particulate Matter < 10 μ (PM10) | N | [10 empty] | BECAUSE OF UNIT SIZE (62.4 MMBTU/HR) AND FUEL TYPE (NATURAL GAS), CONTROL IS COST PROHIBITIVE.
NJ-0045 | MERCK - RAHWAY PLANT | MERCK | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-01-14 | 1997 | CHEMICAL MANUFACTURING | BOILERS - NAT GAS (3) | 13.31 | NATURAL GAS | 99.5 | MMBTU/H |  | Sulfur Dioxide (SO2) | N | NONE | 0.1 | LB/H |  |  |  |  | 0.001 | LB/MMBTU
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 8 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 50 | MMBTU/H | THE NUMBER 8 PAPER MACHINE CONSISTS OF THREE SOURCES: THE NATURAL GAS FIRED BURNERS, THE PAPER MACHINE, AND THE DUST SYSTEM. STACK TESTING FOR CO AND NOX. | Sulfur Dioxide (SO2) | P | CLEAN FUEL | 0.0007 | LB/MMBTU |  | 0 |  |  | 0.0007 | LB/MMBTU
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 5 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 21 | MMBTU/H | THE BURNERS FOR THE NUMBER 5 PAPER MACHINE HAVE BEEN UPGRADED. | Sulfur Dioxide (SO2) | P | CLEAN FUEL | 0.0007 | LB/MMBTU |  | 0 |  |  | 0.0007 | LB/MMBTU
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 6 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 58.4 | MMBTU/H | THE BURNERS FOR THE NUMBER 6 PAPER MACHINE HAVE BEEN UPGRADED. | Sulfur Dioxide (SO2) | P | CLEAN FUEL | 0.0007 | LB/MMBTU |  | 0 |  |  | 0.0007 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HIGH PRESSURE BOILER #2-R2 | 13.31 | FUEL OIL | 0.3 | MMBTU/H | PERMIT NO: 97-A-416 FUEL OIL < 10,674,202 GALLONS/Y PER WHOLE FACILITY SULFUR CONTENT OF FUEL OIL < 0.05 % BY WEIGHT | Sulfur Dioxide (SO2) | P | LIMIT CHOSEN TO STAY UNDER PSD SIGNIFICANCE. | 1.26 | T/YR |  | 2.5 | LB/MMBTU |  | 2.5 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #1 | 13.31 | NATURAL GAS | 2.3 | MMBTU/H | FUEL IS NATURAL GAS AND FUEL OIL ONLY. PERMIT NUMBER: 97-A-377. 20 % OPACITY NSPS SUBPART BC SO2 - 9.46 TPY, SET TO STAY UNDER PSD SIGNIFICANCE LEVELS | Sulfur Dioxide (SO2) | N | SO2 LIMITS SET TO STAY BELOW PSD SIGNIFICANCE | 9.46 | T/YR |  |  |  |  | 0.9 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HYDROGEN PLANT BURNER R9 | 13.31 |  |  |  | PERMIT NUMBER: 97-A-391 20% OPACITY - 1A 23.3(2)D. THIS PROCESS GENERATES HYDROGEN FROM NATURAL GAS. THE HYDROGEN IS USED FOR THE HYDROGENATION OF THE SOYBEAN OIL. | Sulfur Dioxide (SO2) | N |  | 0.04 | T/YR |  |  |  |  | 0.0006 | LB/MMBTU
KY-0068 | TOYOTA MOTOR MANUFACTURING, USA, INC | TOYOTA MOTOR MANUFACTURING, USA, INC | KY | KENTUCKY DEP, DIV FOR AIR QUALITY | 1997-05-29 | 1997 | MODIFICATION OF AN AUTOMOBILE ASSEMBLY PLANT (THIRD REVISION OF PERMIT) | BOILER (NATURAL GAS) | 13.31 | NATURAL GAS | 96 | MMBTU/H | A SEPARATELY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING FUEL OIL (BACKUP FUEL). WHEN FIRING NATURAL GAS, ANNUAL OPERATING HOURS SHALL NOT EXCEED 6132 H/YR. | Sulfur Dioxide (SO2) | P | THE SULFUR CONTENT OF NO.2 FUEL SHALL NOT EXCEED 0.3%. | 0.3 | LB/MMBTU |  | 40 | T/YR |  | 0.3 | LB/MMBTU
AL-0139 | ANNISTON ARMY DEPOT | U.S. ARMY - ANNISTON ARMY DEPOT | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-06-19 | 1997 |  | BOILER, NATURAL GAS FIRED, 2 | 13.31 | NATURAL GAS | 13.4 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | CLEAN FUEL | 0.016 | LB/H |  |  |  |  | 0.0012 | LB/MMBTU
AL-0140 | ANNISTON ARMY DEPOT | U.S. ARMY - ANNISTON ARMY DEPOT | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 1997-06-19 | 1997 |  | BOILER, NATURAL GAS FIRED, 2 | 13.31 | NATURAL GAS | 11.7 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | CLEAN FUEL | 0.014 | LB/H |  |  |  |  | 0.0012 | LB/MMBTU
WI-0188 | GOLDEN BOOKS PUBLISHING COMPANY INC. | GOLDEN BOOKS PUBLISHING COMPANY INC. | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 1997-06-24 | 1997 | PRINTING FACILITY | SPACE HEAT & COMBUSTION SOURCES, (P01 S01) | 13.31 | NATURAL GAS | 93 | MMBTU/H | SECOND FUEL: PROPANE | Sulfur Dioxide (SO2) | N | REGULATORY BASIS: STATE REG. | 0.99 | LB/H |  |  |  |  | 0.011 | LB/MMBTU
AK-0036 | KUPARUK CENTRAL PRODUCTION FACILITY | ARCO ALASKA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1998-02-13 | 1998 |  | PROCESS HEATER | 13.31 | NATURAL GAS | 8 | MMBTU/H | OTHER COMPLIANCE: FACILITY OPERATING REPORTS. PERMIT LIMITS NOX AND H2S IN FUEL (SO2, PM10 AND VE). CO AND VOC ARE NOT INCLUDED IN THIS PERMIT. | Sulfur Dioxide (SO2) | P | NATURAL GAS FUEL. PERMIT LIMIT IS USE OF FUEL WITH H2S < 200 PPMV H2S. |  |  | SEE NOTE | [6 empty] | PERMIT LIMIT IS USE OF FUEL WITH H2S < 200 PPMV H2S.
TX-0300 | SALT CREEK GAS PLANT | MOBIL EXPLORATION & PRODUCING US INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-10-13 | 1998 | MOBIL EXPLORATION & PRODUCING US INC HAS REQUESTED AN AMENDMENT TO PERMIT NO 20660 AND A MODIFICATION TO PSD-TX-795 TO (1) INCREASE THE CO AND VOC ALLOWABLES ON THEIR COOPER-BESSEMER GMVH-12C2 ENGINES TO ALLOW THEM TO BETTER CONTROL NOX TO THE 2 G/HP-H LE | HOT OIL HEATER, EPN 26 | 13.31 | NAT GAS | 32.2 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | FUEL IS LIMITED TO PIPELINE-QUALITY, SWEET NATURAL GAS CONTAINING NO MORE THAN 5 GR S/100 DSCF | 0.01 | LB/H |  | 0.04 | T/YR |  | 0.0003 | LB/MMBTU | CALCULATED | STANDARD EMISSION LIMITS CALCULATED FROM HOURLY EMISSION LIITS AND HEATERS RATED CAPACITY.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | WASTE HEAT RECOVERY, UNIT 10 | 13.31 | NATURAL GAS | 52.8 | MMBTU/H | MAXIMUM OPERATION DURING COMMISSIONING PERIOD: 1848 H MAXIMUM OPERATION AFTER COMMISSIONING PERIOD: 1000 H UNDER NORMAL LONG-TERM OPERATIONS, THE WASTE HEAT RECOVERY SUPPLEMENTAL BURNER WILL NOT BE OPERATED. OPERATION OF THIS BURNER IS UNDER AN ALTERNATIV | Sulfur Dioxide (SO2) | P | HYDROGEN SULFIDE CONTENT OF NATURAL GAS FUEL SHALL NOT EXCEED 50 PPMV. | 500 | PPM | AVERAGED OVER 3 HOURS |  |  |  | 2.55 | LB/MMBTU | CONVERTED FROM 500 PPM
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | GLYCOL REBOILER, UNIT 13 | 13.31 | NATURAL GAS | 5 | MMBTU/H | MAXIMUM OPERATION DURING COMMISSIONING PERIOD: 1848 H. MAXIMUM OPERATION AFTER COMMISSIONING PERIOD: 8760 H/YR. | Sulfur Dioxide (SO2) | P | HYDROGEN SULFIDE CONTENT OF NATURAL GAS FUEL SHALL NOT EXCEED 50 PPMV. | 500 | PPM | AV OVER A PERIOD OF 3 H |  |  |  | 2.55 | LB/MMBTU | CONVERTED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMIT. STATE: EMISSION LIMIT 1
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | GLYCOL SKID HEATER (NATURAL GAS), UNIT NO. 14 | 13.31 | NATURAL GAS | 1.05 | MMBTU/H | SECOND FUEL FOR GLYCOL SKID HEATER IS DIESEL- LISTED SEPARATELY. MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. | Sulfur Dioxide (SO2) | P | HYDROGEN SULFIDE CONTENT OF NATURAL GAS FUEL SHALL NOT EXCEED 50 PPMV. | 500 | PPM | AVERAGED OVER 3 H |  |  |  | 2.55 | LB/MMBTU | CALCULATED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMIT STATE: EMISSION LIMIT 1
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | SPACE HEATER, WAREHOUSE, UNIT NO. 15, 16 | 13.31 | NATURAL GAS | 0.5 | MMBTU/H | MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. | Sulfur Dioxide (SO2) | P | HYDROGEN SULFIDE CONTENT OF NATURAL GAS FUEL SHALL NOT EXCEED 50 PPMV. | 500 | PPM |  |  |  |  | 2.55 | LB/MMBTU | CALCULATED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMIT STATE: EMISSION LIMIT 1
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | SPACE HEATER, WAREHOUSE, UNIT NO. 17 | 13.31 | NATURAL GAS | 0.63 | MMBTU/H | MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. | Sulfur Dioxide (SO2) | P | HYDROGEN SULFIDE CONTENT OF NATURAL GAS FUEL SHALL NOT EXCEED 50 PPMV. | 500 | PPM | AV OVER A PERIOD OF 3 H |  |  |  | 2.55 | LB/MMBTU | CALCULATED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMITS STATE: EMISSION LIMIT NO. 1
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | SPACE HEATER, WAREHOUSE, UNIT NO. 18 | 13.31 | NATURAL GAS | 1.06 | MMBTU/H | MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. | Sulfur Dioxide (SO2) | P | HYDROGEN SULFIDE CONTENT OF NATURAL GAS SHALL NOT EXCEED 50 PPMV. | 500 | PPM | AVERAGED OVER 3 H |  |  |  | 2.55 | LB/MMBTU | CALCULATED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMIT STATE: EMISSION LIMIT 1
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | RIG BOILER (NATURAL GAS), UNIT 206, 207 | 13.31 | NATURAL GAS | 6.3 | MMBTU/H | PERMIT LISTS UNIT 206 AND 207 WITH NATURAL GAS AND DIESEL, LISTED SEPARATELY IN DATABASE. TYPICAL OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 924 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. DURING PRE- SEALFIT PERIOD AND COMMI | Sulfur Dioxide (SO2) | P | HYDROGEN SULFIDE CONTENT OF NATURAL GAS FUEL SHALL NOT EXCEED 50 PPMV | 500 | PPM | AV OVER 3 H |  |  |  | 2.55 | LB/MMBTU | CALCULATED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMIT STATE: EMISSION LIMIT 1 PLUS FUEL RESTRICTIONS
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATER (NATURAL GAS), UNIT 208, 209 | 13.31 | NATURAL GAS | 3.5 | MMBTU/H | UNITS 208 AND 209 ARE LISTED IN PERMIT AS BURNING BOTH NATURAL GAS AND DIESEL FUEL. THESE ARE LISTED SEPARATELY IN DATABASE. DURING PRE-SEALIFT PERIOD AND COMMISSIONING PERIOD, UNITS MAY BE OPERATED WITH NATURAL GAS OR DIESEL FOR THE SAME AMOUNT OF TIME. | Sulfur Dioxide (SO2) | P | HYDROGEN SULFIDE CONTENT OF NATURAL GAS FUEL SHALL NOT EXCEED 50 PPMV. | 500 | PPM | AV OVER 3 H |  |  |  | 2.55 | LB/MMBTU | CALCULATED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMIT STATE: EMISSION LIMIT 1 AND SULFUR RESTRICTION TO THE FUEL
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATER (NATURAL GAS), UNIT 210 | 13.31 | NATURAL GAS | 4.2 | MMBTU/H | THE SOURCE INVENTORY TABLE IN THE PERMIT LISTED ONLY DIESEL, BUT GAVE OPERATIONAL HOURS TYPICAL FOR BOTH NAT GAS AND DIESEL (SIMILAR TO OTHER SOURCES). FOOTNOTE STATED THAT UNIT 210 BURNS NATURAL GAS AND DIESEL, THEREFORE IT WAS ASSUMED THAT NAT GAS WAS E | Sulfur Dioxide (SO2) | P | HYDROGEN SULFIDE CONTENT OF NATURAL GAS FUEL SHALL NOT EXCEED 50 PPMV. | 500 | PPM | AV OVER 3 H |  |  |  | 2.55 | LB/MMBTU | CALCULATED FROM 500 PPM | BACT: FUEL SULFUR CONTENT LIMIT STATE: EMISSION LIMIT 1 AND SULFUR CONTENT RESTRICTION TO FUEL
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 1 (NATURAL GAS) | 13.31 | NATURAL GAS | 84.4 | MMBTU/H | MFR. IS COMBUSTION ENGINEERING. ONLY NATURAL GAS, A MIXTURE OF NO. 2 OIL AND LASALOCID OIL, AND NO. 2 OIL SHALL BE FIRED IN BOILER 1. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. AFTER APRIL 3 | Sulfur Dioxide (SO2) | N | NONE LISTED | 0.1 | LB/H |  |  |  |  | 0.001 | LB/MMBTU
MA-0029 | SITHE MYSTIC DEVELOPMENT LLC | SITHE MYSTIC DEVELOPMENT LLC | MA | MASSACHUSETTS DIV OF AIR QUAL CONTROL | 1999-09-29 | 1999 | COMBINED CYCLE ELECTRIC GENERATING FACILITY | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 96 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | NATURAL GAS FUEL WITH NO MORE THAN .8 GRAINS OF SULFUR PER 100 CU FT. | 0.3 | LB/H |  |  |  |  | 0.0029 | LB/MMBTU
OK-0051 | GREEN COUNTRY ENERGY PROJECT | COGENTRIX ENERGY INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 1999-10-01 | 1999 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS |  |  |  | Sulfur Dioxide (SO2) | P | USE OF NATURAL GAS | 0.006 | LB/MMBTU |  |  |  |  | 0.006 | LB/MMBTU
OK-0050 | ONETA GENERATING STA | CALPINE CORP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2000-01-21 | 2000 | ELECTRIC GENERATION PLANT | DUCT BURNERS (4) | 13.31 | NATURAL GAS | 328 | MMBTU/H | The emission limits indicted are for the duct burners only. Emission limits for the turbines associated with these duct burners are provided under the process Combustion Turbines | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL - NATURAL GAS | 0.0013 | LB/MMBTU |  |  |  |  | 0.0013 | LB/MMBTU
TX-0309 | FORMOSA PLASTICS TEXAS | FORMOSA PLASTICS CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-02-10 | 2000 | THIS PERMIT AUTHORIZES THE OPERATION OF THE FORMOSA ETHYLENE GLYCOL PLANT & A PRODUCTION INCREASE, EQUIPMENT UPGRADES & CHANGES, ADDITIONAL FUGITIVE EMISSIONS, & AN ADDITIONAL COOLING TOWER CELL. THE APPLICANT WISHES TO CONSOLIDATE ALL FUGITIVE EMISSION P | WASTE HEAT BOILER, 70Z401 | 13.31 | NAT GAS |  |  | SHALL BE MAINTAINED AT A MINIMUM COMBUSTION CHAMBER TEMP OF 1450 F. | Sulfur Dioxide (SO2) | N | NONE INDICATED | 0.26 | LB/H |  | 0.23 | T/YR
AK-0053 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFI | CRUDE HEATER, CF-H-31003A | 13.31 | FUEL GAS | 65.6 | MMBTU/H | PERMIT INFORMATION LISTS FUEL TYPE AS FUEL GAS" BUT TECHNICAL DOCUMENTS INDICATE THAT FUEL IS NATURAL GAS. SCC AND PROCESS CODES WERE CHOSEN FOR NATURAL GAS." | Sulfur Dioxide (SO2) | P | USE ONLY FUEL GAS WITH A HYDROGEN SULFIDE CONTENT NOT TO EXCEED 200 PPM AND USE DISTILLATE FUEL OIL WITH A SULFUR CONTENT NOT TO EXCEED 0.15%. |  |  | SEE CONTROL DESCRIPTION AND NOTES | [5 empty] | NOT AVAILABLE | 18 AAC 50.055(C) LIMIT IS 500 PPM, 3 H AVER
AK-0053 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFI | CRUDE HEATER, CF-H-31003B | 13.31 | FUEL GAS | 65.6 | MMBTU/H | PERMIT INFORMATION INDICATES FUEL TYPE IS FUEL GAS" BUT TECHNICAL INFORMATION INDICATES FUEL GAS IS NATURAL GAS. SCC AND PROCESS CODES WERE CHOSEN FOR NATURAL GAS. UNIT IS DESCRIBED AS BORN." | Sulfur Dioxide (SO2) | P | USE ONLY FUEL GAS WITH A HYDROGEN SULFIDE CONTENT NOT TO EXCEED 200 PPM AND USE DISTILLATE FUEL OIL WITH A SULFUR CONTENT NOT TO EXCEED 0.15%. |  |  | SEE CONTROL DESCRIPTION AND NOTES | [5 empty] | NOT AVAILABLE | 18 AAC 50.055(C) LIMIT IS 500 PPM, 3 HR AVER
TX-0274 | SOLAR GAS TURBINE COGEN. | AMERIPOL SYNPOL CORP. | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-04-03 | 2000 | AMERIPOL PROPOSES TO CONSTRUCT A COGENERATION FACILITY, TURBINE WITH DUCT BURNER FIRED HEAT RECOVERY STEAM GENERATOR (HRSG) AND AN AUXILLIARY BOILER. THE TURBINE IS A 4.4 MW (DESIGN CAPACITY AT ISO CONDITIONS, BASE LOAD) NATURAL GAS FIRED SOLAR TURBINE, M | AUXILIARY BOILER | 13.31 | NATURAL GAS | 54.01 | MMBTU/H | WILL BE OPERATED 175 H/YR ONLY DURING PERIODS OF CTG DOWNTIME. | Sulfur Dioxide (SO2) | P | FUEL SPECIFICATIONS OF NO MORE THAN 2.5 GRAINS TOTAL SULFUR PER 100 DRY STANDARD CUBIC FEET ON A SHORT-TERM BASIS AND 0.5 GRAIN TOTAL SULFUR PER 100 DSCF ON A ROLLING 12-MONTH AVERAGE BASIS. | 0.77 | LB/H |  | 0.07 | T/YR |  | 0.014 | LB/MMBTU | CONVERTED USING THROUGHPUT
MI-0301 | ALCHEM ALUMINUM | ALCHEM ALUMINUM, INC. | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 2000-05-02 | 2000 | SECONDARY ALUMINUM PRODUCTION. | FLUES | 13.31 | NATURAL GAS | 42000 | LB/H | HOLDING CAPACITIES ARE 170,000 AND 250,000 LBS. BURNER CAPACITIES ARE 34,000,000 AND 48,000,000 BTU/HR. | Sulfur Dioxide (SO2) | N | COMBUSTION FLUES ARE WITHOUT ADD-ON CONTROLS. ONLY PIPELINE QUALITY NATURAL GAS FOR FUEL. | 0.12 | LB/H |  | 0.54 | T/YR |  |  | LB/MMBTU
MA-0027 | CABOT POWER CORPORATION | CABOT POWER CORPORATION | MA | MASSACHUSETTS DIV OF AIR QUAL CONTROL | 2000-05-07 | 2000 | COMBINED CYCLE ELECTRIC GENERATING FACILITY. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 26.6 | MMBTU/H | PROCESS RESTRICTED TO 500 HOURS PER YEAR (12,881,000 SCF NATURAL GAS) | Sulfur Dioxide (SO2) | P | NATURAL GAS FUEL OF < .8 GRAINS PER 100 SCF. | 0.06 | LB/H |  |  |  |  | 0.0022 | LB/MMBTU
TX-0430 | DIAMOND SHAMROCK MCKEE PLANT | DIAMOND SHAMROCK REFINING CO. | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-05-23 | 2000 | LOCATED AT 6701 FM 119, SUNRAY, TX | HEATERS, REFINERY | 13.3 | NATURAL GAS |  |  | MULTIPLE HEATERS, FIRING NATURAL GAS AND REFINERY FUEL GAS | Sulfur Dioxide (SO2) | P | LOW SULFUR REFINERY GAS OR PURCHASED NATURAL GAS |  |  | SEE NOTE | [6 empty] | BACT IS CLEAN FUEL, NO EMISSION RATE LIMIT.
AK-0045 | NORTH COOK INLET UNIT | PHILLIPS PETROLEUM COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-06-06 | 2000 | THIS PERMIT ALLOWS PHILLIPS TO INSTALL TWO SOLAR TAURUS 60 T-7300 TURBINES RATED AT 6740 HP AT ISO CONDITIONS. THE TURBINES ARE SUBJECT TO PSD REVIEW FOR NOX AND PM10. | GLYCOL HEATER NOS. 1, 2, AND 3 | 13.31 | NATURAL GAS | 8.36 | MMBTU/H | THREE PROCESS UNITS ARE INCLUDED IN THIS ENTRY. THE OWNER REQUESTED TO LIMIT THE SULFUR CONTENT OF GASEOUS AND LIQUID FUELS TO 200-PPM HYDROGEN SULFIDE AND 0.25% SULFUR BY WEIGHT TO AVOID A PSD PRE-CONSTRUCTION REVIEW OF EXISTING EQUIPMENT. THE OWNER WILL | Sulfur Dioxide (SO2) | P | USE NATURAL GAS WITH A HYDROGEN SULFIDE CONTENT NOT TO EXCEED 200 PPM AND FUEL OIL WITH A SULFUR CONTENT NOT TO EXCEED 0.25% BY WEIGHT. | 500 | PPM | EACH, 3 H AV | 0.28 | LB/H |  | 0.033 | LB/MMBTU | EACH, CALCULATED | BASIS OF DETERMINATION IS 18 AAC 50.055(C). THE HOURLY EMISSION LIMIT WAS CONVERTED INTO STANDARDIZED UNITS BY DIVIDING IT BY THE THROUGHPUT. THE OWNER REQUESTED TO LIMIT THE SULFUR CONTENT OF GASEOUS AND LIQUID FUELS TO 200-PPM HYDROGEN SULFIDE AND 0.25%
AK-0045 | NORTH COOK INLET UNIT | PHILLIPS PETROLEUM COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-06-06 | 2000 | THIS PERMIT ALLOWS PHILLIPS TO INSTALL TWO SOLAR TAURUS 60 T-7300 TURBINES RATED AT 6740 HP AT ISO CONDITIONS. THE TURBINES ARE SUBJECT TO PSD REVIEW FOR NOX AND PM10. | DRILLING BOILER NO. 1 | 13.31 | NATURAL GAS | 100 | HP | THE OWNER REQUESTED TO LIMIT THE SULFUR CONTENT OF GASEOUS AND LIQUID FUELS TO 200-PPM HYDROGEN SULFIDE AND 0.25% SULFUR BY WEIGHT AND LIMITED HOURS OF OPERATION TO 1080 PER 12 MO PERIOD TO AVOID A PSD PRE-CONSTRUCTION REVIEW OF EXISTING EQUIPMENT. | Sulfur Dioxide (SO2) | P | USE NATURAL GAS WITH A HYDROGEN SULFIDE CONTENT NOT TO EXCEED 200 PPM AND FUEL OIL WITH A SULFUR CONTENT NOT TO EXCEED 0.25% BY WEIGHT. | 500 | PPM | 3 H AV | 0.15 | LB/H |  | 0.033 | LB/MMBTU | CALCULATED | BASIS OF DETERMINATION- 18 AAC 50.055(C). THE HOURLY EMISSION LIMIT WAS CONVERTED INTO STANDARDIZED UNITS BY DIVIDING IT BY THE THROUGHPUT.
TX-0363 | SAINT-GOBAIN VETROTEX AMERICA | VETROTEX AMERICA | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-11-13 | 2000 | VETROTEX AMERICA (VETROTEX) OPERATES A FIBER GLASS MANUFACTURING PLANT. THE VETROTEX PLANT PRODUCES FIBERGLASS REINFORCEMENT PRODUCTS AND IS COMPRISED OF FIVE GLASS MANUFACTURING FURNACES AND ASSOCIATED EQUIPMENT. THESE REFINFORCEMENT PRODUCTS ARE USED IN | BOILER NO 3 | 13.31 | NAT GAS |  |  |  | Sulfur Dioxide (SO2) | N | NONE INDICATED | 0.03 | LB/H |  | 0.12 | T/YR |  |  |  | NOT AVAILABLE
SC-0065 | BROAD RIVER INVESTORS - GAFFNEY | BROAD RIVER INVESTORS, LLC | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 2000-12-21 | 2000 | ELECTRIC GENERATION FACILITY | HOT WATER HEATERS, NAT. GAS (2) | 13.31 | NATURAL GAS | 11 | MMBTU/H (EACH) |  | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL | 0.0065 | LB/H | EACH | [6 empty] | STATE BACT PERFORMED
AR-0040 | DUKE ENERGY HOT SPRINGS | DUKE ENERGY HOT SPRINGS | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2000-12-29 | 2000 | NATURAL GAS FIRED POWER PLANT | BOILERS, AUXILIARY 2 | 13.31 | NATURAL GAS | 44.1 | MMBTU/H | THROUGHPUT FOR EACH | Sulfur Dioxide (SO2) | P | LOW SULFUR FUELS | 2 | GR/DSCF |  |  |  |  | 0.006 | LB/MMBTU
AL-0168 | GENPOWER KELLEY LLC | GENPOWER KELLEY LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-01-12 | 2001 | ELECTRIC GENERATION | BOILER | 13.31 | NATURAL GAS | 83 | MMBTU/H | BOILER OPERATION LIMITED TO 1000 HR/YR | Sulfur Dioxide (SO2) | N |  | 0.001 | LB/MMBTU |  | 0.13 | LB/H |  | 0.001 | LB/MMBTU
IN-0090 | NUCOR STEEL | NUCOR STEEL | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-01-19 | 2001 |  | LADLE PREHEATERS | 13.31 | NATURAL GAS | 15 | MMBTU/HR EACH | TUNDISH PREHEATERS 6 MMBTU/H EACH, TUNDISH NOZZLE PREHEATERS 1 MMBTU/H EACH, TUNDISH DRYERS 9 MMBTU/H, TRANSITION PIECE PREHEATERS 15 MMBTU/H | Sulfur Dioxide (SO2) | P | PERMIT LIMITATION IS NATURAL GAS OR PROPANE USAGE
AL-0169 | BLOUNT MEGAWATT FACILITY | BLOUNT COUNTY ENERGY LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-02-05 | 2001 | ELECTRIC GENERATING FACILITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 40 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | GOOD COMBUSTION PRACTICES | 0.006 | LB/MMBTU |  | 0.24 | LB/H |  | 0.006 | LB/MMBTU
OH-0255 | PSEG WATERFORD ENERGY LLC | PSEG WATERFORD ENERGY LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-03-29 | 2001 | THREE 170 MW NATURAL GAS-FIRED COMBUSTION TURBINES; STAGE I SIMPLE CYCLE TO STAGE II COMBINED CYCLE | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 85.2 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | LOW S NATURAL GAS, 2 GR/100 SCF | 0.05 | LB/H |  | 0.22 | T/YR |  | 0.0006 | LB/MMBTU
SC-0061 | COLUMBIA ENERGY LLC | COLUMBIA ENERGY LLC | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 2001-04-09 | 2001 | ELECTRIC COGENERATION POWER PLANT SUPPLYING STEAM AND ENERGY, A EASTMAN CHEMICAL CO. | HOT WATER HEATERS (2) | 13.31 | NATURAL GAS | 11 | MMBTU/H | USED FOR PREHEATING THE NATURAL GAS PRIOR TO SUPPLY TO THE COMBUSTION TURBINES, SUBJECT TO SUBPART Dc - STANDARDS OF PERFORMANCE FOR SMALL INDUSTRIAL-COMMERCIAL-INSTITUTIONAL STEAM GENERATING UNITS | Sulfur Dioxide (SO2) | P | CLEAN FUEL | 3.5 | LB/MMBTU |  |  |  |  | 3.5 | LB/MMBTU
IN-0086 | MIRANT SUGAR CREEK, LLC | MIRANT SUGAR CREEK, LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-05-09 | 2001 |  | AUXILARY BOILER, NATURAL GAS (2) | 13.31 | NATURAL GAS | 35 | MMBTU/H | AUXILARY BOILERS ARE LIMITED TO 5,000 H/YR OF OPERATION. THROUGH PUT IS FOR EACH BOILER. | Sulfur Dioxide (SO2) | P | LOW SULFUR NATURAL GAS ONLY (LESS THAN 0.8% BY WEIGHT). LB/H LIMIT IS FOR EACH BOILER. | 0.0006 | LB/MMBTU |  | 0.021 | LB/H |  | 0.0006 | LB/MMBTU
NV-0039 | CHUCK LENZIE GENERATING STATION | NEVADA POWER COMPANY | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2001-06-01 | 2001 | A NEW ELECTRIC POWER PLANT CONSISTING OF FOUR COMBUSTION TURBINE GENERATORS, FOUR HEAT RECOVERY STEAM GENERATORS EACH WITH DUCT FIRING, AND TWO STEAM TURBINE GENERATORS FOR A TOTAL NOMINAL OUTPUT OF 1170 MW. THE FACILITY IS LOCATED AT 11405 U.S. HIGHWAY 9 | AUXILIARY BOILERS | 13.31 | NATURAL GAS | 44.1 | MMBTU/H | THESE (TWO) BOILERS WILL EACH BE OPERATED A MAXIMUM OF 6,000 HOURS PER YEAR ACCORDING TO THE APPLICATION FOR ATC. | Sulfur Dioxide (SO2) | P | USE OF PIPELINE-QUALITY NATURAL GAS | 0.4 | LB/H |  |  |  |  | 0.009 | LB/MMBTU |  | EMISSION LIMIT 1 APPLIES TO EACH AUXILIARY BOILER.
IN-0087 | DUKE ENERGY, VIGO LLC | DUKE ENERGY, VIGO LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-06-06 | 2001 |  | AUXILARY BOILER, NATURAL GAS (2) | 13.31 | NATURAL GAS | 46 | MMBTU/H | NATURAL GAS FIRED BOILERS (THROUGHPUT FOR EACH) LIMITED TO 500 H/YR OPERATION | Sulfur Dioxide (SO2) | P | NATURAL GAS AS FUEL. LIMIT IS FOR EACH BOILER. | 0.0006 | LB/MMBTU |  | 0.028 | LB/H |  | 0.0006 | LB/MMBTU
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-5302A AND H-5302B | 13.31 | NATURAL GAS | 35 | MMBTU/H EA | 35 MMBTU/H MAXIMUM RATE/CAPACITY EA, 30 MMBTU/H NOMINAL CAPACITY EA. | Sulfur Dioxide (SO2) | P | BURN NATURAL GAS WITH NO GREATER THAN 100 PPM H2S. BURN FUEL OIL WITH NO GREATER THAN 0.30 % SULFUR BY WEIGHT. | 500 | PPM | 3 H AVERAGE |  |  |  | 2.55 | LB/MMBTU | CALCULATED, SEE NOTES | EMISSIONS IN LB/MMBTU WERE CALCULATED USING THE ASSUMPTION THAT EMISSIONS IN PPM ARE AT 15% O2 AND THE FUEL IS NATURAL GAS.
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-4510A AND H-4510B | 13.31 | NAT GAS | 14.4 | MMBTU/H EACH |  | Sulfur Dioxide (SO2) | P | USE FUEL OIL WITH NO GREATER THAN 0.3% SULFUR BY WEIGHT AND NATURAL GAS WITH NO GREATER THAN 100 PPMVD. | 500 | PPM | 3 H AV |  |  |  | 2.55 | LB/MMBTU | CALCULATED, SEE NOTES | EMISSIONS IN LB/MMBTU WERE CALCULATED USING THE ASSUMPTION THAT EMISSIONS IN PPM ARE AT 15% O2 AND THE FUEL IS NATURAL GAS.
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-5701A AND H-5701B | 13.31 | NAT GAS | 29 | MMBTU/H EACH | 29 MMBTU/H MAXIMUM RATE/CAPACITY EA, 22.7 MMBTU/H NOMINAL CAPACITY EA. HEATERS BURN BOTH NATURAL GAS AND DIESEL FUELS. OPERATING RESTRICTION OF NO MORE THAN 200 H DURING ANY 12 CONSECUTIVE MOS, COMBINED, WHILE FIRING FUEL OIL. OPERATING RESTRICTION OF COM | Sulfur Dioxide (SO2) | P | BURN NATURAL GAS WITH NO GREATER THAN 100 PPM H2S. BURN FUEL OIL WITH NO GREATER THAN 0.30 % SULFUR BY WEIGHT. | 500 | PPM | 3 H AV |  |  |  | 2.55 | LB/MMBTU | CALCULATED, SEE NOTES | EMISSIONS IN LB/MMBTU WERE CALCULATED USING THE ASSUMPTION THAT EMISSIONS IN PPM ARE AT 15% O2 AND THE FUEL IS NATURAL GAS.
AL-0190 | GE PLASTICS | GE PLASTICS | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-07-13 | 2001 | SYNTHETIC ORGANIC CHEMICAL MANUFACTURER THAT PRODUCES POLYCARBONATE RESIN PELLETS | FURNACE, HOT OIL, 10 MMBTU/H | 13.31 | NATURAL GAS | 10 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | GOOD COMBUSTION PRACTICES | 0.01 | LB/H |  | 0.001 | LB/MMBTU |  | 0.001 | LB/MMBTU
AL-0190 | GE PLASTICS | GE PLASTICS | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-07-13 | 2001 | SYNTHETIC ORGANIC CHEMICAL MANUFACTURER THAT PRODUCES POLYCARBONATE RESIN PELLETS | FURNACE, HOT OIL, 20 MMBTU/H | 13.31 | NATURAL GAS | 20 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | GOOD COMBUSTION PRACTICES | 0.01 | LB/H |  | 0.0005 | LB/MMBTU |  | 0.0005 | LB/MMBTU
OH-0263 | FREMONT ENERGY CENTER, LLC | CALPINE CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-08-09 | 2001 | TWO 180 MW COMBINED CYCLE TURBINES (2 HRSGS),USING SELECTIVE CATALYTIC REDUCTION (SCR) AND OXIDATION CATALYST | AUXILIARY BOILER | 13.31 | NATURAL GAS | 80 | MMBTU/H | Auxiliary boiler, natural gas-fired, 80 mmBtu/hr | Sulfur Dioxide (SO2) | N |  | 0.48 | LB/H |  | 2.1 | T/YR |  | 0.006 | LB/MMBTU
OK-0044 | SMITH POCOLA ENERGY PROJECT | SMITH COGENERATION OK INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-16 | 2001 | ELEC. POWER GENERATION | AUXILIARY BOILERS, (2) | 13.31 | NATURAL GAS | 48 | MMBTU/H | THROUGHPUT FOR EACH | Sulfur Dioxide (SO2) | P | USE OF PIPELINE NATURAL GAS W/SULFUR CONTENT 2 GRAINS SULFUR/100 SCF | 0.57 | LB/H | combined | 2.47 | T/YR | combined | 0.2 | LB/MMBTU
IN-0110 | COGENTRIX LAWRENCE CO., LLC | COGENTRIX LAWRENCE CO., LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-10-05 | 2001 | POWER PLANT | BOILER, AUXILIARY, NATURAL GAS | 13.31 | NATURAL GAS | 35 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | GOOD COMBUSTION PRACTICE | 0.006 | LB/MMBTU |  | 0.21 | LB/H |  | 0.006 | LB/MMBTU
OH-0265 | DRESDEN ENERGY LLC | Dresden Energy | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-10-16 | 2001 | TWO 171.7 MW NATURAL GAS AND FUEL OIL- FIRED COMBUSTION TURBINES, COMBINED CYCLE; 49 MMBTU/HR NATURAL GAS FIRED BOILER; 2,250,000 GALLON FIXED ROOF STORAGE TANK FOR #2 FUEL OIL. | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 49 | MMBTU/H | Boiler is restricted to 800 hour of operation per a rolling 12 months. | Sulfur Dioxide (SO2) | P | THE MAXIMUM SULFUR CONTENT OF THE NATURAL GAS SHALL NOT EXCEED 0.3 GRAINS PER 100 STANDARD CUBIC FEET. | 0.05 | LB/H |  | 0.02 | T/YR |  | 0.001 | LB/MMBTU |  | Boiler is restricted to 800 hours or operation per a rolling 12 months.
OK-0043 | WEBERS FALLS ENERGY FACILITY | ENERGETIX | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-10-22 | 2001 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 30 | MMBTU/H | BOILER OPERATIONS LIMITED TO 3,000 HOURS/YEAR. | Sulfur Dioxide (SO2) | P | USE OF NATURAL GAS | 150 | PPM | [6 empty] | NOT AVAILABLE
AL-0181 | DUKE ENERGY AUTAUGA, LLC | DUKE ENERGY AUTAUGA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-10-23 | 2001 | COMBINED CYCLE ELECTRIC GENERATING PLANT. | 31.4 MMBTU/HR NATURAL GAS FIRED BOILER | 13.31 | NATURAL GAS | 31.4 | MMBTU/H | Operation limited to 2500 hrs/yr. | Sulfur Dioxide (SO2) | P | NATURAL GAS IS EXCLUSIVE FUEL. | 0.0057 | LB/MMBTU |  | 0.2 | LB/H
*WA-0292 | SATSOP COMBUSTION TURBINE PROJECT | GRAYS HARBOR ENERGY LLC | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2001-10-23 | 2001 | GE F7 TURBINE BASED COMBINED CYCLE NATURAL GAS ONLY FUELED COMBUSTION TURBINE INCLUDES COOLING TOWER AND EMERGENCY ICE GENERATOR AND FIRE WATER ENGINES | AUXILIARY BOILER | 13.31 | NAT GAS | 29.3 | MMBTU/H | 29.3 MMBTU/H IS THE DESIGN HEAT INPUT RATE FOR THE BOILER, AS PROVIDED BY THE STATE CONTACT PERSON. | Sulfur Dioxide (SO2) | N |  | 0.07 | LB/H | ANNUAL AVERAGE, CALCULATED MONTHLY | 1 | PPM @ 3% O2 | 3-H AVERAGE |  |  | NOT AVAILABLE | THE ORIGINAL PERMIT LIMITED SO2 EMISSIONS TO 0.03 LB/HR AND 0.001 LB/MMBTU.
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | 2001 | ELECTRICITY GENERATION | FUEL GAS HEATER | 13.31 | NATURAL GAS | 16 | MMBTU/H | FUEL GAS HEATER PRE-HEATS THE PIPELINE NATURAL GAS FUEL ENTERING THE COMBUSTION TURBINE UNITS AT 70 DEGREES F | Sulfur Dioxide (SO2) | P | NATURAL GAS FUEL | 0.069 | LB/H |  | 0.253 | T/YR |  | 0.0043 | LB/MMBTU
OK-0071 | MCCLAIN ENERGY FACILITY | NRG MCCLAIN LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-10-25 | 2001 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | USE OF PIPELINE QUALITY NATURAL GAS | 0.001 | LB/MMBTU |  |  |  |  | 0.001 | LB/MMBTU
PR-0007 | COGENERATION PLANT (AES-PRCP) | AES PUERTO RICO | PR | PUERTO RICO ENV QUALITY BOARD, AIR PROGRAM | 2001-10-29 | 2001 | COGENERATION UNIT | LIMESTONE DRYER | 13.31 | PROPANE | 13 | MMBTU/H | LIMESTONE DRYER INCLUDES A CRUSHER. HEATED AIR BOTH CLASSIFIES THE GROUND LIMESTONE AND DRIES THE MATERIAL. UNIT IS LIMITED TO A 505 CAPACITY FACTOR CALCULATED BASED ON 4380 H/CALENDAR YR. COMBUSTION CONTROLS WILL BE USED TO MINIMIZE AIR EMISSIONS. | Sulfur Dioxide (SO2) | P | USING PROPANE AND LOW SULFUR DISTILLATE OIL AND DIRECT CONTACT WITH LIMESTONE | 0.26 | LB/H |  |  |  |  | 0.02 | LB/MMBTU
TX-0378 | LA PORTE POLYPROPYLENE PLANT | ATOFINA PETROCHEMICALS INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-11-05 | 2001 | ATOFINA PROPOSES TO INSTALL A 60 MMBTU/H PACKAGE BOILER TO PROVIDE NEEDED STEAM CAPACITY. THE BURNER WILL MEET ESAD LIMIT OF 0.015 LB NOX/MMBTU FOR HOUSTON/GALVESTON. UPON STARTUP OF EPN ES-206, THE 40 MMBTU/H TEMPORARY BOILER (EPN TEMPBOILER) SHALL BE RE | PACKAGE BOILER BO-4 | 13.31 | NAT GAS | 60 | MMBTU/H |  | Sulfur Dioxide (SO2) | N | NONE INDICATED | 0.95 | LB/H |  | 4.17 | T/YR |  | 0.02 | LB/MMBTU | CALCULATED USING THROUGHPUT
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | 2001 | SOYBEAN EXTRACTION PLANT | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. There is a separate process entry for this boiler when firing fuel oil. | Sulfur Dioxide (SO2) | N |  | 0.055 | LB/H |  | 0.6 | LB/MMCF |  | 0.0006 | LB/MMBTU |  | Using AP-42 emission factor of 0.6 lb/million cubic feet
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | 2001 | SOYBEAN EXTRACTION PLANT | DRYER, SOY PROTEIN CONCENTRATE - COMBUSTION | 13.31 | NATURAL GAS | 37 | MMBTU/H | Baghouse with 100% capture. Process is in 2 parts - dryer - combustion, and dryer - pm. | Sulfur Dioxide (SO2) | N |  | 0.021 | LB/H |  | 0.09 | T/YR |  | 0.0006 | LB/MMBTU |  | Emissions from natural gas combustion, using 0.0006 lb SO2/mmBtu
IN-0095 | ALLEGHENY ENERGY SUPPLY CO. LLC | ALLEGHENY ENERGY SUPPLY CO. LLC (ACADIA BAY ENERGY | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-12-07 | 2001 | ELECTRIC POWER GENERATING STATION | AUXILLIARY BOILER | 13.31 | NATURAL GAS | 21 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | LOW SULFUR CONTENT NATURAL GAS | 0.0006 | LB/MMBTU |  |  |  |  | 0.0006 | LB/MMBTU
AL-0180 | DUKE ENERGY DALE, LLC | DUKE ENERGY DALE, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-12-11 | 2001 | NATURAL GAS FIRED COMBINED CYCLE ELECTRIC GENERATING PLANT. | 35 MMBTU/HR NAT. GAS FIRED AUXILIARY BOILER | 13.31 | NATURAL GAS | 35 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | NATURAL GAS | 0.0057 | LB/MMBTU |  | 0.2 | LB/H
OH-0257 | JACKSON COUNTY POWER, LLC | JACKSON COUNTY POWER, LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-12-27 | 2001 | FOUR 305 MW NATURAL-GAS FIRED COMBUSTION TURBINES, COMBINED CYCLE, WITH DLN AND SCR | AUXILIARY BOILER | 13.31 | NATURAL GAS | 76 | MMBTU/H | Limited to 3000 hours of operation per rolling 12 month period. | Sulfur Dioxide (SO2) | N | LOW SULFUR FUEL, NATURAL GAS SULFUR LIMIT - 2 GR/100 SCF | 0.5 | LB/H |  | 0.75 | T/YR |  | 0.006 | LB/MMBTU |  | Additional limit: 2 grains/100 scf natural gas
LA-0174 | PORT HUDSON OPERATIONS | GEORGIA-PACIFIC CORPORATION | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2002-01-25 | 2002 | PULP MILL | POWER BOILER NO. 2 | 13.31 | NAT GAS | 65.5 | MMBTU/H | EMISSION POINT NO. 6. | Sulfur Dioxide (SO2) | P | FIRING NATURAL GAS | 0.26 | LB/H |  | 0.17 | T/YR |  | 0.004 | LB/MMBTU
TX-0388 | SAND HILL ENERGY CENTER | AUSTIN ELECTRIC UTILITY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-02-12 | 2002 | ELECTRIC POWER GENERATOR CONSISTING OF NATURAL GAS-FIRED COMBUSTION TURBINE WITH HRSG. | INLET AIR HEATERS (3) | 13.31 |  |  |  |  | Sulfur Dioxide (SO2) | P | FUEL RESTRICTED TO 0.23 GR S/100 DSCF. | 0.003 | LB/H |  | 0.0015 | T/YR
AR-0051 | DUKE ENERGY-JACKSON FACILITY | DUKE ENERGY | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-04-01 | 2002 | 620 MW NATURAL GAS TURBINE ELECTRIC UTILITY PLANT. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | FUELS LIMIT: < 2 GR/100 DSCF |  |  | see notes | [6 empty] | no emission rate limit, fuels limit.
OH-0264 | NORTON ENERGY STORAGE, LLC | NORTON ENERGY | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-05-23 | 2002 | NINE 300 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE WITH DLN AND SCR; TEN 11.45 MMBTU/H NATURAL GAS-FIRED FUEL SUPPLY HEATERS/BOILERS; SEVEN 12.84 MMBTU/H NATURAL GAS-FIRED RECUPERATOR PRE HEATERS/BOILERS | RECUPERATOR PRE-HEATERS (9) | 13.31 | NATURAL GAS | 12.84 | MMBTU/H | Each boiler is limited to 100 hour of operation per rolling 12 months. | Sulfur Dioxide (SO2) | P | THE MAXIMUM SULFUR CONTENT OF THE NATURAL GAS SHALL NOT EXCEED 0.6 GRAINS PER 100 STANDARD CUBIC FEET. | 0.023 | LB/H |  | 0.0012 | T/YR |  | 0.002 | LB/MMBTU |  | Limits are for each boiler. Each boiler is retricted to 100 hours of operation.
OH-0264 | NORTON ENERGY STORAGE, LLC | NORTON ENERGY | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-05-23 | 2002 | NINE 300 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE WITH DLN AND SCR; TEN 11.45 MMBTU/H NATURAL GAS-FIRED FUEL SUPPLY HEATERS/BOILERS; SEVEN 12.84 MMBTU/H NATURAL GAS-FIRED RECUPERATOR PRE HEATERS/BOILERS | FUEL SUPPLY HEATERS (9) | 13.31 | NATURAL GAS | 11.45 | MMBTU/H | Each fuel supply heater is limited to a maximum annual cumulative fuel heat input of 47,630 mmBtu per rolling 12 months. | Sulfur Dioxide (SO2) | P | THE MAXIMUM SULFUR CONTENT OF THE NATURAL GAS SHALL NOT EXCEED 0.6 GRAINS PER 100 STANDARD CUBIC FEET. | 0.021 | LB/H |  | 0.04 | T/YR |  | 0.002 | LB/MMBTU |  | Limits are for each heater.
NM-0044 | CLOVIS ENERGY FACILITY | DUKE ENERGY CURRY LLC | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2002-06-27 | 2002 | THIS IS A 1,200 MW COMBINED CYCLE MERCHANT POWER PLANT. | AUXILIARY BOILERS (AUX-1 AND AUX-2) | 13.31 | NATURAL GAS | 33 | MMBTU/H | Emission limits are for each (Aux-1 and Aux-2) Auxiliary Boiler. | Sulfur Dioxide (SO2) | P | NATURAL GAS, GOOD COMBUSTION PRACTICE | 0.1 | LB/H |  |  |  |  | 0.003 | LB/MMBTU | calculated
KY-0087 | QUEBECOR WORLD FRANKLIN | QUEBECOR WORLD FRANKLIN | KY | KENTUCKY DEP, DIV FOR AIR QUALITY | 2002-07-12 | 2002 | ROTOGRAVURE PRINTING PLANT | BOILER, NATURAL GAS, #4 | 13.31 | NATURAL GAS | 33.5 | MMBTU/H | Boiler is a Cleaver Brooks indirect heat exchanger, using natural gas as primary fuel and no. 2 fuel oil as standby fuel. | Sulfur Dioxide (SO2) | P | CLEAN FUEL: FUEL OIL LIMITED TO < 0.5% S BY WT | 1.057 | LB/MMBTU |  |  |  |  | 1.057 | LB/MMBTU
OH-0248 | LAWRENCE ENERGY | CALPINE CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-09-24 | 2002 | THREE 180 MW GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE, WITH DLN, SCR AND OXIDATION CATALYST | BOILER | 13.31 | NATURAL GAS | 99 | MMBTU/H |  | Sulfur Dioxide (SO2) | N |  | 0.56 | LB/H |  | 0.0057 | LB/MMBTU |  | 0.0057 | LB/MMBTU |  | Limits are for each boiler.
WI-0195 | SENA NIAGARA MILL | STORA ENSO NORTH AMERICA | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2002-10-18 | 2002 |  | PROCESS HEATER, PAPER MACHINE P51 | 13.31 | NATURAL GAS | 34.4 | MMBTU/H | Throughput is total for natural gas IR and flotation dryers. | Sulfur Dioxide (SO2) | P | BACT IS USE OF NATURAL GAS |  |  | see notes | [6 empty] | No emission rate limits, BACT is pollution prevention
NJ-0062 | CONSOLIDATE EDISON DEVELOPMENT (CED) | CONSOLIDATED EDISON DVPMT.- LAKEWOOD GEN. FACILITY | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2002-10-22 | 2002 | POWER GENERATION | FUEL GAS HEATERS (3 UNITS) | 13.31 | NATURAL GAS | 4.62 | MMBTU/H | INSTALLATION OF 3 NEW FUEL GAS HEATERS@ 4.62 MMBTU/HR EACH. FUEL: NATURAL GAS. | Sulfur Dioxide (SO2) | N | LOW SULFUR FUEL. | 0.014 | LB/H |  | 0.003 | LB/MMBTU
VA-0255 | VA POWER - POSSUM POINT | Virginia Power | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-11-18 | 2002 | THIE PERMIT WAS AMENDED AND APPROVED ON 11/18/2002 FROM THE PERMIT THAT WAS DATED 10/05/2001. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 99 | MMBTU/H | 2 Auxiliary boilers. | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL AND GOOD COMBUSTION PRACTICES. | 0.1 | LB/H | EACH UNIT | 0.44 | T/YR | UNITS COMBINED | 0.001 | LB/MMBTU | EACH UNIT
TX-0408 | INDIAN ROCK GATHERING COMPANY LP | INDIAN ROCK GATHERING COMPANY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-11-22 | 2002 | NATURAL GAS PROCESSING FACILITY | AUXILIARY BOILER, (2) | 13.31 | NATURAL GAS | 6 | MMBTU/H | BOILERS ARE UNCONTROLLED BECAUSE BOILER DUTY IS <40 MMBTU/H. | Sulfur Dioxide (SO2) | N |  | 0.01 | LB/H | EACH | 0.02 | T/YR | EACH | 0.0017 | LB/MMBTU |  | UNCONTROLLED BECAUSE BOILER IS LESS THAN 40 MMBTU/H.
VA-0243 | STANLEY FURNITURE |  | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-12-01 | 2002 | WOOD HOUSEHOLD FURNITURE MFG. | BOILER, NAT GAS & OIL | 13.31 | NATURAL GAS | 26.5 | MMBTU/H | KEWANEE NATURAL GAS/DISTILLATE OIL BOILER. THROUGHPUT 26.5 MMBTU/HR - 450,000 GAL #2 OIL. ADDITIONAL SCC, 10200502. FOR ALL POLLUTANTS, NO CONTROLS, EMISSION LIMITS IN T/YR ONLY | Sulfur Dioxide (SO2) | N | EMISSION LIMITS IN T/YR ONLY | 16 | T/YR | [6 empty] | NOT AVAILABLE
TX-0392 | LUCITE BEAUMONT | INEOS ACRYLICS, INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-09 | 2002 | SULFURIC ACID REGENERATION FACILITY | NO.1 PRE-HEATER | 13.31 | NATURAL GAS |  |  |  | Sulfur Dioxide (SO2) | N |  | 0.1 | LB/H |  | 0.55 | T/YR
TX-0392 | LUCITE BEAUMONT | INEOS ACRYLICS, INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-09 | 2002 | SULFURIC ACID REGENERATION FACILITY | NO. 2 PRE-HEATER | 13.31 | NATURAL GAS |  |  |  | Sulfur Dioxide (SO2) | N |  | 0.1 | LB/H |  | 0.55 | T/YR
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | HEAT TRANSFER FLUID HEATER, H202 | 13.31 | NATURAL GAS | 31 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | FUEL GAS SHALL BE SWEET NATURAL GAS CONTAINING NO MORE THAN 5 GR S/100 DSCF. | 0.02 | LB/H |  | 0.08 | T/YR |  | 0.0006 | LB/MMBTU | CALCULATED, USING THROUGHPUT
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | HEAT TRANSFER FLUID HEATER, H2202 | 13.31 | NATURAL GAS | 31 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | FUEL GAS SHALL BE SWEET NATURAL GAS CONTAINING NO MORE THAN 0.5 GR S/100 DSCF. | 0.02 | LB/H |  | 0.08 | T/YR |  | 0.0006 | LB/MMBTU | CALCULATED USING THROUGHPUT
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | (2) STEAM BOILERS, X-426A AND X-426B | 13.31 | NATURAL GAS | 15.8 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | FUEL GAS SHALL BE SWEET NATURAL GAS CONTAINING NO MORE THAN 5 GR S/100 DSCF. | 0.01 | LB/H | EACH | 0.04 | T/YR | EACH | 0.0006 | LB/MMBTU | EACH, CALCULATED USING THROUGHPUT
IA-0062 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT (IPL) | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-12-20 | 2002 | PERMITS WERE AMENDED ON 6/26/03. RBLC ID IA-0062 WAS CORRECTED AS MOST OF THE CHANGES WERE MINOR (BASED ON OPERATIONAL & DESIGN CHANGES BEING MADE AS PLANT IS CONSTRUCTED). THE NEW DEW POINT HEATER HAS BEEN GIVEN A NEW RBLC ID. | GAS HEATER, (2) | 13.31 | NATURAL GAS | 16.4 | MMBTU/H | Natural Gas fired Heaters, 16.4 MMBTU/HR capacity for each. Operating hours reduced from 8760 hours to 6000 hours each. | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL, NG | 0.0006 | LB/MMBTU |  |  |  |  | 0.0006 | LB/MMBTU
IA-0062 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT (IPL) | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-12-20 | 2002 | PERMITS WERE AMENDED ON 6/26/03. RBLC ID IA-0062 WAS CORRECTED AS MOST OF THE CHANGES WERE MINOR (BASED ON OPERATIONAL & DESIGN CHANGES BEING MADE AS PLANT IS CONSTRUCTED). THE NEW DEW POINT HEATER HAS BEEN GIVEN A NEW RBLC ID. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 68 | MMBTU/H | Limited to 6000 hours of operation per year. | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL, NG | 0.0006 | LB/MMBTU |  |  |  |  | 0.0006 | LB/MMBTU
TX-0389 | BAYTOWN CARBON BLACK PLANT | DEGUSSA ENGINEERED CARBONS, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-31 | 2002 |  | BACK-UP BOILER | 13.31 | NATURAL GAS | 13.4 | MMBUT/H |  | Sulfur Dioxide (SO2) | N |  | 0.01 | LB/H |  | 0.05 | T/YR
VA-0279 | CINCAP - MARTINSVILLE | Cinergy Capital & Trading | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-01-08 | 2003 | POWER PLANT | HEATER, PIPELINE WATER BATH, NATURAL GAS | 13.31 | NATURAL GAS | 5 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | FUEL SULFUR LIMIT: 0.8 GR/100 DSCF ANNUAL AVG., 1.5 GR/100 DSCF ON AN HOURLY BASIS |  |  | see note | [6 empty] | limit is fuel sulfur limit, no emission rate limit.
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HOT OIL HEATER, EPN6 | 13.31 | NAT GAS | 12 | MMBTU/H |  | Sulfur Dioxide (SO2) | N | NONE INDICATED | 0.01 | LB/H |  | 0.03 | T/YR |  | 0.0008 | LB/MMBTU | SEE NOTE | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | GLYCOL REBOILER, EPN11 | 13.31 | NAT GAS | 2.5 | MMBTU/H |  | Sulfur Dioxide (SO2) | N | NONE INDICATED | 0.02 | LB/H |  | 0.01 | T/YR |  | 0.008 | LB/MMBTU | SEE NOTE | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HOT OIL HEATER, EPN26 | 13.31 | NAT GAS | 32.5 | MMBTU/H |  | Sulfur Dioxide (SO2) | N | NONE INDICATED | 0.02 | LB/H |  | 0.08 | T/YR |  | 0.0006 | LB/MMBTU | SEE NOTE | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HP TEG FIREBOX, EPN30 | 13.31 | NAT GAS | 3 | MMBTU/H |  | Sulfur Dioxide (SO2) | N | NONE INDICATED | 0.01 | LB/H |  | 0.01 | T/YR |  | 0.003 | LB/MMBTU | CALCULATED, SEE NOTE | STANDARDIZED EMISSION LIMIT CALCULATED FROM HEAT RATING AND HOURLY EMISSION LIMIT.
OK-0090 | DUKE ENERGY STEPHENS, LLC STEPHENS ENERGY | DUKE ENERGY | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2003-03-21 | 2003 | MERCHANT POWER PLANT - NOMINAL TOTAL OF 620 MW. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | BACT IS USE OF PIPE-LINE QUALITY NATURAL GAS | 0.2 | LB/H |  |  |  |  | 0.006 | LB/MMBTU | calculated
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 | 2003 |  | BOILER NO. 1 | 13.31 | NATURAL GAS | 43.2 | MMBTU/H | One of two boilers | Sulfur Dioxide (SO2) | B | CONTINUOUS EMISSION MONITORING SYSTEM AND GOOD COMBUSTION PRACTICES. | 2.19 | LB/H | each unit |  |  |  | 0.05 | LB/MMBTU |  | One of two units.
OH-0276 | CHARTER STEEL | CHARTER MANUFACTURING CO., INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-04-14 | 2003 | NEW MELT SHOP AT EXISTING FACILITY, INCLUDES NEW: ELECTRIC ARC FURNACE; LADLE METALLURGY FURNACE; VACUUM OXYGEN DEGASSER (VOD); VOC BOILER; CONTINUOUS CASTING MACHINES; 3 SILOS; 6 LADLE PREHEATERS; CUT-OFF-TORCH; 3 TUNDISH PREHEATERS; PROCESS SPACE HEATER | BOILER FOR VACUUM OXYGEN DEGASSER VESSEL | 13.31 | NATURAL GAS | 25 | MMBTU/H | VACUUM OXYGEN DEGASSER VESSEL BOILER, WITH LOW NOX BURNER | Sulfur Dioxide (SO2) | N |  | 0.01 | LB/H | FROM NATURAL GAS COMBUSTION | 0.06 | T/YR | FROM NATURAL GAS COMBUSTION |  |  | NOT AVAILABLE
IA-0068 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT - EMERY GENERATING STATI | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2003-06-26 | 2003 | IPL CHANGED NAMES FROM THE POWER IOWA ENERGY CENTER (PIEC) TO THE EMERY GENERATING STATION. | GAS HEATER | 13.31 | NATURAL GAS | 9 | MMBTU/H | One natural gas dew point heater is added. | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL, NATURAL GAS | 0.0006 | LB/MMBTU |  | 0.02 | T/YR |  | 0.0006 | LB/MMBTU
TX-0458 | JACK COUNTY POWER PLANT | DUKE ENERGY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-07-22 | 2003 | DUKE ENERGY JACK, L.P. IS CONSTRUCTING A 620 MW COMBINED CYCLE POWER PLANT. TWO COMBUSTION TURBINES WILL EACH PROVIDE APPROXIMATELY 170 MW OF ELECTRICITY. A 550 MMBTU/HR DUCT BURNER ON EACH TURBINE EXHAUST STREAM WILL ADD SUPPLEMENTAL HEAT TO THE HEAT REC | AUXILIARY BOILER | 13.31 | NATURAL GAS | 36 | mmbtu/h |  | Sulfur Dioxide (SO2) | N |  | 0.3 | LB/H |  | 0.7 | T/YR
OH-0254 | DUKE ENERGY WASHINGTON COUNTY LLC | DUKE ENERGY NORTH AMERICA | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-08-14 | 2003 | TWO 170 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE | BOILER | 13.31 | NATURAL GAS | 30.6 | MMBTU/H | THE MAXIMUM ANNUAL FUEL HEAT INPUT SHALL NOT EXCEED 128,000 MMBTU/ROLLING 12-MONTHS | Sulfur Dioxide (SO2) | N |  | 0.031 | LB/H |  | 0.07 | T/ROLLING 12-MONTHS |  | 0.001 | LB/MMBTU
AZ-0049 | LA PAZ GENERATING FACILITY | ALLEGHENY ENERGY SUPPLY LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2003-09-04 | 2003 | NATURAL GAS FIRED, COMBINED CYCLE GENERATING STATION | AUXILIARY BOILER FOR GE TURBINE | 13.31 | NATURAL GAS | 41 | MMBTU/H | THIS BOILER IS TO BE USED IF THE GE TURBINE SETUP IS SELECTED. | Sulfur Dioxide (SO2) | N |  | 0.0025 | LB/MMBTU |  |  |  |  | 0.0025 | LB/MMBTU
AZ-0049 | LA PAZ GENERATING FACILITY | ALLEGHENY ENERGY SUPPLY LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2003-09-04 | 2003 | NATURAL GAS FIRED, COMBINED CYCLE GENERATING STATION | AUXILIARY BOILER FOR SIEMENS TURBINES | 13.31 | NATURAL GAS | 55.34 | MMBTU/H | THIS BOILER IS FOR USE WHEN THE SIEMENS TURBINE SYSTEM IS SELECTED. | Sulfur Dioxide (SO2) | N |  | 0.0025 | LB/MMBTU |  |  |  |  | 0.0025 | LB/MMBTU
IN-0108 | NUCOR STEEL | NUCOR STEEL | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2003-11-21 | 2003 | STEEL MINI MILL | BOILER, NATURAL GAS, (2) | 13.31 | NATURAL GAS | 34 | MMBTU/H | Throughput for each. Propane is backup fuel. These boilers supply steam to the entire cold mill area of the plant. Subject to NSPS Subpart Dc | Sulfur Dioxide (SO2) | P | COMPLIANCE BY USING NATURAL GAS | 0.0006 | LB/MMBTU |  |  |  |  | 0.0006 | LB/MMBTU
MN-0054 | MANKATO ENERGY CENTER |  | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2003-12-04 | 2003 | COMBINED CYCLE GAS TURBINE ELECTRIC POWER PLANT. TWO IDENTICAL GE FRAME F7A GAS TURBINES EACH WITH HRSG W/DUCT BURNERS FEEDING STEAM TO COMMON STEAM TURBINES. PRIMARY FUEL IS NG, NO. 2 VERY LOW SULFUR DISTILLATE OIL FOR BACKUP. ALSO, AUX. BOILER, DIESEL E | BOILER, COMMERCIAL | 13.31 | NATURAL GAS | 70 | MMBTU/H | NATURAL GAS ONLY | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL | 0.001 | LB/MMBTU |  |  |  |  | 0.001 | LB/MMBTU
AR-0076 | U.S. ARMY, PINE BLUFF ARSENAL | U.S. ARMY, PINE BLUFF ARSENAL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-02-17 | 2004 | PINE BLUFF ARSENAL IS THE ARMY'S ONLY CHEMICAL ARSENAL AND THE ONLY INSTALLATION WITH BOTH MANUFACTURING AND DEPOT FUNCTIONS. OPERATIONAL FUNCTIONS INCLUDE: AMMUNITION OPERATIONS; CHEMICAL AND BIOLOGICAL DEFENSE OPERATIONS; PRODUCT AND PROCESS DEVELOPMENT | BOILER, PROCESS STEAM, (2) SN-PBCDF-03, -04 | 13.31 | NATURAL GAS | 0.03 | MMDSCF/H | THROUGH PUT FOR EACH. ADDITIONAL THROUGHPUT: 28.4 MMBTU/H (EACH). PROCESS STEAM BOILER SERVES BRINE REDUCTION AREA EQUIPMENT. | Sulfur Dioxide (SO2) | P | LOW-SULFUR NATURAL GAS ONLY. | 0.1 | LB/H | EACH |  |  |  | 0.0035 | LB/MMBTU | CALCULATED
AR-0076 | U.S. ARMY, PINE BLUFF ARSENAL | U.S. ARMY, PINE BLUFF ARSENAL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-02-17 | 2004 | PINE BLUFF ARSENAL IS THE ARMY'S ONLY CHEMICAL ARSENAL AND THE ONLY INSTALLATION WITH BOTH MANUFACTURING AND DEPOT FUNCTIONS. OPERATIONAL FUNCTIONS INCLUDE: AMMUNITION OPERATIONS; CHEMICAL AND BIOLOGICAL DEFENSE OPERATIONS; PRODUCT AND PROCESS DEVELOPMENT | BOILER, HOT WATER, (2) SN-PBCDF-05, -06 | 13.31 | NATURAL GAS | 0.01 | MMDSCF/H | ADDITIONAL THROUGHPUT: 11.7 MMBTU/H, THROUGHPUT FOR EACH. | Sulfur Dioxide (SO2) | P | LOW-SULFUR NATURAL GAS ONLY. | 0.1 | LB/H | EACH |  |  |  | 0.0085 | LB/MMBTU | CALCULATED
AR-0076 | U.S. ARMY, PINE BLUFF ARSENAL | U.S. ARMY, PINE BLUFF ARSENAL | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-02-17 | 2004 | PINE BLUFF ARSENAL IS THE ARMY'S ONLY CHEMICAL ARSENAL AND THE ONLY INSTALLATION WITH BOTH MANUFACTURING AND DEPOT FUNCTIONS. OPERATIONAL FUNCTIONS INCLUDE: AMMUNITION OPERATIONS; CHEMICAL AND BIOLOGICAL DEFENSE OPERATIONS; PRODUCT AND PROCESS DEVELOPMENT | BOILER, LABORATORY SN-PBCDF-16 | 13.31 | NATURAL GAS | 1.4 | mmbtu/h |  | Sulfur Dioxide (SO2) | P | LOW-SULFUR NATURAL GAS ONLY. | 0.1 | LB/H |  |  |  |  | 0.071 | LB/MMBTU | CALCULATED
NV-0037 | COPPER MOUNTAIN POWER | SEMPRA ENERGY RESOURCES | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2004-05-14 | 2004 | A 600 MW COMBINED CYCLE ELECTRICAL GENERATION FACILITY CONSISTING OF TWO COMBUSTION TURBINE GENERATORS WITH HEAT RECOVERY STEAM GENERATORS, ONE STEAM TURBINE GENERATOR, AND ONE AUXILIARY BOILER. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 60 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | USE OF LOW-SULFUR NATURAL GAS | 0.04 | LB/H
AR-0086 | NUCOR-YAMATO STEEL COMPANY, BLYTHEVILLE MILL | NUCOR-YAMATO STEEL COMPANY | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-06-11 | 2004 |  | VTD BOILER | 13.31 | NATURAL GAS | 50 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | GOOD COMBUSTION PRACTICE, NATURAL GAS COMBUSTION | 0.1 | LB/H |  | 0.2 | T/YR |  | 0.0006 | LB/MMBTU
NE-0026 | NUCOR STEEL DIVISION | NUCOR STEEL CORP. | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2004-06-22 | 2004 |  | NNII REHEAT FURNACE | 13.31 | NATURAL GAS | 143 | MMBTU/H |  | Sulfur Dioxide (SO2) | N |  | 0.0006 | LB/MMBTU
NE-0026 | NUCOR STEEL DIVISION | NUCOR STEEL CORP. | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2004-06-22 | 2004 |  | NNII BILET POST-HEATER | 13.31 | NATURAL GAS | 6.8 | MMBTU/H |  | Sulfur Dioxide (SO2) | N |  | 0.0006 | LB/MMBTU
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | 2004 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, NATURAL GAS (1) | 13.31 | NATURAL GAS | 40 | MMBTU/H | AUXILIARY BOILER. | Sulfur Dioxide (SO2) | P | LOW SULFUR FUEL 0.8 GR/SCF, CALENDAR YEAR AVERAGE |  |  | see note | [6 empty] | BACT is fuel sulfur limit.
AR-0077 | BLUEWATER PROJECT | STEELCORR, INC. | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-07-22 | 2004 | THE FACILITY IS A NEW SPECIALTY STEEL MILL PRODUCING VARIOUS HOT ROLLED, COLD ROLLED AND GALVANIZED PRODUCTS FOR VARIOUS END USE MARKETS. AFIN: 47-00541 | BOILERS | 13.31 | NATURAL GAS | 22 | MMBTU/H | ENTRY INCLUDES TWO BOILERS. THE 22 MMBTU/H PICKLE LINE BOILER, 51 MMBTU/H VACUUM DEGASSER BOILERS. | Sulfur Dioxide (SO2) | P | NATURAL GAS COMBUSTION ONLY | 0.0006 | LB/MMBTU |  |  |  |  | 0.0006 | LB/MMBTU
WI-0226 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE (WPS) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-08-27 | 2004 | ELECTRIC UTILITY | NATURAL GAS FIRED BOILER | 13.31 | NATURAL GAS | 46.2 | MMBTU/H | NOT PSD | Sulfur Dioxide (SO2) | P | NATURAL GAS FUEL ONLY | 0.05 | LB/H
WI-0227 | PORT WASHINGTON GENERATING STATION | WE ENERGIES (WEPCO) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-13 | 2004 | ELECTRIC GENERATION | NATURAL GAS FIRED AUXILLIARY BOILER | 13.31 | NATURAL GAS | 97.1 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | NATURAL GAS FUEL | 0.06 | LB/H |  |  |  |  | 0.006 | LB/MMBTU | CALCULATED
WI-0227 | PORT WASHINGTON GENERATING STATION | WE ENERGIES (WEPCO) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-13 | 2004 | ELECTRIC GENERATION | GAS HEATER (P06, S06) | 13.31 | NATURAL GAS | 10 | MMBTU/H | GAS CONDITIONING HEATER | Sulfur Dioxide (SO2) | P | NATURAL GAS FUEL | 0.02 | LB/H |  |  |  |  | 0.002 | LB/MMBTU | CALCULATED
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | B63, S63; B64, S64 - NATURAL GAS STATION HEATER 1 AND 2 | 13.31 | NATURAL GAS | 0.75 | MMBTU/H | EMISSION LIMITS ARE THOSE FOR EACH UNIT. | Sulfur Dioxide (SO2) | P | NATURAL GAS | 0.0004 | LB/H | [6 empty] | NOT AVAILABLE | (LIMIT IS FOR EACH UNIT)
AZ-0047 | WELLTON MOHAWK GENERATING STATION | DOME VALLEY ENERGY PARTNERS | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2004-12-01 | 2004 | COMBINED CYCLE GAS-FIRED ELECTRICITY GENERATING STATION | AUXILIARY BOILER | 13.31 | NATURAL GAS | 38 | MMBTU/H |  | Sulfur Dioxide (SO2) | N |  | 0.0023 | LB/MMBTU | BASED ON HIGHER HEATING VALUE OF FUEL |  |  |  | 0.0023 | LB/MMBTU
OH-0252 | DUKE ENERGY HANGING ROCK ENERGY FACILITY | DUKE ENERGY HANGING ROCK, LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2004-12-28 | 2004 | FOUR NATURAL GAS (NG) FIRED COMBUSTION TURBINES, WITH DUCT BURNERS; COMBINED CYCLE, EACH 172 MW | BOILERS (2) | 13.31 | NATURAL GAS | 30.6 | MMBTU/H | LIMITS ARE FOR EACH BOILER INDIVIDUALLY. THE MAXIMUM FUEL HEAT INPUT SHALL NOT EXCEED 91,500 MMBTU/ROLLING 12-MONTHS FOR EACH BOILER. | Sulfur Dioxide (SO2) | P | THE MAXIMUM S CONTENT OF THE NATURAL GAS SHALL NOT EXCEED 2 GRAINS PER 100 CUBIC FEET. | 0.031 | LB/H | EACH BOILER | 0.046 | T/ROLLING 12-MONTHS | EACH BOILER | 0.001 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
LA-0192 | CRESCENT CITY POWER | CRESENT CITY POWER, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-06-06 | 2005 | NEW 600 MW NATURAL GAS-FIRED COMBINED CYCLE POWER PLANT | FUEL GAS HEATERS (3) | 13.31 |  | 19 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | USE OF LOW SULFUR PIPELINE NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.008 | LB/H | HOURLY MAXIMUM | 0.003 | T/YR | *SEE NOTES. ANNUAL MAXIMUM | 0.0004 | LB/MMBTU | ANNUAL AVERAGE | *TPY LIMIT FOR ALL 3 HEATERS. AGGREGATE HEAT INPUT IS LIMITED TO 14,250 MM BTU/YR. ONLY 2 OF THE 3 HEATERS ARE ALLOWED TO OPERATE AT ANY GIVEN TIME.
LA-0203 | OAKDALE OSB PLANT | MARTCO LIMITED PARTNERSHIP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-06-13 | 2005 | PSD FOR A NEW ORIENTED STRAND BOARD (OSB) MANUFACTURING FACILITY CAPABLE OF PRODUCING 900,000 MSF 3/8 INCH OSB PER YEAR. | AUXILIARY THERMAL OIL HEATER | 13.31 | NATURAL GAS | 66.5 | MMBTU/H | OPERATING TIME = 500 HR/YR. | Sulfur Dioxide (SO2) | P | USE OF NATURAL GAS AS FUEL AND GOOD COMBUSTION PRACTICES | 0.05 | LB/H | HOURLY MAXIMUM |  |  |  | 0.001 | LB/MMBTU | CALCULATED BY CATC
AK-0062 | BADAMI DEVELOPMENT FACILITY | BP EXPLORATION ALASKA | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2005-08-19 | 2005 | OIL AND GAS PROCESSING FACILITY | NATCO PRODUCTION HEATER | 13.31 | NATURAL GAS | 34 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | LIMIT SULFUR CONTENT IN FUEL COMBUSTED | 250 | PPMV | H2S CONTENT OF NATURAL GAS | [6 empty] | LIMIT SULFUR CONTENT IN FUEL COMBUSTED * EMISSION UNITS AND NUMERIC LIMITS ARE REQUIRED FOR SO2 USING APPENDIX E. PROCESS CODE 13.110
AK-0062 | BADAMI DEVELOPMENT FACILITY | BP EXPLORATION ALASKA | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2005-08-19 | 2005 | OIL AND GAS PROCESSING FACILITY | NATCO MISCIBLE INJECTION HEATER | 13.31 | NATURAL GAS | 14.87 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | LIMIT SULFUR CONTENT OF FUEL COMBUSTED | 250 | PPMV | H2S CONTENT OF NATURAL GAS |  |  |  | 1.28 | *LB/MMBTU | *SEE NOTES | * LIMIT SULFUR CONTENT OF FUEL COMBUSTED
AK-0062 | BADAMI DEVELOPMENT FACILITY | BP EXPLORATION ALASKA | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2005-08-19 | 2005 | OIL AND GAS PROCESSING FACILITY | NATCO TEG REBOILER | 13.31 | NATURAL GAS | 1.34 | MMBTU/H |  | Sulfur Dioxide (SO2) | P | LIMIT SULFUR CONTENT OF FUEL COMBUSTED | 250 | PPMV | H2S CONTENT OF NATURAL GAS |  |  |  | 1.28 | LB/MMBTU | *SEE NOTES | LIMIT SULFUR CONTENT OF FUEL COMBUSTED
*NV-0046 | GOODSPRINGS COMPRESSOR STATION | KERN RIVER GAS TRANSMISSION COMPANY | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2006-05-16 | 2006 | THE FACILITY IS A COMPRESSOR STATION ON AN INTER-STATE PIPELINE FOR TRANSPORTING NATURAL GAS. THE FACILITY IS A MAJOR STATIONARY SOURCE FOR NITROGEN OXIDES IN A NON-ATTAINMENT AREA FOR OZONE AIR QUALITY. | COMMERCIAL/INSTITUTIONAL BOILER | 13.31 | NATURAL GAS | 3.85 | MMBTU/H | THE UNIT'S MODEL IDENTIFICATION IS PEERLESS 724 FDA WU. | Sulfur Dioxide (SO2) | P | LOW-SULFUR NATURAL GAS IS THE ONLY FUEL FOR THE PROCESS. | 0.0026 | LB/MMBTU |  | 0.01 | T/YR |  | 0.0026 | LB/MMBTU
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | 2007 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NATURAL GAS | 13.31 | NATURAL GAS | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. WITH #2 OIL BACKUP TWO SET OF LIMITS, THIS ONE FOR NATURAL GAS | Sulfur Dioxide (SO2) | N |  | 0.01 | LB/H |  | 3.64 | T/YR |  | 0.0006 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
*AL-0231 | NUCOR DECATUR LLC | NUCOR CORPORATION | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-06-12 | 2007 | THE FACILITY PRODUCES STEEL COILS PRIMARILY FROM STEEL SCRAP USING THE ELECTRIC ARC FURNACE (EAF) PROCESS. | VACUUM DEGASSER BOILER | 13.31 | NATURAL GAS | 95 | MMBTU/H |  | Sulfur Dioxide (SO2) | N |  | 0.0006 | LB/MMBTU |  | 0.057 | LB/H
*AL-0231 | NUCOR DECATUR LLC | NUCOR CORPORATION | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-06-12 | 2007 | THE FACILITY PRODUCES STEEL COILS PRIMARILY FROM STEEL SCRAP USING THE ELECTRIC ARC FURNACE (EAF) PROCESS. | GALVANIZING LINE FURNACE | 13.31 | NATURAL GAS | 98.7 | MMBTU/H |  | Sulfur Dioxide (SO2) | N |  | 0.0006 | LB/MMBTU |  | 0.006 | LB/H
IA-0088 | ADM CORN PROCESSING - CEDAR RAPIDS | ARCHER DANIELS MIDLAND | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-06-29 | 2007 | CONSISTS OF THREE DISTINCT OPERATIONS: CORN WET MILL, CORN DRY MILL AND BOILERHOUSE | INDIRECT-FIRED DDGS DRYER | 13.31 | NATURAL GAS | 93.7 | MMBTU/H | PROJECT INCLUDES THE INSTALLATION OF EIGHT IDENTICAL DDGS DRYERS. PERMITS 07-A-546-P, 547, 548, 549, 550, 557, 558 AND 559. THE COMBUSTION CHAMBER AND THE FEED CHAMBER ARE SEPERATED BY A HEAT EXCHANGER. THE DRYERS CAN FIRE NATURAL GAS, BIOGAS FROM THE WWT | Sulfur Dioxide (SO2) | N |  | 6 | PPMVD | AVERAGE OF 3 TEST RUNS
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED BATCH ANNEALING FURNACE (535) | 13.31 | NATURAL GAS | 99 | MMBTU/H | THIS PROCESS IS COVERED UNDER 503-0095-X005. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Sulfur Dioxide (SO2) | N |  | 0.0006 | LB/MMBTU |  | 0.06 | LB/H
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED PASSIVE ANNEALING FURNACE (LO41) | 13.31 | NATURAL GAS | 27.2 | MMBTU/H | THIS PROCESS IS COVERED UNDER 503-0095-X013. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Sulfur Dioxide (SO2) | N |  | 0.0006 | LB/MMBTU |  | 0.016 | LB/H
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED BATCH ANNEALING FURNACES (LA63, LA64) | 13.31 | NATURAL GAS | 33.4 | MMBTU each | THIS PROCESS IS COVERED UNDER 503-0095-X014. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Sulfur Dioxide (SO2) | N |  | 0.0006 | LB/MMBTU |  | 0.02 | LB/H
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | 3 NATURAL GAS-FIRED BOILERS WITH ULNB & EGR (537-539) | 13.31 | NATURAL GAS | 64.9 | MMBtu each | THIS PROCESS IS COVERED UNDER 503-0095-X026. | Sulfur Dioxide (SO2) | N |  | 0.0006 | LB/MMBTU |  | 0.04 | LB/H
CA-0919 | COCA COLA | COCA COLA | CA | SOUTH COAST AQMD, CA | 1999-11-23 | 1999 |  | BOILER, FIRE TUBE | 13.31 | NATURAL GAS | 31.5 | MMBTU/H | ARB RECORD # A310-947-00 SCOTCH MARINE CUSTOM FIRE-TUBE BOILER USED TO PROVIDE STEAM FOR SANITATION. BACT LIMITS ARE APPLIED TO NOX AND CO LEVELS. NO BACT LIMITS WERE APPLIED TO PM, ROG, AND SOX. DEFAULT EMISSION FACTORS ARE THE BASIS OF THE PM, ROG AND S | Sulfur Oxides (SOx) | N | NO BACT LIMITS WERE APPLIED TO SOX. DEFAULT EMISSION FACTORS ARE THE BASIS OF THE SOX LEVEL LISTED HERE. | 0.0008 | LB/MMBTU |  |  |  |  | 0.0008 | LB/MMBTU
IN-0090 | NUCOR STEEL | NUCOR STEEL | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-01-19 | 2001 |  | TUNDISH PREHEATERS (2) | 13.31 |  | 6 | MMBTU/H | THROUGHPUT FOR EACH | Sulfur Oxides (SOx) | P | PERMIT LIMITATION IS USE OF NATURAL GAS.
OK-0074 | KIAMICHI ENERGY FACILITY | KIOWA POWER PARTNERS LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-05-01 | 2001 | ENERGY PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 27.5 | MMBTU/H |  | Sulfur Oxides (SOx) | P | USE OF NATURAL GAS WITH LOW SULFUR CONTENT | 2 | GR/100 SCF | [6 empty] | NOT AVAILABLE
*PA-0210 | DART CONTAINER CORP OF PA | DART CONTAINER CORP OF PA | PA | PENNSYLVANIA DEP, BUR OF AIR QUAL CTRL | 2001-12-14 | 2001 | NEW BOILERS ARE SUBJECT TO 40 CFR, PART 60, SUBPART DC AND BAT AND 25 PA CODE , CHAPTER 123. | BOILER, (2) | 13.31 | NATURAL GAS | 33.5 | MMBTU/H | CLEAVER BROOKS BOILERS. Boilers subject to NSPS/BAT/SIP | Sulfur Oxides (SOx) | P | LOW SULFUR FUEL | 4 | LB/MMBTU |  |  |  |  | 4 | LB/MMBTU
NV-0044 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S ENTERTAINMENT | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2007-01-04 | 2007 | THE FACILITY IS A NEW MAJOR STATIONARY SOURCE FOR NITROGEN OXIDES AS A RESULT OF CONSOLIDATING SIX LARGE HOTEL/CASINO RESORTS, WHICH ARE HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. | COMMERCIAL/INSTITUTIONAL-SIZE BOILERS | 13.31 | NATURAL GAS | 35.4 | MMBTU/H | THE BACT DETERMINATIONS REPORTED HERIN ARE SPECIFICALLY FOR THE TWO HURST BOILERS INSTALLED AT CAESAR'S PALACE. EACH OF THEM HAS A RATED HEAT INPUT OF 35.4 MMBTU/HR. THE PERMITTING ACTION ALSO APPROVED THE INSTALLATION OF A NUMBER OF SMALL BOILERS, ALL OF | Sulfur Oxides (SOx) | P | USE OF NATURAL GAS AS THE ONLY FUEL | 0.001 | LB/MMBTU |  | 0.04 | LB/H |  | 0.001 | LB/MMBTU |  | THE DATA PERTAIN TO EITHER ONE OF THE HURST BOILERS, WHICH RATED HEAT INPUT IS 35.4 MMBTU/H.
WI-0227 | PORT WASHINGTON GENERATING STATION | WE ENERGIES (WEPCO) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-13 | 2004 | ELECTRIC GENERATION | NATURAL GAS FIRED AUXILLIARY BOILER | 13.31 | NATURAL GAS | 97.1 | MMBTU/H |  | Sulfur Trioxide | P | NATURAL GAS FUEL | 0.09 | LB/H | SULFURIC ACID |  |  |  | 0.0009 | LB/MMBTU | CALCULATED | (LISTED AS SULFURIC ACID EMISSIONS)
OK-0050 | ONETA GENERATING STA | CALPINE CORP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2000-01-21 | 2000 | ELECTRIC GENERATION PLANT | DUCT BURNERS (4) | 13.31 | NATURAL GAS | 328 | MMBTU/H | The emission limits indicted are for the duct burners only. Emission limits for the turbines associated with these duct burners are provided under the process Combustion Turbines | Sulfuric Acid (mist, vapors, etc) | P | LOW SULFUR FUEL | 0.15 | E-3 LB/MMBTU | SEE POLLUTANT NOTES | [6 empty] | REGULATED POLLUTANT IS SULFURIC ACID MIST. EMISSION LIMIT IS 0.00015 LB/MMBTU
MN-0054 | MANKATO ENERGY CENTER |  | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2003-12-04 | 2003 | COMBINED CYCLE GAS TURBINE ELECTRIC POWER PLANT. TWO IDENTICAL GE FRAME F7A GAS TURBINES EACH WITH HRSG W/DUCT BURNERS FEEDING STEAM TO COMMON STEAM TURBINES. PRIMARY FUEL IS NG, NO. 2 VERY LOW SULFUR DISTILLATE OIL FOR BACKUP. ALSO, AUX. BOILER, DIESEL E | BOILER, COMMERCIAL | 13.31 | NATURAL GAS | 70 | MMBTU/H | NATURAL GAS ONLY | Sulfuric Acid (mist, vapors, etc) | P | LOW SULFUR FUEL | 0.8 | GR/100 SCF
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | B63, S63; B64, S64 - NATURAL GAS STATION HEATER 1 AND 2 | 13.31 | NATURAL GAS | 0.75 | MMBTU/H | EMISSION LIMITS ARE THOSE FOR EACH UNIT. | Sulfuric Acid (mist, vapors, etc) | P | NATURAL GAS | 0.0001 | LB/H | SULFURIC ACID MIST | [6 empty] | (LIMIT IS FOR EACH UNIT)
NJ-0045 | MERCK - RAHWAY PLANT | MERCK | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-01-14 | 1997 | CHEMICAL MANUFACTURING | BOILERS - NAT GAS (3) | 13.31 | NATURAL GAS | 99.5 | MMBTU/H |  | Total Suspended Particulates | N |  | 0.33 | LB/H |  | 0.0033 | LB/MMBTU |  | 0.0033 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HIGH PRESSURE BOILER #2-R2 | 13.31 | FUEL OIL | 0.3 | MMBTU/H | PERMIT NO: 97-A-416 FUEL OIL < 10,674,202 GALLONS/Y PER WHOLE FACILITY SULFUR CONTENT OF FUEL OIL < 0.05 % BY WEIGHT | Total Suspended Particulates | P | LOW NOX/FGR | 0.18 | LB/H |  | 0.8 | T/YR |  | 0.6 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #3 B3 | 13.31 | NATURAL GAS | 2.3 | MMBTU/HR | BOILER BURNS NATURAL GAS OR FUEL OIL. PERMIT NO: 97-A-408 20% OPACITY PER NSPS SUBPART DC SO2 SET AT 9.46 TPY TO STAY UNDER PSD SIGNIFICANCE | Total Suspended Particulates | P | LOW NOX BURNER, FLUE GAS RECIRC. | 1.39 | LB/H |  | 6.07 | T/YR |  | 0.6 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #2 B2 | 13.31 | NATURAL GAS | 2.3 | MMBTU/H | 20% OPACITY BY NSPS SUBPART DC SO2 - 9.46 TPY TO STAY UNDER PSD SIGNIFICANCE | Total Suspended Particulates | P | LOW NOX BURNER, FLUE GAS RECIRC | 1.39 | LB/H |  | 6.07 | T/YR |  | 0.6 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #1 | 13.31 | NATURAL GAS | 2.3 | MMBTU/H | FUEL IS NATURAL GAS AND FUEL OIL ONLY. PERMIT NUMBER: 97-A-377. 20 % OPACITY NSPS SUBPART BC SO2 - 9.46 TPY, SET TO STAY UNDER PSD SIGNIFICANCE LEVELS | Total Suspended Particulates | P | LOW NOX BURNER, FLUE GAS RECIRCULATION | 1.39 | LB/H |  | 6.07 | T/YR |  | 0.6 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HYDROGEN PLANT BURNER R9 | 13.31 |  |  |  | PERMIT NUMBER: 97-A-391 20% OPACITY - 1A 23.3(2)D. THIS PROCESS GENERATES HYDROGEN FROM NATURAL GAS. THE HYDROGEN IS USED FOR THE HYDROGENATION OF THE SOYBEAN OIL. | Total Suspended Particulates | N |  | 0.21 | LB/H |  | 0.9 | T/YR |  | 0.014 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HIGH PRESSURE BOILER #1 | 13.31 | NATURAL GAS | 0.3 | MMBTU/H | FUELS ARE NATURAL GAS AND #2FUEL OIL. PERMIT NUMBER 97-A-390 20% OPACITY BY NSPS SUBPART DC SO2 LIMIT 1.26 TPY TO STAY UNDER PSD SIGNIFICANCE | Total Suspended Particulates | N |  | 0.18 | LB/H |  | 0.8 | T/YR |  | 0.6 | LB/MMBTU
NJ-0062 | CONSOLIDATE EDISON DEVELOPMENT (CED) | CONSOLIDATED EDISON DVPMT.- LAKEWOOD GEN. FACILITY | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2002-10-22 | 2002 | POWER GENERATION | FUEL GAS HEATERS (3 UNITS) | 13.31 | NATURAL GAS | 4.62 | MMBTU/H | INSTALLATION OF 3 NEW FUEL GAS HEATERS@ 4.62 MMBTU/HR EACH. FUEL: NATURAL GAS. | Total Suspended Particulates | N |  | 0.05 | LB/H |  | 0.011 | LB/MMBTU
KY-0068 | TOYOTA MOTOR MANUFACTURING, USA, INC | TOYOTA MOTOR MANUFACTURING, USA, INC | KY | KENTUCKY DEP, DIV FOR AIR QUALITY | 1997-05-29 | 1997 | MODIFICATION OF AN AUTOMOBILE ASSEMBLY PLANT (THIRD REVISION OF PERMIT) | BOILER (NATURAL GAS) | 13.31 | NATURAL GAS | 96 | MMBTU/H | A SEPARATELY LISTED PROCESS SHOWS EMISSION LIMITS WHEN FIRING FUEL OIL (BACKUP FUEL). WHEN FIRING NATURAL GAS, ANNUAL OPERATING HOURS SHALL NOT EXCEED 6132 H/YR. | Visible Emissions (VE) | N | N/A | 20 | % OPACITY |  |  |  |  | 20 | % OPACITY
AK-0036 | KUPARUK CENTRAL PRODUCTION FACILITY | ARCO ALASKA INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1998-02-13 | 1998 |  | PROCESS HEATER | 13.31 | NATURAL GAS | 8 | MMBTU/H | OTHER COMPLIANCE: FACILITY OPERATING REPORTS. PERMIT LIMITS NOX AND H2S IN FUEL (SO2, PM10 AND VE). CO AND VOC ARE NOT INCLUDED IN THIS PERMIT. | Visible Emissions (VE) | N |  | 20 | % OPACITY |  |  |  |  | 20 | % OPACITY
ND-0018 | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ARCHER DANIELS MIDLAND CO. - NORTHERN SUN VEG. OIL | ND | NORTH DAKOTA STATE DEPARTMENT OF HEALTH | 1998-07-09 | 1998 | VEGETABLE OIL PLANT | BOILER, NEBRASKA, NAT GAS | 13.31 | NATURAL GAS | 28 | MMBTU/H | See separate process for backup fuel (No. 2 oil) requirements. | Visible Emissions (VE) | N |  | 20 | % OPACITY |  |  |  |  | 20 | % OPACITY
WI-0161 | AARROW CAST | AARROW CAST | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 1998-10-01 | 1998 |  | CORE WASH OVEN, S07 | 13.3 | NATURAL GAS | 10 | MMBTU/H | Limit required for PM and VE only | Visible Emissions (VE) | P | BACT FOR THIS PROCESS IS COMBUSTION OF NATURAL GAS | 20 | % OPACITY |  |  |  |  | 20 | % OPACITY
GA-0080 | RAYONIER, INC.- SWAINSBORO | RAYONIER, INC. - SWAINSBORO | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 1998-11-05 | 1998 | LUMBER MILL | OIL HEATER OH-1 | 13.31 | NATURAL GAS | 75 | MMBTU/H | HOT OIL HEATER FIRES NATURAL GAS WITH THE CAPABILITY OF FIRING NO. 2 FUEL OIL. | Visible Emissions (VE) | N |  | 20 | % OPACITY | 6 MIN AV |  |  |  | 20 | % OPACITY | 6 MIN AV
OH-0245 | REPUBLIC TECHNOLOGIES INTERNATIONAL | REPUBLIC TECHNOLOGIES INTERNATIONAL/CANTON | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 1999-01-27 | 1999 | STEEL MILL. THIS PLANT IS PSD FOR PM, SO2, NOX, CO, AND VOC. THIS MODIFICATION IS A SIGNIFICANT INCREASE FOR NOX. | ECCENTRIC BOTTOM TAPPING LADLE PREHEATER FURNACE | 13.31 | NATURAL GAS | 14 | MMBTU/H |  | Visible Emissions (VE) | N |  | 5 | % OPACITY | 6 minute average |  |  |  | 5 | % OPACITY | 6 minute average
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | WASTE HEAT RECOVERY, UNIT 10 | 13.31 | NATURAL GAS | 52.8 | MMBTU/H | MAXIMUM OPERATION DURING COMMISSIONING PERIOD: 1848 H MAXIMUM OPERATION AFTER COMMISSIONING PERIOD: 1000 H UNDER NORMAL LONG-TERM OPERATIONS, THE WASTE HEAT RECOVERY SUPPLEMENTAL BURNER WILL NOT BE OPERATED. OPERATION OF THIS BURNER IS UNDER AN ALTERNATIV | Visible Emissions (VE) | N | NONE INDICATED. | 20 | % OPACITY | FOR > 3 MIN/ANY 1 HOUR |  |  |  | 20 | % OPACITY | FOR > 3 MIN/ANY 1 HOUR | BACT IS TO COMPLY WITH STATE STANDARD 18 AAC 50.055 FOR FUEL BURNING EQUIPMENT.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | GLYCOL REBOILER, UNIT 13 | 13.31 | NATURAL GAS | 5 | MMBTU/H | MAXIMUM OPERATION DURING COMMISSIONING PERIOD: 1848 H. MAXIMUM OPERATION AFTER COMMISSIONING PERIOD: 8760 H/YR. | Visible Emissions (VE) | N | NONE INDICATED. | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H |  |  |  | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H | BACT IS TO COMPLY WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | GLYCOL SKID HEATER (NATURAL GAS), UNIT NO. 14 | 13.31 | NATURAL GAS | 1.05 | MMBTU/H | SECOND FUEL FOR GLYCOL SKID HEATER IS DIESEL- LISTED SEPARATELY. MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. | Visible Emissions (VE) | N | NONE INDICATED. | [6 empty] | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 HOUR | BACT IS CONSIDERED COMPLIANCE WITH THE STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | SPACE HEATER, WAREHOUSE, UNIT NO. 15, 16 | 13.31 | NATURAL GAS | 0.5 | MMBTU/H | MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. | Visible Emissions (VE) | P | GOOD OPERATION PRACTICES. | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H |  |  |  | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H | BACT IS TO COMPLY WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | SPACE HEATER, WAREHOUSE, UNIT NO. 17 | 13.31 | NATURAL GAS | 0.63 | MMBTU/H | MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. | Visible Emissions (VE) | P | GOOD OPERATIONS PRACTICES. | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H |  |  |  | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | SPACE HEATER, WAREHOUSE, UNIT NO. 18 | 13.31 | NATURAL GAS | 1.06 | MMBTU/H | MAXIMUM OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 1848 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. | Visible Emissions (VE) | P | GOOD OPERATIONS PRACTICES. | [6 empty] | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | RIG BOILER (NATURAL GAS), UNIT 206, 207 | 13.31 | NATURAL GAS | 6.3 | MMBTU/H | PERMIT LISTS UNIT 206 AND 207 WITH NATURAL GAS AND DIESEL, LISTED SEPARATELY IN DATABASE. TYPICAL OPERATION: DURING PRE-SEALIFT PERIOD, 8760 H; DURING COMMISSIONING PERIOD, 924 H; AFTER COMMISSIONING PERIOD, 8760 H/YR. DURING PRE- SEALFIT PERIOD AND COMMI | Visible Emissions (VE) | P | GOOD OPERATIONS PRACTICES | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H |  |  |  | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATER (NATURAL GAS), UNIT 208, 209 | 13.31 | NATURAL GAS | 3.5 | MMBTU/H | UNITS 208 AND 209 ARE LISTED IN PERMIT AS BURNING BOTH NATURAL GAS AND DIESEL FUEL. THESE ARE LISTED SEPARATELY IN DATABASE. DURING PRE-SEALIFT PERIOD AND COMMISSIONING PERIOD, UNITS MAY BE OPERATED WITH NATURAL GAS OR DIESEL FOR THE SAME AMOUNT OF TIME. | Visible Emissions (VE) | P | GOOD OPERATIONS PRACTICES. | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H |  |  |  | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0038 | NORTHSTAR DEVELOPMENT PROJECT | BP EXPLORATION INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 1999-02-05 | 1999 | PERMIT TO ESTABLISH AN OIL AND GAS PROCESSING FACILITY, TRANSPORTABLE DRILL RIG, CAMP INFRASTRUCTURE, AND EMISSION SOURCES ASSOCIATED WITH DEVELOPMENT DRILLING, PIPELINE TIE-IN, ON-ISLAND CONSTRUCTION ACTIVITIES, AND CRUDE OIL PROCESSING. | HEATER (NATURAL GAS), UNIT 210 | 13.31 | NATURAL GAS | 4.2 | MMBTU/H | THE SOURCE INVENTORY TABLE IN THE PERMIT LISTED ONLY DIESEL, BUT GAVE OPERATIONAL HOURS TYPICAL FOR BOTH NAT GAS AND DIESEL (SIMILAR TO OTHER SOURCES). FOOTNOTE STATED THAT UNIT 210 BURNS NATURAL GAS AND DIESEL, THEREFORE IT WAS ASSUMED THAT NAT GAS WAS E | Visible Emissions (VE) | P | GOOD OPERATIONS PRACTICES. | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H |  |  |  | 20 | % OPACITY | FOR > 3 MIN IN ANY 1 H | BACT IS CONSIDERED COMPLIANCE WITH STATE STANDARD 18 AAC 50.055.
AK-0053 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFI | CRUDE HEATER, CF-H-31003A | 13.31 | FUEL GAS | 65.6 | MMBTU/H | PERMIT INFORMATION LISTS FUEL TYPE AS FUEL GAS" BUT TECHNICAL DOCUMENTS INDICATE THAT FUEL IS NATURAL GAS. SCC AND PROCESS CODES WERE CHOSEN FOR NATURAL GAS." | Visible Emissions (VE) | N | NONE INDICATED | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H |  |  |  | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H | BASIS OF DETERMINATION IS 18 AAC 50.055(A)(1)
AK-0053 | KENAI REFINERY | TESORO ALASKA COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-03-21 | 2000 | THIS PERMIT REVISES THE PERMIT TERMS AND CONDITIONS OF AIR QUALITY PERMIT TO OPERATE NO. 9323-AA008 AND RESCINDS CONSTRUCTION PERMIT NO. 9723-AC004. THIS PERMIT ALLOWS THE USE OF REFINERY GAS IN SPECIFIED HEATERS, AN INCREASE IN NATURAL GAS HYDROGEN SULFI | CRUDE HEATER, CF-H-31003B | 13.31 | FUEL GAS | 65.6 | MMBTU/H | PERMIT INFORMATION INDICATES FUEL TYPE IS FUEL GAS" BUT TECHNICAL INFORMATION INDICATES FUEL GAS IS NATURAL GAS. SCC AND PROCESS CODES WERE CHOSEN FOR NATURAL GAS. UNIT IS DESCRIBED AS BORN." | Visible Emissions (VE) | N | NONE INDICATED | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H |  |  |  | 20 | % OPACITY | FOR NO MORE THAN 3 MIN/H | BASIS OF DETERMINATION IS 18 AAC 50.055(A)(1)
AK-0045 | NORTH COOK INLET UNIT | PHILLIPS PETROLEUM COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-06-06 | 2000 | THIS PERMIT ALLOWS PHILLIPS TO INSTALL TWO SOLAR TAURUS 60 T-7300 TURBINES RATED AT 6740 HP AT ISO CONDITIONS. THE TURBINES ARE SUBJECT TO PSD REVIEW FOR NOX AND PM10. | GLYCOL HEATER NOS. 1, 2, AND 3 | 13.31 | NATURAL GAS | 8.36 | MMBTU/H | THREE PROCESS UNITS ARE INCLUDED IN THIS ENTRY. THE OWNER REQUESTED TO LIMIT THE SULFUR CONTENT OF GASEOUS AND LIQUID FUELS TO 200-PPM HYDROGEN SULFIDE AND 0.25% SULFUR BY WEIGHT TO AVOID A PSD PRE-CONSTRUCTION REVIEW OF EXISTING EQUIPMENT. THE OWNER WILL | Visible Emissions (VE) | N | NONE INDICATED | 20 | % OPACITY | EACH, EXCEPT FOR 3 MIN IN ANY 1 H |  |  |  | 20 | % OPACITY | EACH, EXCEPT FOR 3 MIN IN ANY 1 H | BASIS OF DETERMINATION- 18 AAC 50.055(A)(1)
AK-0045 | NORTH COOK INLET UNIT | PHILLIPS PETROLEUM COMPANY | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2000-06-06 | 2000 | THIS PERMIT ALLOWS PHILLIPS TO INSTALL TWO SOLAR TAURUS 60 T-7300 TURBINES RATED AT 6740 HP AT ISO CONDITIONS. THE TURBINES ARE SUBJECT TO PSD REVIEW FOR NOX AND PM10. | DRILLING BOILER NO. 1 | 13.31 | NATURAL GAS | 100 | HP | THE OWNER REQUESTED TO LIMIT THE SULFUR CONTENT OF GASEOUS AND LIQUID FUELS TO 200-PPM HYDROGEN SULFIDE AND 0.25% SULFUR BY WEIGHT AND LIMITED HOURS OF OPERATION TO 1080 PER 12 MO PERIOD TO AVOID A PSD PRE-CONSTRUCTION REVIEW OF EXISTING EQUIPMENT. | Visible Emissions (VE) | N | NONE INDICATED | 20 | % OPACITY | EXCEPT FOR 3 MIN IN ANY 1 H |  |  |  | 20 | % OPACITY | EXCEPT FOR 3 MIN IN ANY 1 H | DETERMINATION BASED ON 18 AAC 50.055(A)(1)
WI-0181 | CHARTER STEEL | CHARTER STEEL | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2000-08-02 | 2000 | STEEL MILL | SPACE HEATERS | 13.31 |  | 5 | MMBTU/H | SPACE HEATERS' THROUGHPUT IS NO MORE THAN 5 MMBTU/H EACH. | Visible Emissions (VE) | N |  | 20 | % OPACITY |  |  |  |  | 20 | % OPACITY
TX-0363 | SAINT-GOBAIN VETROTEX AMERICA | VETROTEX AMERICA | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-11-13 | 2000 | VETROTEX AMERICA (VETROTEX) OPERATES A FIBER GLASS MANUFACTURING PLANT. THE VETROTEX PLANT PRODUCES FIBERGLASS REINFORCEMENT PRODUCTS AND IS COMPRISED OF FIVE GLASS MANUFACTURING FURNACES AND ASSOCIATED EQUIPMENT. THESE REFINFORCEMENT PRODUCTS ARE USED IN | BOILER NO 3 | 13.31 | NAT GAS |  |  |  | Visible Emissions (VE) | N | NONE INDICATED | 5 | % OPACITY | 6 MIN AV |  |  |  | 5 | % OPACITY | 6 MIN AV
SC-0065 | BROAD RIVER INVESTORS - GAFFNEY | BROAD RIVER INVESTORS, LLC | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 2000-12-21 | 2000 | ELECTRIC GENERATION FACILITY | HOT WATER HEATERS, NAT. GAS (2) | 13.31 | NATURAL GAS | 11 | MMBTU/H (EACH) |  | Visible Emissions (VE) | P | GOOD COMBUSTION CONTROL, CLEAN BURNING FUELS | 20 | % OPACITY | METHOD 9 |  |  |  | 20 | % OPACITY |  | STATE REG
OH-0258 | PRO TEC COATING COMPANY | USS GALVANIZING, INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-02-15 | 2001 | STEEL FINISHING MILL: METAL COATING WITH 2 NON-INSIGNIFICANT ANNEALING FURNACES AND 4 BOILERS | BOILERS (4) | 13.31 | NATURAL GAS | 20.9 | MMBTU/H | This permit is a modification to only 2 of the 4 boilers at this facility. Permit limits the same for each of the boilers being modified. | Visible Emissions (VE) | N |  | 20 | % OPACITY | 6 min avg |  |  |  | 20 | % OPACITY | 6 min avg
OH-0255 | PSEG WATERFORD ENERGY LLC | PSEG WATERFORD ENERGY LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-03-29 | 2001 | THREE 170 MW NATURAL GAS-FIRED COMBUSTION TURBINES; STAGE I SIMPLE CYCLE TO STAGE II COMBINED CYCLE | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 85.2 | MMBTU/H |  | Visible Emissions (VE) | N |  | 20 | % OPACITY | 6 MINUTE AVERAGE |  |  |  | 20 | % OPACITY | 6 MINUTE AVERAGE
SC-0061 | COLUMBIA ENERGY LLC | COLUMBIA ENERGY LLC | SC | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL | 2001-04-09 | 2001 | ELECTRIC COGENERATION POWER PLANT SUPPLYING STEAM AND ENERGY, A EASTMAN CHEMICAL CO. | HOT WATER HEATERS (2) | 13.31 | NATURAL GAS | 11 | MMBTU/H | USED FOR PREHEATING THE NATURAL GAS PRIOR TO SUPPLY TO THE COMBUSTION TURBINES, SUBJECT TO SUBPART Dc - STANDARDS OF PERFORMANCE FOR SMALL INDUSTRIAL-COMMERCIAL-INSTITUTIONAL STEAM GENERATING UNITS | Visible Emissions (VE) | P | CLEAN FUEL | 20 | % OPACITY |  |  |  |  | 20 | % OPACITY
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-5302A AND H-5302B | 13.31 | NATURAL GAS | 35 | MMBTU/H EA | 35 MMBTU/H MAXIMUM RATE/CAPACITY EA, 30 MMBTU/H NOMINAL CAPACITY EA. | Visible Emissions (VE) | N |  | 20 | % OPACITY | 3 MIN/H |  |  |  | 20 | % OPACITY | 3 MIN/H
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-4510A AND H-4510B | 13.31 | NAT GAS | 14.4 | MMBTU/H EACH |  | Visible Emissions (VE) | N |  | 20 | % OPACITY | 3 MIN/H |  |  |  | 20 | % OPACITY | 3 MIN/H
AK-0047 | MILNE POINT PRODUCTION FACILITY | BP EXPLORATION (ALASKA) INC. | AK | ALASKA DEPT OF ENVIRONMENTAL CONS | 2001-07-13 | 2001 | NATURAL GAS, CRUDE OIL, AND WATER ARE EXTRACTED FROM THE SUBSURFACE OF WELL PADS. THIS MIXTURE OF FLUIDS IS TRANSPORTED BY PIPELINE TO THE CENTRAL FACILITY PAD (CFP) WHERE THE GAS, CRUDE, AND WATER ARE SEPARATED. SOME OF THE NATURAL GAS IS USED AS FUEL IN | HEATERS (2), H-5701A AND H-5701B | 13.31 | NAT GAS | 29 | MMBTU/H EACH | 29 MMBTU/H MAXIMUM RATE/CAPACITY EA, 22.7 MMBTU/H NOMINAL CAPACITY EA. HEATERS BURN BOTH NATURAL GAS AND DIESEL FUELS. OPERATING RESTRICTION OF NO MORE THAN 200 H DURING ANY 12 CONSECUTIVE MOS, COMBINED, WHILE FIRING FUEL OIL. OPERATING RESTRICTION OF COM | Visible Emissions (VE) | N |  | 20 | % OPACITY | 3 MIN/H |  |  |  | 20 | % OPACITY | 3 MIN/H
OH-0263 | FREMONT ENERGY CENTER, LLC | CALPINE CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-08-09 | 2001 | TWO 180 MW COMBINED CYCLE TURBINES (2 HRSGS),USING SELECTIVE CATALYTIC REDUCTION (SCR) AND OXIDATION CATALYST | AUXILIARY BOILER | 13.31 | NATURAL GAS | 80 | MMBTU/H | Auxiliary boiler, natural gas-fired, 80 mmBtu/hr | Visible Emissions (VE) | N |  | 10 | % OPACITY | as a 6 minute average |  |  |  | 10 | % OPACITY | as a 6 minute average
IN-0110 | COGENTRIX LAWRENCE CO., LLC | COGENTRIX LAWRENCE CO., LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-10-05 | 2001 | POWER PLANT | BOILER, AUXILIARY, NATURAL GAS | 13.31 | NATURAL GAS | 35 | MMBTU/H |  | Visible Emissions (VE) | P | CLEAN FUEL, GOOD COMBUSTION PRACTICES | 20 | % OPACITY |  |  |  |  | 20 | % OPACITY
OH-0265 | DRESDEN ENERGY LLC | Dresden Energy | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-10-16 | 2001 | TWO 171.7 MW NATURAL GAS AND FUEL OIL- FIRED COMBUSTION TURBINES, COMBINED CYCLE; 49 MMBTU/HR NATURAL GAS FIRED BOILER; 2,250,000 GALLON FIXED ROOF STORAGE TANK FOR #2 FUEL OIL. | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 49 | MMBTU/H | Boiler is restricted to 800 hour of operation per a rolling 12 months. | Visible Emissions (VE) | N |  | 20 | % OPACITY | as a six minute average |  |  |  | 20 | % OPACITY | as a six minute average | Boiler is restricted to 800 hours or operation per a rolling 12 months.
PR-0007 | COGENERATION PLANT (AES-PRCP) | AES PUERTO RICO | PR | PUERTO RICO ENV QUALITY BOARD, AIR PROGRAM | 2001-10-29 | 2001 | COGENERATION UNIT | LIMESTONE DRYER | 13.31 | PROPANE | 13 | MMBTU/H | LIMESTONE DRYER INCLUDES A CRUSHER. HEATED AIR BOTH CLASSIFIES THE GROUND LIMESTONE AND DRIES THE MATERIAL. UNIT IS LIMITED TO A 505 CAPACITY FACTOR CALCULATED BASED ON 4380 H/CALENDAR YR. COMBUSTION CONTROLS WILL BE USED TO MINIMIZE AIR EMISSIONS. | Visible Emissions (VE) | A | ESP AND BAGHOUSES | 20 | % OPACITY | 6 MIN AV | 27 | % OPACITY | 1 6 MIN SET/H | 20 | % OPACITY | 6 MIN AV
TX-0378 | LA PORTE POLYPROPYLENE PLANT | ATOFINA PETROCHEMICALS INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-11-05 | 2001 | ATOFINA PROPOSES TO INSTALL A 60 MMBTU/H PACKAGE BOILER TO PROVIDE NEEDED STEAM CAPACITY. THE BURNER WILL MEET ESAD LIMIT OF 0.015 LB NOX/MMBTU FOR HOUSTON/GALVESTON. UPON STARTUP OF EPN ES-206, THE 40 MMBTU/H TEMPORARY BOILER (EPN TEMPBOILER) SHALL BE RE | PACKAGE BOILER BO-4 | 13.31 | NAT GAS | 60 | MMBTU/H |  | Visible Emissions (VE) | N | NONE INDICATED | 5 | % OPACITY | 6 MIN AV |  |  |  | 5 | % OPACITY | 6 MIN AV
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | 2001 | SOYBEAN EXTRACTION PLANT | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. There is a separate process entry for this boiler when firing fuel oil. | Visible Emissions (VE) | N |  | 20 | % OPACITY | 6-minute average |  |  |  | 20 | % OPACITY | 6-minute average
MS-0058 | CHOCTAW GAS GENERATION, LLC | CHOCTAW GAS GENERATION, LLC | MS | MISSISSIPPI DEPT OF ENV QUALITY | 2001-12-13 | 2001 | POWER PLANT, 700 MW | HEATER, FUEL GAS | 13.31 | NATURAL GAS | 5.6 | MMBTU/H | Limited to 2160 hours per year | Visible Emissions (VE) | N |  | 40 | % OPACITY |  |  |  |  | 40 | % OPACITY
OH-0257 | JACKSON COUNTY POWER, LLC | JACKSON COUNTY POWER, LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-12-27 | 2001 | FOUR 305 MW NATURAL-GAS FIRED COMBUSTION TURBINES, COMBINED CYCLE, WITH DLN AND SCR | AUXILIARY BOILER | 13.31 | NATURAL GAS | 76 | MMBTU/H | Limited to 3000 hours of operation per rolling 12 month period. | Visible Emissions (VE) | N |  | 20 | % OPACITY | 6 minute average |  |  |  | 20 | % OPACITY | 6 minute average
IA-0058 | GREATER DES MOINES ENERGY CENTER | MIDAMERICAN ENERGY | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-04-10 | 2002 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 68 | MMBTU/H |  | Visible Emissions (VE) | N |  | 0 | % OPACITY |  |  |  |  | 0 | % OPACITY
OH-0264 | NORTON ENERGY STORAGE, LLC | NORTON ENERGY | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-05-23 | 2002 | NINE 300 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE WITH DLN AND SCR; TEN 11.45 MMBTU/H NATURAL GAS-FIRED FUEL SUPPLY HEATERS/BOILERS; SEVEN 12.84 MMBTU/H NATURAL GAS-FIRED RECUPERATOR PRE HEATERS/BOILERS | RECUPERATOR PRE-HEATERS (9) | 13.31 | NATURAL GAS | 12.84 | MMBTU/H | Each boiler is limited to 100 hour of operation per rolling 12 months. | Visible Emissions (VE) | N |  | 10 | % OPACITY | as a six minute average |  |  |  | 10 | % OPACITY | as a six minute average | Limits are for each boiler. Each boiler is retricted to 100 hours of operation.
OH-0264 | NORTON ENERGY STORAGE, LLC | NORTON ENERGY | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-05-23 | 2002 | NINE 300 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE WITH DLN AND SCR; TEN 11.45 MMBTU/H NATURAL GAS-FIRED FUEL SUPPLY HEATERS/BOILERS; SEVEN 12.84 MMBTU/H NATURAL GAS-FIRED RECUPERATOR PRE HEATERS/BOILERS | FUEL SUPPLY HEATERS (9) | 13.31 | NATURAL GAS | 11.45 | MMBTU/H | Each fuel supply heater is limited to a maximum annual cumulative fuel heat input of 47,630 mmBtu per rolling 12 months. | Visible Emissions (VE) | N |  | 10 | % OPACITY | as a six minute average |  |  |  | 10 | % OPACITY | as a six minute average | Limits are for each heater.
KY-0087 | QUEBECOR WORLD FRANKLIN | QUEBECOR WORLD FRANKLIN | KY | KENTUCKY DEP, DIV FOR AIR QUALITY | 2002-07-12 | 2002 | ROTOGRAVURE PRINTING PLANT | BOILER, NATURAL GAS, #4 | 13.31 | NATURAL GAS | 33.5 | MMBTU/H | Boiler is a Cleaver Brooks indirect heat exchanger, using natural gas as primary fuel and no. 2 fuel oil as standby fuel. | Visible Emissions (VE) | N |  | 20 | % OPACITY |  |  |  |  | 20 | % OPACITY |  | VE limited to 40% opacity when cleaning firebox or blowing soot, and for no more than 6 min/h
AL-0192 | HONDA MANUFACTURING OF ALABAMA, LLC | HONDA MANUFACTURING OF ALABAMA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2002-10-18 | 2002 | AUTOMOBILE MANUFACTURING PLANT | BOILERS, NATURAL GAS, (3) | 13.31 | NATURAL GAS | 30 | MMBTU/H | throughput for each boiler. BACT for CO, NOx, PM10, and VE | Visible Emissions (VE) | N |  | 10 | % OPACITY |  |  |  |  | 10 | % OPACITY
WI-0195 | SENA NIAGARA MILL | STORA ENSO NORTH AMERICA | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2002-10-18 | 2002 |  | PROCESS HEATER, PAPER MACHINE P51 | 13.31 | NATURAL GAS | 34.4 | MMBTU/H | Throughput is total for natural gas IR and flotation dryers. | Visible Emissions (VE) | P | NATURAL GAS AS FUEL, GOOD COMBUSTION PRACTICE. | 20 | % OPACITY |  |  |  |  | 20 | % OPACITY |  | State reg is regulatory basis.
GA-0101 | MURRAY ENERGY FACILITY | DUKE ENERGY MURRAY LLC | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2002-10-23 | 2002 | ELECTRIC GENERATING FACILITY | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 31.4 | MMBTU/H | HOURS OF OPERATION NOT TO EXCEED 6,000 H/YR. | Visible Emissions (VE) | P | GOOD COMBUSTION PRACTICE | 10 | % OPACITY |  |  |  |  | 10 | % OPACITY
IN-0116 | PSEG LAWRENCEBURG ENERGY CO., INC. | PSEG LAWRENCEBURG ENERGY CO., INC. | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2002-12-23 | 2002 | POWER PLANT | HEATER, STARTUP GAS, NATURAL GAS | 13.31 | NATURAL GAS | 2.4 | MMBTU/H | Startup gas heater. Natural gas usage shall not exceed 5.3 MMSCF/ 12 mo period rolled on monthly basis | Visible Emissions (VE) | N |  | 20 | % OPACITY | 6-min avg | 27 | % OPACITY | one 6-min period per hour | 20 | % OPACITY
WA-0291 | WALLULA POWER PLANT | WALLULA GENERATION, LLC | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2003-01-03 | 2003 | WALLULA GENERATION, LLC, PROPOSES TO CONSTRUCT AND OPERATE A 1,300 MW COMBINED CYCLE ELECTRIC POWER PLANT. THE PROJECT WILL CONSIST OF TWO INDEPENDENT POWER BLOCKS WITH CRITICAL BACK-UP SYSTEMS TO MAINTAIN OVERALL PLANT RELIABILITY AND AVAILABILITY. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 55.3 | MMBTU/H | Operational limit of 4,000 hr per year | Visible Emissions (VE) | N |  | 10 | % OPACITY | 6 min ave |  |  |  | 10 | % OPACITY
GA-0098 | RINCON POWER PLANT | GENPOWER RINCON LLC | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2003-03-24 | 2003 | ELECTRIC GENERATING FACILITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 83 | MMBTU/H | THE BOILER IS LIMITED TO 1,000 H/YR OF OPERATION. | Visible Emissions (VE) | N |  | 10 | % OPACITY |  |  |  |  | 10 | % OPACITY
OH-0276 | CHARTER STEEL | CHARTER MANUFACTURING CO., INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-04-14 | 2003 | NEW MELT SHOP AT EXISTING FACILITY, INCLUDES NEW: ELECTRIC ARC FURNACE; LADLE METALLURGY FURNACE; VACUUM OXYGEN DEGASSER (VOD); VOC BOILER; CONTINUOUS CASTING MACHINES; 3 SILOS; 6 LADLE PREHEATERS; CUT-OFF-TORCH; 3 TUNDISH PREHEATERS; PROCESS SPACE HEATER | BOILER FOR VACUUM OXYGEN DEGASSER VESSEL | 13.31 | NATURAL GAS | 25 | MMBTU/H | VACUUM OXYGEN DEGASSER VESSEL BOILER, WITH LOW NOX BURNER | Visible Emissions (VE) | N |  | 20 | % OPACITY | 6 M AV |  |  |  | 20 | % OPACITY | AS A 6-MINUTE AVERAGE | VE MAY EXCEED 20% OPACITY, AS A 6-MINUTE AV, FOR NOT MORE THAN 6 CONSECUTIVE MINUTES IN ANY 60 MINUTES, BUT SHALL NOT EXCEED 60% OPACITY AS A 6-MINUTE AV AT ANY TIME.
MS-0057 | SMEPA - SILVER CREEK GENERATING | SOUTH MISSISSIPPI ELECTRIC POWER ASSOC. | MS | MISSISSIPPI DEPT OF ENV QUALITY | 2003-05-29 | 2003 | POWER PLANT - SIMPLE CYCLE, NATURAL GAS | BOILERS, NATURAL GAS (3) | 13.31 | NATURAL GAS | 5.4 | MMBTU/H | natural gas fired heater | Visible Emissions (VE) | N |  | 40 | % OPACITY |  |  |  |  | 40 | % OPACITY
OH-0254 | DUKE ENERGY WASHINGTON COUNTY LLC | DUKE ENERGY NORTH AMERICA | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-08-14 | 2003 | TWO 170 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE | BOILER | 13.31 | NATURAL GAS | 30.6 | MMBTU/H | THE MAXIMUM ANNUAL FUEL HEAT INPUT SHALL NOT EXCEED 128,000 MMBTU/ROLLING 12-MONTHS | Visible Emissions (VE) | N |  | 20 | % OPACITY | 6 min avg |  |  |  | 20 | % OPACITY
AZ-0047 | WELLTON MOHAWK GENERATING STATION | DOME VALLEY ENERGY PARTNERS | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2004-12-01 | 2004 | COMBINED CYCLE GAS-FIRED ELECTRICITY GENERATING STATION | AUXILIARY BOILER | 13.31 | NATURAL GAS | 38 | MMBTU/H |  | Visible Emissions (VE) | N |  | 10 | % OPACITY | 6-MINUTE AVERAGE |  |  |  | 10 | % OPACITY
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | 2007 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NATURAL GAS | 13.31 | NATURAL GAS | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. WITH #2 OIL BACKUP TWO SET OF LIMITS, THIS ONE FOR NATURAL GAS | Visible Emissions (VE) | N |  | 5 | % OPACITY | AS A 6-MINUTE AVERAGE |  |  |  | 5 | % OPACITY | AS A 6-MINUTE AVERAGE | OPACITY AT ANY STACK FROM EITHER BOILER.
IA-0088 | ADM CORN PROCESSING - CEDAR RAPIDS | ARCHER DANIELS MIDLAND | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-06-29 | 2007 | CONSISTS OF THREE DISTINCT OPERATIONS: CORN WET MILL, CORN DRY MILL AND BOILERHOUSE | INDIRECT-FIRED DDGS DRYER | 13.31 | NATURAL GAS | 93.7 | MMBTU/H | PROJECT INCLUDES THE INSTALLATION OF EIGHT IDENTICAL DDGS DRYERS. PERMITS 07-A-546-P, 547, 548, 549, 550, 557, 558 AND 559. THE COMBUSTION CHAMBER AND THE FEED CHAMBER ARE SEPERATED BY A HEAT EXCHANGER. THE DRYERS CAN FIRE NATURAL GAS, BIOGAS FROM THE WWT | Visible Emissions (VE) | N |  | 0 | % | SIX-MINUTE AVERAGE
NJ-0045 | MERCK - RAHWAY PLANT | MERCK | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1997-01-14 | 1997 | CHEMICAL MANUFACTURING | BOILERS - NAT GAS (3) | 13.31 | NATURAL GAS | 99.5 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N | NONE | 0.33 | LB/H |  | 0.0033 | LB/MMBTU |  | 0.0033 | LB/MMBTU |  | ADDITIONAL VOC LIMIT IS 50 PPMVD @7% O2.
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 8 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 50 | MMBTU/H | THE NUMBER 8 PAPER MACHINE CONSISTS OF THREE SOURCES: THE NATURAL GAS FIRED BURNERS, THE PAPER MACHINE, AND THE DUST SYSTEM. STACK TESTING FOR CO AND NOX. | Volatile Organic Compounds (VOC) | N |  | 0.0192 | LB/MMBTU |  | 0 |  |  | 0.0192 | LB/MMBTU
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 5 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 21 | MMBTU/H | THE BURNERS FOR THE NUMBER 5 PAPER MACHINE HAVE BEEN UPGRADED. | Volatile Organic Compounds (VOC) | N |  | 0.0564 | LB/MMBTU |  | 0 |  |  | 0.0564 | LB/MMBTU
AR-0020 | GEORGIA-PACIFIC CORPORATION | GEORGIA-PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 1997-02-28 | 1997 |  | BURNERS, NUMBER 6 PAPER MACHINE, GAS FIRED | 13.31 | NATURAL GAS | 58.4 | MMBTU/H | THE BURNERS FOR THE NUMBER 6 PAPER MACHINE HAVE BEEN UPGRADED. | Volatile Organic Compounds (VOC) | N |  | 0.0192 | LB/MMBTU |  | 0 |  |  | 0.0192 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #3 B3 | 13.31 | NATURAL GAS | 2.3 | MMBTU/HR | BOILER BURNS NATURAL GAS OR FUEL OIL. PERMIT NO: 97-A-408 20% OPACITY PER NSPS SUBPART DC SO2 SET AT 9.46 TPY TO STAY UNDER PSD SIGNIFICANCE | Volatile Organic Compounds (VOC) | P | LOW NOX BURNER FLUE GAS RECIRCULATION | 2.37 | LB/H |  | 4.11 | T/YR |  | 1 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #2 B2 | 13.31 | NATURAL GAS | 2.3 | MMBTU/H | 20% OPACITY BY NSPS SUBPART DC SO2 - 9.46 TPY TO STAY UNDER PSD SIGNIFICANCE | Volatile Organic Compounds (VOC) | P | LOW NOX BURNER, FLUE GAS RECIRC. ADDITIONAL EMISSION LIMIT: 70 PPM | 2.37 | LB/H |  | 4.11 | T/YR |  | 1 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | BOILER #1 | 13.31 | NATURAL GAS | 2.3 | MMBTU/H | FUEL IS NATURAL GAS AND FUEL OIL ONLY. PERMIT NUMBER: 97-A-377. 20 % OPACITY NSPS SUBPART BC SO2 - 9.46 TPY, SET TO STAY UNDER PSD SIGNIFICANCE LEVELS | Volatile Organic Compounds (VOC) | P | LOW NOX BURNER, FLUE GAS RECIRC. | 2.37 | LB/H |  | 411 | T/YR |  | 1 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HYDROGEN PLANT BURNER R9 | 13.31 |  |  |  | PERMIT NUMBER: 97-A-391 20% OPACITY - 1A 23.3(2)D. THIS PROCESS GENERATES HYDROGEN FROM NATURAL GAS. THE HYDROGEN IS USED FOR THE HYDROGENATION OF THE SOYBEAN OIL. | Volatile Organic Compounds (VOC) | N |  | 0.025 | LB/H |  | 0.11 | T/YR |  | 0.002 | LB/MMBTU
IA-0054 | BUNGE CORPORATION | BUNGE CORPORATION | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 1997-05-20 | 1997 | SOYBEAN PROCESSING | HIGH PRESSURE BOILER #1 | 13.31 | NATURAL GAS | 0.3 | MMBTU/H | FUELS ARE NATURAL GAS AND #2FUEL OIL. PERMIT NUMBER 97-A-390 20% OPACITY BY NSPS SUBPART DC SO2 LIMIT 1.26 TPY TO STAY UNDER PSD SIGNIFICANCE | Volatile Organic Compounds (VOC) | N |  | 0.25 | LB/H |  | 1.1 | T/YR |  | 0.8 | LB/MMBTU
WI-0188 | GOLDEN BOOKS PUBLISHING COMPANY INC. | GOLDEN BOOKS PUBLISHING COMPANY INC. | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 1997-06-24 | 1997 | PRINTING FACILITY | SPACE HEAT & COMBUSTION SOURCES, (P01 S01) | 13.31 | NATURAL GAS | 93 | MMBTU/H | SECOND FUEL: PROPANE | Volatile Organic Compounds (VOC) | N | REGULATORY BASIS: STATE REGULATION. | 0.49 | LB/H |  |  |  |  | 0.005 | LB/MMBTU
TX-0300 | SALT CREEK GAS PLANT | MOBIL EXPLORATION & PRODUCING US INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 1998-10-13 | 1998 | MOBIL EXPLORATION & PRODUCING US INC HAS REQUESTED AN AMENDMENT TO PERMIT NO 20660 AND A MODIFICATION TO PSD-TX-795 TO (1) INCREASE THE CO AND VOC ALLOWABLES ON THEIR COOPER-BESSEMER GMVH-12C2 ENGINES TO ALLOW THEM TO BETTER CONTROL NOX TO THE 2 G/HP-H LE | HOT OIL HEATER, EPN 26 | 13.31 | NAT GAS | 32.2 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 2.8 | LB/MMSCF |  | 0.03 | LB/H |  |  |  |  | VOC ADDITIONAL EMISSION LIMITS: 0.13 T/YR
NJ-0042 | ROCHE VITAMINS | ROCHE VITAMINS, INC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 1999-02-05 | 1999 | COGENERATION | BOILER 1 (NATURAL GAS) | 13.31 | NATURAL GAS | 84.4 | MMBTU/H | MFR. IS COMBUSTION ENGINEERING. ONLY NATURAL GAS, A MIXTURE OF NO. 2 OIL AND LASALOCID OIL, AND NO. 2 OIL SHALL BE FIRED IN BOILER 1. TOTAL OPERATING HOURS FOR BURNING NO. 2 OIL IN EACH BOILER SHALL NOT EXCEED 500 HOURS ON ANY CALENDAR YEAR. AFTER APRIL 3 | Volatile Organic Compounds (VOC) | N | NONE LISTED | 0.2 | LB/H |  | 4.4 | PPMVD @ 7% O2 |  | 0.002 | LB/MMBTU
MA-0029 | SITHE MYSTIC DEVELOPMENT LLC | SITHE MYSTIC DEVELOPMENT LLC | MA | MASSACHUSETTS DIV OF AIR QUAL CONTROL | 1999-09-29 | 1999 | COMBINED CYCLE ELECTRIC GENERATING FACILITY | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 96 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | EMISSION OFFSET | 0.8 | LB/H |  |  |  |  | 0.08 | LB/MMBTU
OK-0051 | GREEN COUNTRY ENERGY PROJECT | COGENTRIX ENERGY INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 1999-10-01 | 1999 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS |  |  |  | Volatile Organic Compounds (VOC) | P | BOILER DESIGN AND GOOD OPERATING PRACTICES | 0.0054 | LB/MMBTU |  |  |  |  | 0.0054 | LB/MMBTU
CA-0923 | ARAMARK UNIFORM CLEANERS | ARAMARK UNIFORM CLEANERS | CA | SAN JOAQUIN VALLEY APCD - CENTRAL REGIONAL OFFICE, CA | 1999-10-04 | 1999 | FACILITY PROCESS SOLVENT-LADEN TOWELS AND UNIFORMS. ITEMS ARE COUNTED ON A TABLE SERVED BY AN UNCONTROLLED EXHAUST HOOD AND PLACED INTO INDUSTRIAL WASHERS AND DRYERS (CHALLENGER CPG4-3S3L BURNERS, 2.75 MMBTU/H) | DRYER, NATURAL GAS | 13.31 | NATURAL GAS | 2.75 | MMBTU/H | ARB RECORD # A340-951-00. DRYER PROCESSES SOLVENT LADEN TOWELS, < 950 LB TOWELS/DAY. BACT NOT TRIGGERED FOR PM10 OR SOX | Volatile Organic Compounds (VOC) | N |  | 0.0055 | LB/MMBTU |  |  |  |  | 0.0055 | LB/MMBTU
CA-0919 | COCA COLA | COCA COLA | CA | SOUTH COAST AQMD, CA | 1999-11-23 | 1999 |  | BOILER, FIRE TUBE | 13.31 | NATURAL GAS | 31.5 | MMBTU/H | ARB RECORD # A310-947-00 SCOTCH MARINE CUSTOM FIRE-TUBE BOILER USED TO PROVIDE STEAM FOR SANITATION. BACT LIMITS ARE APPLIED TO NOX AND CO LEVELS. NO BACT LIMITS WERE APPLIED TO PM, ROG, AND SOX. DEFAULT EMISSION FACTORS ARE THE BASIS OF THE PM, ROG AND S | Volatile Organic Compounds (VOC) | N | NO BACT LIMITS WERE APPLIED TO ROG. DEFAULT EMISSION FACTORS ARE THE BASIS OF THE ROG LEVEL LISTED HERE. | 0.0067 | LB/MMBTU | REACTIVE ORGANIC GASES |  |  |  | 0.0067 | LB/MMBTU | REACTIVE ORGANIC GASES | LIMITS ARE FOR REACTIVE ORGANIC GASES.
OK-0041 | MCCLAIN ENERGY FACILITY | NRG MCCLAIN LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2000-01-19 | 2000 | POWER PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 22 | MMBTU/H | See RBLC ID OK-0071 for updated emission limits based on increased hours of operatuion. | Volatile Organic Compounds (VOC) | P | COMBUSTION CONTROLS | 0.2 | T/YR | [6 empty] | Not Available
OK-0050 | ONETA GENERATING STA | CALPINE CORP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2000-01-21 | 2000 | ELECTRIC GENERATION PLANT | DUCT BURNERS (4) | 13.31 | NATURAL GAS | 328 | MMBTU/H | The emission limits indicted are for the duct burners only. Emission limits for the turbines associated with these duct burners are provided under the process Combustion Turbines | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION | 0.02 | LB/MMBTU |  |  |  |  | 0.02 | LB/MMBTU
TX-0309 | FORMOSA PLASTICS TEXAS | FORMOSA PLASTICS CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-02-10 | 2000 | THIS PERMIT AUTHORIZES THE OPERATION OF THE FORMOSA ETHYLENE GLYCOL PLANT & A PRODUCTION INCREASE, EQUIPMENT UPGRADES & CHANGES, ADDITIONAL FUGITIVE EMISSIONS, & AN ADDITIONAL COOLING TOWER CELL. THE APPLICANT WISHES TO CONSOLIDATE ALL FUGITIVE EMISSION P | WASTE HEAT BOILER, 70Z401 | 13.31 | NAT GAS |  |  | SHALL BE MAINTAINED AT A MINIMUM COMBUSTION CHAMBER TEMP OF 1450 F. | Volatile Organic Compounds (VOC) | A | THE WASTE HEAT BOILER IS A CONTROL FOR VOC | 1.2 | LB/H |  | 3.84 | T/YR
TX-0309 | FORMOSA PLASTICS TEXAS | FORMOSA PLASTICS CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-02-10 | 2000 | THIS PERMIT AUTHORIZES THE OPERATION OF THE FORMOSA ETHYLENE GLYCOL PLANT & A PRODUCTION INCREASE, EQUIPMENT UPGRADES & CHANGES, ADDITIONAL FUGITIVE EMISSIONS, & AN ADDITIONAL COOLING TOWER CELL. THE APPLICANT WISHES TO CONSOLIDATE ALL FUGITIVE EMISSION P | WASTE HEAT BOILER, 70Z401 | 13.31 | NAT GAS |  |  | SHALL BE MAINTAINED AT A MINIMUM COMBUSTION CHAMBER TEMP OF 1450 F. | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 5.47 | LB/H |  | 14.32 | T/YR |  |  |  |  | POLLUTANT IS A MIXTURE OF PROPYLENE AND PROPANE.
TX-0274 | SOLAR GAS TURBINE COGEN. | AMERIPOL SYNPOL CORP. | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-04-03 | 2000 | AMERIPOL PROPOSES TO CONSTRUCT A COGENERATION FACILITY, TURBINE WITH DUCT BURNER FIRED HEAT RECOVERY STEAM GENERATOR (HRSG) AND AN AUXILLIARY BOILER. THE TURBINE IS A 4.4 MW (DESIGN CAPACITY AT ISO CONDITIONS, BASE LOAD) NATURAL GAS FIRED SOLAR TURBINE, M | AUXILIARY BOILER | 13.31 | NATURAL GAS | 54.01 | MMBTU/H | WILL BE OPERATED 175 H/YR ONLY DURING PERIODS OF CTG DOWNTIME. | Volatile Organic Compounds (VOC) | N | NONE INDICATED. | 0.29 | LB/H |  | 0.03 | T/YR
MI-0301 | ALCHEM ALUMINUM | ALCHEM ALUMINUM, INC. | MI | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | 2000-05-02 | 2000 | SECONDARY ALUMINUM PRODUCTION. | FLUES | 13.31 | NATURAL GAS | 42000 | LB/H | HOLDING CAPACITIES ARE 170,000 AND 250,000 LBS. BURNER CAPACITIES ARE 34,000,000 AND 48,000,000 BTU/HR. | Volatile Organic Compounds (VOC) | N | COMBUSTION FLUES DO NOT HAVE ADD-ON CONTROLS. | 0.69 | LB/H |  | 3.04 | T/YR |  |  | LB/MMBTU
MA-0027 | CABOT POWER CORPORATION | CABOT POWER CORPORATION | MA | MASSACHUSETTS DIV OF AIR QUAL CONTROL | 2000-05-07 | 2000 | COMBINED CYCLE ELECTRIC GENERATING FACILITY. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 26.6 | MMBTU/H | PROCESS RESTRICTED TO 500 HOURS PER YEAR (12,881,000 SCF NATURAL GAS) | Volatile Organic Compounds (VOC) | P | COMBUSTION CONTROLS, OXIDATION CATALYST. | 0.4 | LB/H |  |  |  |  | 0.016 | LB/MMBTU
WI-0181 | CHARTER STEEL | CHARTER STEEL | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2000-08-02 | 2000 | STEEL MILL | BOILER | 13.31 | NATURAL GAS | 10 | MMBTU/H | THIS BOILER IS SUBJECT TO NSPS | Volatile Organic Compounds (VOC) | P | BACT FOR VOC IS DETERMINED TO BE USE OF NATURAL GAS TO FUEL BOILER. NO EMISSION RATE LIMIT.
WI-0181 | CHARTER STEEL | CHARTER STEEL | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2000-08-02 | 2000 | STEEL MILL | SPACE HEATERS | 13.31 |  | 5 | MMBTU/H | SPACE HEATERS' THROUGHPUT IS NO MORE THAN 5 MMBTU/H EACH. | Volatile Organic Compounds (VOC) | P | BACT FOR VOC IS DETERMINED TO BE GOOD COMBUSTION CONTROL AND THE USE OF NATURAL GAS TO FUEL THE SPACE HEATERS AND SIMILAR COMBUSTION APPLIANCES. NO EMISSION RATE LIMIT.
TX-0363 | SAINT-GOBAIN VETROTEX AMERICA | VETROTEX AMERICA | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2000-11-13 | 2000 | VETROTEX AMERICA (VETROTEX) OPERATES A FIBER GLASS MANUFACTURING PLANT. THE VETROTEX PLANT PRODUCES FIBERGLASS REINFORCEMENT PRODUCTS AND IS COMPRISED OF FIVE GLASS MANUFACTURING FURNACES AND ASSOCIATED EQUIPMENT. THESE REFINFORCEMENT PRODUCTS ARE USED IN | BOILER NO 3 | 13.31 | NAT GAS |  |  |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 0.05 | LB/H |  | 0.2 | T/YR
AR-0040 | DUKE ENERGY HOT SPRINGS | DUKE ENERGY HOT SPRINGS | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2000-12-29 | 2000 | NATURAL GAS FIRED POWER PLANT | BOILERS, AUXILIARY 2 | 13.31 | NATURAL GAS | 44.1 | MMBTU/H | THROUGHPUT FOR EACH | Volatile Organic Compounds (VOC) | P | CLEAN FUELS, PROPER COMBUSTION. LB/HR LIMIT FOR EACH BOILER. | 0.016 | LB/MMBTU |  | 0.8 | LB/H |  | 0.016 | LB/MMBTU
NM-0042 | DEMING ENERGY FACILITY | DUKE ENERGY LUNA | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2000-12-29 | 2000 | THIS FACILITY WILL GENERATE APPROXIMATELY 640 MW (NOMINAL). IT WILL BE A COMBINED CYCLE FACILITY CONSISTING OF 2 GENERAL ELECTRIC PG7241 (FA) COMBUSTION TURBINES, 2 DUCT BURNERS, AN AUXILIARY BOILER, AND A COOLING TOWER. THE NOX FROM THE COMBUSTION TURBIN | AUX-1 AUXILARY BOILER | 13.31 | NATURAL GAS | 44.1 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION DESIGN | 0.7 | LB/H |  |  |  |  | 0.016 | LB/MM BTU
AL-0168 | GENPOWER KELLEY LLC | GENPOWER KELLEY LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-01-12 | 2001 | ELECTRIC GENERATION | BOILER | 13.31 | NATURAL GAS | 83 | MMBTU/H | BOILER OPERATION LIMITED TO 1000 HR/YR | Volatile Organic Compounds (VOC) | P | EFFICIENT COMBUSTION | 0.006 | LB/MMBTU |  | 0.46 | LB/H |  | 0.006 | LB/MMBTU
AL-0169 | BLOUNT MEGAWATT FACILITY | BLOUNT COUNTY ENERGY LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-02-05 | 2001 | ELECTRIC GENERATING FACILITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 40 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.02 | LB/MMBTU |  | 0.8 | LB/H |  | 0.02 | LB/MMBTU
OH-0258 | PRO TEC COATING COMPANY | USS GALVANIZING, INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-02-15 | 2001 | STEEL FINISHING MILL: METAL COATING WITH 2 NON-INSIGNIFICANT ANNEALING FURNACES AND 4 BOILERS | BOILERS (4) | 13.31 | NATURAL GAS | 20.9 | MMBTU/H | This permit is a modification to only 2 of the 4 boilers at this facility. Permit limits the same for each of the boilers being modified. | Volatile Organic Compounds (VOC) | N |  | 0.11 | LB/H |  | 0.005 | LB/MMBTU |  | 0.005 | LB/MMBTU |  | Limit is for each boiler. Only 2 of the 4 boilers modified in this permit. Additional limit: 0.48 T/YR
OH-0255 | PSEG WATERFORD ENERGY LLC | PSEG WATERFORD ENERGY LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-03-29 | 2001 | THREE 170 MW NATURAL GAS-FIRED COMBUSTION TURBINES; STAGE I SIMPLE CYCLE TO STAGE II COMBINED CYCLE | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 85.2 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N |  | 0.35 | LB/H |  | 0.0041 | LB/MMBTU |  | 0.0041 | LB/MMBTU
OK-0074 | KIAMICHI ENERGY FACILITY | KIOWA POWER PARTNERS LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-05-01 | 2001 | ENERGY PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 27.5 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES AND DESIGN | 0.0055 | LB/MMBTU
IN-0086 | MIRANT SUGAR CREEK, LLC | MIRANT SUGAR CREEK, LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-05-09 | 2001 |  | AUXILARY BOILER, NATURAL GAS (2) | 13.31 | NATURAL GAS | 35 | MMBTU/H | AUXILARY BOILERS ARE LIMITED TO 5,000 H/YR OF OPERATION. THROUGH PUT IS FOR EACH BOILER. | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION. LB/H LIMIT IS FOR EACH BOILER. | 0.0054 | LB/MMBTU |  | 0.19 | LB/H |  | 0.0054 | LB/MMBTU
OK-0046 | THUNDERBIRD POWER PLT | THUNDERBIRD GENERATION LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-05-17 | 2001 | ELECTRICAL PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 20 | MMBTU/H | CO limits are not provided in permit. | Volatile Organic Compounds (VOC) | N |  | 0.005 | LB/MMBTU |  |  |  |  | 0.005 | LB/MMBTU
NV-0039 | CHUCK LENZIE GENERATING STATION | NEVADA POWER COMPANY | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2001-06-01 | 2001 | A NEW ELECTRIC POWER PLANT CONSISTING OF FOUR COMBUSTION TURBINE GENERATORS, FOUR HEAT RECOVERY STEAM GENERATORS EACH WITH DUCT FIRING, AND TWO STEAM TURBINE GENERATORS FOR A TOTAL NOMINAL OUTPUT OF 1170 MW. THE FACILITY IS LOCATED AT 11405 U.S. HIGHWAY 9 | AUXILIARY BOILERS | 13.31 | NATURAL GAS | 44.1 | MMBTU/H | THESE (TWO) BOILERS WILL EACH BE OPERATED A MAXIMUM OF 6,000 HOURS PER YEAR ACCORDING TO THE APPLICATION FOR ATC. | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION CONTROL | 0.8 | LB/H |  |  |  |  | 0.018 | LB/MMBTU |  | EMISSION LIMIT 1 APPLIES TO EACH AUXILIARY BOILER.
IN-0087 | DUKE ENERGY, VIGO LLC | DUKE ENERGY, VIGO LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-06-06 | 2001 |  | AUXILARY BOILER, NATURAL GAS (2) | 13.31 | NATURAL GAS | 46 | MMBTU/H | NATURAL GAS FIRED BOILERS (THROUGHPUT FOR EACH) LIMITED TO 500 H/YR OPERATION | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION. LIMIT IS FOR EACH BOILER. | 0.0054 | LB/MMBTU |  | 0.25 | LB/H |  | 0.0054 | LB/MMBTU
AL-0190 | GE PLASTICS | GE PLASTICS | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-07-13 | 2001 | SYNTHETIC ORGANIC CHEMICAL MANUFACTURER THAT PRODUCES POLYCARBONATE RESIN PELLETS | FURNACE, HOT OIL, 10 MMBTU/H | 13.31 | NATURAL GAS | 10 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.1 | LB/H |  | 0.01 | LB/MMBTU |  | 0.01 | LB/MMBTU
AL-0190 | GE PLASTICS | GE PLASTICS | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-07-13 | 2001 | SYNTHETIC ORGANIC CHEMICAL MANUFACTURER THAT PRODUCES POLYCARBONATE RESIN PELLETS | FURNACE, HOT OIL, 20 MMBTU/H | 13.31 | NATURAL GAS | 20 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.1 | LB/H |  | 0.005 | LB/MMBTU |  | 0.005 | LB/MMBTU
OH-0263 | FREMONT ENERGY CENTER, LLC | CALPINE CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-08-09 | 2001 | TWO 180 MW COMBINED CYCLE TURBINES (2 HRSGS),USING SELECTIVE CATALYTIC REDUCTION (SCR) AND OXIDATION CATALYST | AUXILIARY BOILER | 13.31 | NATURAL GAS | 80 | MMBTU/H | Auxiliary boiler, natural gas-fired, 80 mmBtu/hr | Volatile Organic Compounds (VOC) | N |  | 0.44 | LB/H |  | 1.9 | T/YR
OK-0044 | SMITH POCOLA ENERGY PROJECT | SMITH COGENERATION OK INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-16 | 2001 | ELEC. POWER GENERATION | AUXILIARY BOILERS, (2) | 13.31 | NATURAL GAS | 48 | MMBTU/H | THROUGHPUT FOR EACH | Volatile Organic Compounds (VOC) | P | COMBUSTION CONTROL | 0.52 | LB/H | combined | 2.27 | T/YR | combined | 0.0055 | LB/MMBTU
OK-0054 | QUAD GRAPHICS OKC FACILITY | QUAD GRAPHICS INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-08-21 | 2001 | PRINT SHOP | BOILERS | 13.31 | NATURAL GAS | 62.77 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION/MAINTENANCE | 4.38 | T/YR
MD-0033 | KELSON RIDGE | FREE STATE ELECTRIC, LLC | MD | MARYLAND, OTHER | 2001-09-27 | 2001 | FACILITY WAS LICENSED; PROJECT WAS THEN CANCELLED BY APPLICANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 40 | MMBTU/H | EMISSIONS LIMITS APPLY TO EACH BOILER | Volatile Organic Compounds (VOC) | B | EXCLUSIVE USE OF NATURAL GAS, ADVANCED DRY LOW-NOX BURNERS; GOOD COMBUSTION CONTROLS HEAT INPUT TO THE AUXILIARY BOILERS (2) SHALL BE LIMITED TO 210,240 MMBTU FOR ANY CONSECUTIVE 12-MONTH PERIOD |  |  | SEE NOTE | [6 empty] | HEAT INPUT TO THE AUXILIARY BOILERS (2) SHALL BE LIMITED TO 210,240 MMBTU FOR ANY CONSECUTIVE 12-MONTH PERIOD
AL-0179 | TENASKA TALLADEGA GENERATING STATION | TENASKA ALABAMA IV PARTNERS, LP | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-10-03 | 2001 | NATURAL GAS/DISTILLATE OIL FIRED COMBINED CYCLE ELECTRIC GENERATING FACILITY. | 30 MMBTU/HR AUXILIARY BOILER | 13.31 | NATURAL GAS | 30 | MMBTU/H | Operation limited to 1000 h/yr. | Volatile Organic Compounds (VOC) | P | EFFICIENT COMBUSTION | 0.004 | LB/MMBTU |  | 0.1 | LB/H |  | 0.004 | LB/MMBTU
IN-0110 | COGENTRIX LAWRENCE CO., LLC | COGENTRIX LAWRENCE CO., LLC | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-10-05 | 2001 | POWER PLANT | BOILER, AUXILIARY, NATURAL GAS | 13.31 | NATURAL GAS | 35 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | CLEAN FUEL, GOOD COMBUSTION PRACTICE | 0.011 | LB/MMBTU |  | 0.39 | LB/H
OH-0265 | DRESDEN ENERGY LLC | Dresden Energy | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-10-16 | 2001 | TWO 171.7 MW NATURAL GAS AND FUEL OIL- FIRED COMBUSTION TURBINES, COMBINED CYCLE; 49 MMBTU/HR NATURAL GAS FIRED BOILER; 2,250,000 GALLON FIXED ROOF STORAGE TANK FOR #2 FUEL OIL. | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 49 | MMBTU/H | Boiler is restricted to 800 hour of operation per a rolling 12 months. | Volatile Organic Compounds (VOC) | N |  | 0.29 | LB/H |  | 0.118 | T/YR |  | 0.006 | LB/MMBTU |  | Boiler is restricted to 800 hours or operation per a rolling 12 months.
OK-0043 | WEBERS FALLS ENERGY FACILITY | ENERGETIX | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2001-10-22 | 2001 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 30 | MMBTU/H | BOILER OPERATIONS LIMITED TO 3,000 HOURS/YEAR. | Volatile Organic Compounds (VOC) | N |  | 0.016 | LB/MMBTU |  |  |  |  | 0.016 | LB/MMBTU
AL-0181 | DUKE ENERGY AUTAUGA, LLC | DUKE ENERGY AUTAUGA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-10-23 | 2001 | COMBINED CYCLE ELECTRIC GENERATING PLANT. | 31.4 MMBTU/HR NATURAL GAS FIRED BOILER | 13.31 | NATURAL GAS | 31.4 | MMBTU/H | Operation limited to 2500 hrs/yr. | Volatile Organic Compounds (VOC) | P | EFFICIENT COMBUSTION. | 0.0104 | LB/MMBTU |  | 0.5 | LB/H
*WA-0292 | SATSOP COMBUSTION TURBINE PROJECT | GRAYS HARBOR ENERGY LLC | WA | WASHINGTON STATE DEPARTMENT OF ECOLOGY | 2001-10-23 | 2001 | GE F7 TURBINE BASED COMBINED CYCLE NATURAL GAS ONLY FUELED COMBUSTION TURBINE INCLUDES COOLING TOWER AND EMERGENCY ICE GENERATOR AND FIRE WATER ENGINES | AUXILIARY BOILER | 13.31 | NAT GAS | 29.3 | MMBTU/H | 29.3 MMBTU/H IS THE DESIGN HEAT INPUT RATE FOR THE BOILER, AS PROVIDED BY THE STATE CONTACT PERSON. | Volatile Organic Compounds (VOC) | N |  | 0.16 | LB/H | 1-H AV, CARBON EQUIVALENT | [5 empty] | NOT AVAILABLE | THE ORIGINAL PERMIT LIMITED VOC EMISSIONS TO 0.469 LB/HR.
*NJ-0036 | AES RED OAK LLC | AES RED OAK LLC | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2001-10-24 | 2001 | ELECTRICITY GENERATION | FUEL GAS HEATER | 13.31 | NATURAL GAS | 16 | MMBTU/H | FUEL GAS HEATER PRE-HEATS THE PIPELINE NATURAL GAS FUEL ENTERING THE COMBUSTION TURBINE UNITS AT 70 DEGREES F | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.11 | LB/H |  | 0.407 | T/YR
PR-0007 | COGENERATION PLANT (AES-PRCP) | AES PUERTO RICO | PR | PUERTO RICO ENV QUALITY BOARD, AIR PROGRAM | 2001-10-29 | 2001 | COGENERATION UNIT | LIMESTONE DRYER | 13.31 | PROPANE | 13 | MMBTU/H | LIMESTONE DRYER INCLUDES A CRUSHER. HEATED AIR BOTH CLASSIFIES THE GROUND LIMESTONE AND DRIES THE MATERIAL. UNIT IS LIMITED TO A 505 CAPACITY FACTOR CALCULATED BASED ON 4380 H/CALENDAR YR. COMBUSTION CONTROLS WILL BE USED TO MINIMIZE AIR EMISSIONS. | Volatile Organic Compounds (VOC) | P | COMBUSTION CONTROL | 0.01 | LB/MMBTU |  | 0.13 | LB/H
TX-0378 | LA PORTE POLYPROPYLENE PLANT | ATOFINA PETROCHEMICALS INC | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2001-11-05 | 2001 | ATOFINA PROPOSES TO INSTALL A 60 MMBTU/H PACKAGE BOILER TO PROVIDE NEEDED STEAM CAPACITY. THE BURNER WILL MEET ESAD LIMIT OF 0.015 LB NOX/MMBTU FOR HOUSTON/GALVESTON. UPON STARTUP OF EPN ES-206, THE 40 MMBTU/H TEMPORARY BOILER (EPN TEMPBOILER) SHALL BE RE | PACKAGE BOILER BO-4 | 13.31 | NAT GAS | 60 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 0.35 | LB/H |  | 1.53 | T/YR
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | 2001 | SOYBEAN EXTRACTION PLANT | BOILER, NATURAL GAS | 13.31 | NATURAL GAS | 91.2 | MMBTU/H | Restriction on the gallons of #2 oil that can be used: 1,787,000 gallons per rolling 12-months. There is a separate process entry for this boiler when firing fuel oil. | Volatile Organic Compounds (VOC) | N |  | 0.65 | LB/H |  | 5.17 | T/YR |  |  |  |  | Using Manufacturer's guaranteed emission rate: 8 lbs VOC/1,000,000 lbs air on natural gas.
*OH-0251 | CENTRAL SOYA COMPANY INC. | CENTRAL SOYA COMPANY INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-11-29 | 2001 | SOYBEAN EXTRACTION PLANT | DRYER, SOY PROTEIN CONCENTRATE - COMBUSTION | 13.31 | NATURAL GAS | 37 | MMBTU/H | Baghouse with 100% capture. Process is in 2 parts - dryer - combustion, and dryer - pm. | Volatile Organic Compounds (VOC) | N |  | 0.1 | LB/H |  | 0.44 | T/YR |  |  |  |  | Emissions are from natural gas combustion, using 0.003 lb VOC/mmBtu
IN-0095 | ALLEGHENY ENERGY SUPPLY CO. LLC | ALLEGHENY ENERGY SUPPLY CO. LLC (ACADIA BAY ENERGY | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2001-12-07 | 2001 | ELECTRIC POWER GENERATING STATION | AUXILLIARY BOILER | 13.31 | NATURAL GAS | 21 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.0054 | LB/MMBTU |  |  |  |  | 0.0054 | LB/MMBTU
AL-0180 | DUKE ENERGY DALE, LLC | DUKE ENERGY DALE, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2001-12-11 | 2001 | NATURAL GAS FIRED COMBINED CYCLE ELECTRIC GENERATING PLANT. | 35 MMBTU/HR NAT. GAS FIRED AUXILIARY BOILER | 13.31 | NATURAL GAS | 35 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION | 0.014 | LB/MMBTU |  | 0.5 | LB/H
AR-0049 | GEORGIA PACIFIC - CROSSETT PAPER | GEORGIA PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-12-14 | 2001 | KRAFT PAPER MILL. | BURNER EXHAUST A, TAD (SN-85A) | 13.31 | NATURAL GAS | 90 | MMBTU/H | Source has not been installed yet. BACT for PM, VOC, CO and NOx. Initial & 3 yr periodic testing required for CO & NOx. | Volatile Organic Compounds (VOC) | N |  | 0.045 | LB/MMBTU | [7 empty] | limit for burners A and B combined: 2.3 lb/h
AR-0049 | GEORGIA PACIFIC - CROSSETT PAPER | GEORGIA PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-12-14 | 2001 | KRAFT PAPER MILL. | BURNER EXHAUST B, TAD | 13.31 | NATURAL GAS | 50 | MMBTU/H | Source not yet installed. BACT for PM, CO, NOx, VOC. Initial & 3 -yr periodic testing is required for NOx & CO. | Volatile Organic Compounds (VOC) | N |  | 0.045 | LB/MMBTU
AR-0049 | GEORGIA PACIFIC - CROSSETT PAPER | GEORGIA PACIFIC CORPORATION | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2001-12-14 | 2001 | KRAFT PAPER MILL. | BURNER, YANKEE | 13.31 | NATURAL GAS | 21 | MMBTU/H | Source is not installed yet. Initial & 3 year periodic testing required for CO & NOx using methods 10 & 7E respectively. BACT for PM, VOC, CO and NOx. | Volatile Organic Compounds (VOC) | N |  | 0.4 | LB/H |  | 0.0192 | LB/MMBTU
OH-0257 | JACKSON COUNTY POWER, LLC | JACKSON COUNTY POWER, LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2001-12-27 | 2001 | FOUR 305 MW NATURAL-GAS FIRED COMBUSTION TURBINES, COMBINED CYCLE, WITH DLN AND SCR | AUXILIARY BOILER | 13.31 | NATURAL GAS | 76 | MMBTU/H | Limited to 3000 hours of operation per rolling 12 month period. | Volatile Organic Compounds (VOC) | N |  | 0.92 | LB/H |  | 1.37 | T/YR |  | 0.011 | LB/MMBTU
NC-0094 | GENPOWER EARLEYS, LLC | GENPOWER EARLEYS, LLC | NC | NORTH CAROLINA DIV OF ENV MGMT | 2002-01-09 | 2002 | POWER GENERATING FACILITY | BOILER, AUXILIARY, NATURAL GAS | 13.31 | NATURAL GAS | 83 | MMBTU/H | Auxiliary boiler supplies steam for start up, and maintain operating temperatures for HSRGs and steam turbine when the CTs are off line. Boiler is allowed to operate < 1000 h/yr. | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES AND DESIGN | 0.45 | LB/H |  |  |  |  | 0.0054 | LB/MMBTU | calculated
CA-1102 | FLETCHER COATING | FLETCHER COATING | CA | SOUTH COAST AQMD, CA | 2002-02-06 | 2002 |  | DRYER OR OVEN, DIRECT OR INDIRECT | 13.31 | NATURAL GAS | 5 | MMBTU/H, 400-600F OPERATING TEMPERATURE | EQUIP: , MFR: INDUSTRIAL PROCESS EQUIPMENT, TYPE: CONVEYORIZED, MODEL: , FUNC EQUIP: POWDER COATING CURING OVEN, FUEL_TYPE: , SCHEDULE: CONTINUOUS, H/D: 8, D/W: 5, W/Y: 52, NOTES: THE MANUFACTURER LITERATURE INDICATES THAT THIS BURNER MAINTAINS ACCEPTABLE | Volatile Organic Compounds (VOC) | N |  | 780 | LB/MO | FACILITYWIDE
OK-0055 | MUSTANG ENERGY PROJECT | MUSTANG POWER LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-02-12 | 2002 |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 31 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N | COMBUSTION CONTROL | 0.0055 | LB/MMBTU
OK-0056 | HORSESHOE ENERGY PROJECT | MUSTANG POWER LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-02-12 | 2002 | POWER PLANT | AUXILIARY BOILERS | 13.31 | NATURAL GAS | 0 |  |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES AND DESIGN | 0.0055 | LB/MMBTU |  |  |  |  | 0.0055 | LB/MMBTU
TX-0388 | SAND HILL ENERGY CENTER | AUSTIN ELECTRIC UTILITY | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-02-12 | 2002 | ELECTRIC POWER GENERATOR CONSISTING OF NATURAL GAS-FIRED COMBUSTION TURBINE WITH HRSG. | INLET AIR HEATERS (3) | 13.31 |  |  |  |  | Volatile Organic Compounds (VOC) | N |  | 0.003 | LB/H |  | 0.015 | T/YR
AR-0051 | DUKE ENERGY-JACKSON FACILITY | DUKE ENERGY | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-04-01 | 2002 | 620 MW NATURAL GAS TURBINE ELECTRIC UTILITY PLANT. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | GOOD OPERATING PRACTICE | 0.016 | LB/MMBTU |  |  |  |  | 0.016 | LB/MMBTU
OK-0072 | REDBUD POWER PLT | REDBUD ENERGY LP | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-05-06 | 2002 | ELECTRICAL GENERATOR | AUXILIARY BOILER | 13.31 | NATURAL GAS | 93 | MMBUT/H |  | Volatile Organic Compounds (VOC) | P | BOILER DESIGN AND GOOD OPERATING PRACTICES | 0.0075 | LB/MMBTU
OH-0264 | NORTON ENERGY STORAGE, LLC | NORTON ENERGY | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-05-23 | 2002 | NINE 300 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE WITH DLN AND SCR; TEN 11.45 MMBTU/H NATURAL GAS-FIRED FUEL SUPPLY HEATERS/BOILERS; SEVEN 12.84 MMBTU/H NATURAL GAS-FIRED RECUPERATOR PRE HEATERS/BOILERS | RECUPERATOR PRE-HEATERS (9) | 13.31 | NATURAL GAS | 12.84 | MMBTU/H | Each boiler is limited to 100 hour of operation per rolling 12 months. | Volatile Organic Compounds (VOC) | N |  | 0.071 | LB/H |  | 0.004 | T/YR |  | 0.006 | LB/MMBTU |  | Limits are for each boiler. Each boiler is retricted to 100 hours of operation.
OH-0264 | NORTON ENERGY STORAGE, LLC | NORTON ENERGY | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-05-23 | 2002 | NINE 300 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE WITH DLN AND SCR; TEN 11.45 MMBTU/H NATURAL GAS-FIRED FUEL SUPPLY HEATERS/BOILERS; SEVEN 12.84 MMBTU/H NATURAL GAS-FIRED RECUPERATOR PRE HEATERS/BOILERS | FUEL SUPPLY HEATERS (9) | 13.31 | NATURAL GAS | 11.45 | MMBTU/H | Each fuel supply heater is limited to a maximum annual cumulative fuel heat input of 47,630 mmBtu per rolling 12 months. | Volatile Organic Compounds (VOC) | N |  | 0.063 | LB/H |  | 0.13 | T/YR |  | 0.006 | LB/MMBTU |  | Limits are for each heater.
OK-0070 | GENOVA OK I POWER PROJECT | GENOVA OKLAHOMA LLC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2002-06-13 | 2002 | COMBINED CYCLE POWER PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | BOILER DESIGN AND GOOD COMBUSTION PRACTICES | 0.016 | LB/MMBTU
NM-0044 | CLOVIS ENERGY FACILITY | DUKE ENERGY CURRY LLC | NM | NEW MEXICO ENVIRONMENT DEPT/APC BUREAU | 2002-06-27 | 2002 | THIS IS A 1,200 MW COMBINED CYCLE MERCHANT POWER PLANT. | AUXILIARY BOILERS (AUX-1 AND AUX-2) | 13.31 | NATURAL GAS | 33 | MMBTU/H | Emission limits are for each (Aux-1 and Aux-2) Auxiliary Boiler. | Volatile Organic Compounds (VOC) | P | CLEAN FUELS, GOOD COMBUSTION PRACTICE | 0.5 | LB/H
TX-0437 | HARTBURG POWER, LP | HARTBURG POWER, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-07-05 | 2002 | LOCATED AT NE OF INDIAN LAKE RD, DEWYVILLE, TX. NEW POWER FACILITY. | BOILERS, AUXILIARY | 13.31 | NATURAL GAS | 40 | mmbtu/h |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES PROPER DESIGN, CLEAN FUEL | 0.02 | LB/MMBTU
AL-0185 | BARTON SHOALS ENERGY | BARTON SHOALS ENERGY, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2002-07-12 | 2002 | ELECTRIC GENERATION - NATURAL GAS FIRED COMBINED CYCLE | TWO (2) 40 MMBTU/H AUXILIARY BOILERS | 13.31 | NATURAL GAS | 40 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.0054 | LB/MMBTU |  | 0.2 | LB/H
IA-0060 | HAWKEYE GENERATING, LLC | ENTERGY | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-07-23 | 2002 | ENTERGY IS INSTALLING TWO GE 7FA (170MW) NATURAL GAS FIRED TURBINES. THEY ARE REQUIRED TO INSTALL SCR FOR CONTROL OF NOX (3 PPMVD, 3 HOUR AVG. TIME) AND CATALYTIC OXIDATION FOR THE CONTROL OF CO (5 PPMVD, 3 HOUR AVG. TIME) FOR COMBINED CYCLE OPERATION. SI | AUXILIARY BOILER (48.5 MMBTU/H) | 13.31 | NATUAL GAS | 48.69 | MILLION CF/YR |  | Volatile Organic Compounds (VOC) | B | GCP | 0.005 | LB/MMBTU
AR-0070 | GENOVA ARKANSAS I, LLC | GENOVA ARKANSAS I, LLC | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2002-08-23 | 2002 | COMBINED CYCLE POWER PLANT | AUXILIARY BOILER | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICE | 0.018 | LB/MMBTU
VA-0261 | CPV CUNNINGHAM CREEK | COMPETITIVE POWER VENTURE | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-09-06 | 2002 | TURBINES USED TO PRODUCE ELECTRICITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 80 | MMBTU/H | one auxiliary boiler | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES. | 0.42 | LB/H |  | 0.63 | T/YR |  |  |  |  | Additional limit: .005 lb/mmBtu
OH-0248 | LAWRENCE ENERGY | CALPINE CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2002-09-24 | 2002 | THREE 180 MW GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE, WITH DLN, SCR AND OXIDATION CATALYST | BOILER | 13.31 | NATURAL GAS | 99 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N |  | 0.545 | LB/H |  | 0.0055 | LB/MMBTU |  | 0.0055 | LB/MMBTU |  | Limits are for each boiler.
WI-0195 | SENA NIAGARA MILL | STORA ENSO NORTH AMERICA | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2002-10-18 | 2002 |  | PROCESS HEATER, PAPER MACHINE P51 | 13.31 | NATURAL GAS | 34.4 | MMBTU/H | Throughput is total for natural gas IR and flotation dryers. | Volatile Organic Compounds (VOC) | P | BACT FOR VOC EMISSIONS FROM ANY NEW (REPLACEMENT) IR BURNERS IS LOW NOX IR BURNERS, GOOD COMBUSTION CONTROL AND USE OF NATURAL GAS. |  |  | see notes | [6 empty] | No emission rate limit, BACT is pollution prevention.
NJ-0062 | CONSOLIDATE EDISON DEVELOPMENT (CED) | CONSOLIDATED EDISON DVPMT.- LAKEWOOD GEN. FACILITY | NJ | NEW JERSEY DEPT OF ENV PROTECTION | 2002-10-22 | 2002 | POWER GENERATION | FUEL GAS HEATERS (3 UNITS) | 13.31 | NATURAL GAS | 4.62 | MMBTU/H | INSTALLATION OF 3 NEW FUEL GAS HEATERS@ 4.62 MMBTU/HR EACH. FUEL: NATURAL GAS. | Volatile Organic Compounds (VOC) | N | GOOD COMBUSTION PRACTICE | 0.22 | LB/H |  | 0.05 | LB/MMBTU |  | 50 | PPMVD@3%O2
GA-0101 | MURRAY ENERGY FACILITY | DUKE ENERGY MURRAY LLC | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2002-10-23 | 2002 | ELECTRIC GENERATING FACILITY | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 31.4 | MMBTU/H | HOURS OF OPERATION NOT TO EXCEED 6,000 H/YR. | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICE | 0.0127 | LB/MMBTU
VA-0255 | VA POWER - POSSUM POINT | Virginia Power | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2002-11-18 | 2002 | THIE PERMIT WAS AMENDED AND APPROVED ON 11/18/2002 FROM THE PERMIT THAT WAS DATED 10/05/2001. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 99 | MMBTU/H | 2 Auxiliary boilers. | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES. | 0.4 | LB/H | EACH UNIT | 2 | T/YR | UNITS COMBINED | 0.004 | LB/MMBTU | EACH UNIT
TX-0408 | INDIAN ROCK GATHERING COMPANY LP | INDIAN ROCK GATHERING COMPANY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-11-22 | 2002 | NATURAL GAS PROCESSING FACILITY | AUXILIARY BOILER, (2) | 13.31 | NATURAL GAS | 6 | MMBTU/H | BOILERS ARE UNCONTROLLED BECAUSE BOILER DUTY IS <40 MMBTU/H. | Volatile Organic Compounds (VOC) | N |  | 0.01 | LB/H | EACH | 0.05 | T/YR | EACH |  |  |  | UNCONTROLLED BECAUSE BOILER IS LESS THAN 40 MMBTU/H.
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | HEAT TRANSFER FLUID HEATER, H202 | 13.31 | NATURAL GAS | 31 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 0.17 | LB/H |  | 0.74 | T/YR
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | HEAT TRANSFER FLUID HEATER, H2202 | 13.31 | NATURAL GAS | 31 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 0.17 | LB/H |  | 0.74 | T/YR
TX-0354 | ATOFINA CHEMICALS INCORPORATED | ATOFINA CHEMICALS INCORPORATED | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-19 | 2002 | ACROLEIN (AC) IS PRODUCED BY THE SELECTIVE OXIDATION OF PROPYLENE ACROSS A FIXED BED CATALYST REACTOR IN A CONTINUOUS PROCESS. PROPYLENE IS DELIVERED TO THE SITE VIA PIPELINE REQUIRING NO ON SITE STORAGE. THIS REACTION IS EXOTHERMIC AND HEAT IS RECOVERED | (2) STEAM BOILERS, X-426A AND X-426B | 13.31 | NATURAL GAS | 15.8 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED. | 0.09 | LB/H | EACH | 0.38 | T/YR | EACH
IA-0062 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT (IPL) | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-12-20 | 2002 | PERMITS WERE AMENDED ON 6/26/03. RBLC ID IA-0062 WAS CORRECTED AS MOST OF THE CHANGES WERE MINOR (BASED ON OPERATIONAL & DESIGN CHANGES BEING MADE AS PLANT IS CONSTRUCTED). THE NEW DEW POINT HEATER HAS BEEN GIVEN A NEW RBLC ID. | GAS HEATER, (2) | 13.31 | NATURAL GAS | 16.4 | MMBTU/H | Natural Gas fired Heaters, 16.4 MMBTU/HR capacity for each. Operating hours reduced from 8760 hours to 6000 hours each. | Volatile Organic Compounds (VOC) | N |  | 0.0054 | LB/MMBTU |  |  |  |  | 0.0054 | LB/MMBTU
IA-0062 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT (IPL) | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2002-12-20 | 2002 | PERMITS WERE AMENDED ON 6/26/03. RBLC ID IA-0062 WAS CORRECTED AS MOST OF THE CHANGES WERE MINOR (BASED ON OPERATIONAL & DESIGN CHANGES BEING MADE AS PLANT IS CONSTRUCTED). THE NEW DEW POINT HEATER HAS BEEN GIVEN A NEW RBLC ID. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 68 | MMBTU/H | Limited to 6000 hours of operation per year. | Volatile Organic Compounds (VOC) | A | CATALYTIC OXIDATION | 0.0054 | LB/MMBTU | [7 empty] | Cat. Ox. primarily controlling CO
TX-0389 | BAYTOWN CARBON BLACK PLANT | DEGUSSA ENGINEERED CARBONS, LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2002-12-31 | 2002 |  | BACK-UP BOILER | 13.31 | NATURAL GAS | 13.4 | MMBUT/H |  | Volatile Organic Compounds (VOC) | N |  | 0.08 | LB/H |  | 0.35 | T/YR
OH-0295 | GMC TRUCK AND BUS, MORAINE ASSEMBLY PLANT | GENERAL MOTORS CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-01-14 | 2003 | LIGHT DUTY TRUCKS AND AUTOMOBILE PRODUCTION, ASSEMBLY PLANT | NATURAL GAS USAGE | 13.31 | NATURAL GAS | 1700 | MMCF/rolling 12-mo | THE INCREASE IN NATURAL GAS USAGE CAUSED THIS PERMIT TO BE PSD FOR NOX. COMBINED NATURAL GAS USAGE FOR: ELPO SAND, GUIDE COAT, BODY SAND, BODY WIPE, TOPCOAT SYSTEM, TOPCOAT ABATEMENT, FINAL REPAIR, DEADNER, BUILDING HEAT. | Volatile Organic Compounds (VOC) | N |  | 4.68 | T/YR
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HOT OIL HEATER, EPN6 | 13.31 | NAT GAS | 12 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 0.08 | LB/H |  | 0.28 | T/YR
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | GLYCOL REBOILER, EPN11 | 13.31 | NAT GAS | 2.5 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 0.02 | LB/H |  | 0.06 | T/YR
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HOT OIL HEATER, EPN26 | 13.31 | NAT GAS | 32.5 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 0.21 | LB/H |  | 0.77 | T/YR
TX-0364 | SALT CREEK GAS PLANT | EXXON MOBIL CORPORATION | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-01-31 | 2003 | EXXON MOBILE REQUESTED AN AMENDMENT TO PERMIT 20660 AND A PSD MAJOR MODIFICATION TO PSD-TX-795M1 TO UPDATE THE FLARE EMISSIONS TO REFLECT REVISED GAS VOLUMES AND INCREASES IN ACID GAS CONTENT. THE AMENDMENT UPDATES THE PROCESS FLARE EMISSIONS BUT DOES NOT | HP TEG FIREBOX, EPN30 | 13.31 | NAT GAS | 3 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N | NONE INDICATED | 0.02 | LB/H |  | 0.07 | T/YR
LA-0199 | NORCO CHEMICAL PLANT, M-UNIT | SHELL CHEMICAL LP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2003-03-21 | 2003 | UNIT MANUFACTURES MEK & SECONDARY BUTANOL PRODUCTS. PSD ADDRESSES THE M-UNIT DEBOTTLENECK PROJECT, WHICH INCREASED CAPACITY OF PUMPS, INCREASED PHASE SEPARATION CAPACITY, AND REROUTED EXISTING HEAT EXCHANGERS. | DEHYDROGENATION FURNACES (4) | 13.31 | NATURAL GAS | 7.7 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES AND ENGINEERING DESIGN | 0.04 | LB/H | HOURLY MAXIMUM | 0.18 | T/YR | ANNUAL MAXIMUM | 0.005 | LB/MMBTU | ANNUAL AVERAGE
OK-0090 | DUKE ENERGY STEPHENS, LLC STEPHENS ENERGY | DUKE ENERGY | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2003-03-21 | 2003 | MERCHANT POWER PLANT - NOMINAL TOTAL OF 620 MW. | BOILER, AUXILIARY | 13.31 | NATURAL GAS | 33 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | BOILER DESIGN AND GOOD OPERATING PRACTICES | 0.016 | LB/MMBTU
GA-0098 | RINCON POWER PLANT | GENPOWER RINCON LLC | GA | GEORGIA DEPARTMENT OF NATURAL RESOURCES | 2003-03-24 | 2003 | ELECTRIC GENERATING FACILITY | AUXILIARY BOILER | 13.31 | NATURAL GAS | 83 | MMBTU/H | THE BOILER IS LIMITED TO 1,000 H/YR OF OPERATION. | Volatile Organic Compounds (VOC) | N |  | 0.004 | LB/MMBTU | AS METHANE
VA-0271 | HARRISONBURG RESOURCE RECOVER FACILITY | CITY OF HARRISONBURG | VA | VIRGINIA ENVIRONMENTAL QUALITY AIR DIV. | 2003-03-24 | 2003 |  | BOILER NO. 1 | 13.31 | NATURAL GAS | 43.2 | MMBTU/H | One of two boilers | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES. | 0.23 | LB/H | each unit | [6 empty] | one of two units
OH-0276 | CHARTER STEEL | CHARTER MANUFACTURING CO., INC. | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-04-14 | 2003 | NEW MELT SHOP AT EXISTING FACILITY, INCLUDES NEW: ELECTRIC ARC FURNACE; LADLE METALLURGY FURNACE; VACUUM OXYGEN DEGASSER (VOD); VOC BOILER; CONTINUOUS CASTING MACHINES; 3 SILOS; 6 LADLE PREHEATERS; CUT-OFF-TORCH; 3 TUNDISH PREHEATERS; PROCESS SPACE HEATER | BOILER FOR VACUUM OXYGEN DEGASSER VESSEL | 13.31 | NATURAL GAS | 25 | MMBTU/H | VACUUM OXYGEN DEGASSER VESSEL BOILER, WITH LOW NOX BURNER | Volatile Organic Compounds (VOC) | N |  | 0.13 | LB/H | FROM NATURAL GAS COMBUSTION | 0.59 | T/YR | FROM NATURAL GAS COMBUSTION
AL-0202 | CORUS TUSCALOOSA | CORUS TUSCALOOSA | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2003-06-03 | 2003 | STEEL MILL | EQUALIZING FURNACE | 13.3 | NATURAL GAS | 1.8 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N | NATURAL GAS/GOOD COMBUSTION | 0.5 | LB/H |  | 3 | LB/MMCF
IA-0068 | EMERY GENERATING STATION | INTERSTATE POWER & LIGHT - EMERY GENERATING STATI | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2003-06-26 | 2003 | IPL CHANGED NAMES FROM THE POWER IOWA ENERGY CENTER (PIEC) TO THE EMERY GENERATING STATION. | GAS HEATER | 13.31 | NATURAL GAS | 9 | MMBTU/H | One natural gas dew point heater is added. | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.0054 | LB/MMBTU |  | 0.21 | T/YR |  | 0.0054 | LB/MMBTU
TX-0458 | JACK COUNTY POWER PLANT | DUKE ENERGY LP | TX | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | 2003-07-22 | 2003 | DUKE ENERGY JACK, L.P. IS CONSTRUCTING A 620 MW COMBINED CYCLE POWER PLANT. TWO COMBUSTION TURBINES WILL EACH PROVIDE APPROXIMATELY 170 MW OF ELECTRICITY. A 550 MMBTU/HR DUCT BURNER ON EACH TURBINE EXHAUST STREAM WILL ADD SUPPLEMENTAL HEAT TO THE HEAT REC | AUXILIARY BOILER | 13.31 | NATURAL GAS | 36 | mmbtu/h |  | Volatile Organic Compounds (VOC) | N |  | 0.6 | LB/H |  | 1.8 | T/YR
OH-0254 | DUKE ENERGY WASHINGTON COUNTY LLC | DUKE ENERGY NORTH AMERICA | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2003-08-14 | 2003 | TWO 170 MW NATURAL GAS-FIRED COMBUSTION TURBINES, COMBINED CYCLE | BOILER | 13.31 | NATURAL GAS | 30.6 | MMBTU/H | THE MAXIMUM ANNUAL FUEL HEAT INPUT SHALL NOT EXCEED 128,000 MMBTU/ROLLING 12-MONTHS | Volatile Organic Compounds (VOC) | N |  | 0.49 | LB/H |  | 1.1 | T/ROLLING 12-MONTHS |  | 0.016 | LB/MMBTU
AZ-0049 | LA PAZ GENERATING FACILITY | ALLEGHENY ENERGY SUPPLY LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2003-09-04 | 2003 | NATURAL GAS FIRED, COMBINED CYCLE GENERATING STATION | AUXILIARY BOILER FOR GE TURBINE | 13.31 | NATURAL GAS | 41 | MMBTU/H | THIS BOILER IS TO BE USED IF THE GE TURBINE SETUP IS SELECTED. | Volatile Organic Compounds (VOC) | N |  | 0.01 | LB/MMBTU
AZ-0049 | LA PAZ GENERATING FACILITY | ALLEGHENY ENERGY SUPPLY LLC | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2003-09-04 | 2003 | NATURAL GAS FIRED, COMBINED CYCLE GENERATING STATION | AUXILIARY BOILER FOR SIEMENS TURBINES | 13.31 | NATURAL GAS | 55.34 | MMBTU/H | THIS BOILER IS FOR USE WHEN THE SIEMENS TURBINE SYSTEM IS SELECTED. | Volatile Organic Compounds (VOC) | N |  | 0.01 | LB/MMBTU |  |  |  |  | 0.01 | LB/MMBTU
LA-0185 | WEST MONROE PACKAGING PLANT | GRAPHIC PACKAGING INTERNATIONAL, INC. | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2003-11-05 | 2003 | FACILITY MANUFACTURES BEVERAGE CARRIERS FROM PAPERBOARD. PROCESSES CONSIST OF PRINTING, CUTTING, FOLDING, AND GLUING. PROJECT INVOLVES INSTALLATION OF ONE PACKAGING ROTOGRAVURE PRESS AND ASSOCIATED DRYER. | DRYER BURNER (9.6 MM BTU/H) | 13.31 |  | 9.6 | MMBTU/H | DRYER ASSOCIATED WITH ROTOGRAVURE PRESS. | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES CONSISTING OF USE OF PIPELINE NATURAL GAS AND PROPER OPERATING AND MAINTENANCE TECHNIQUES. | 0.069 | LB/H | HOURLY MAXIMUM | 0.231 | T/YR | ANNUAL MAXIMUM | 0.007 | LB/MMBTU | ANNUAL AVERAGE
IN-0108 | NUCOR STEEL | NUCOR STEEL | IN | INDIANA DEPT OF ENV MGMT, OFC OF AIR | 2003-11-21 | 2003 | STEEL MINI MILL | BOILER, NATURAL GAS, (2) | 13.31 | NATURAL GAS | 34 | MMBTU/H | Throughput for each. Propane is backup fuel. These boilers supply steam to the entire cold mill area of the plant. Subject to NSPS Subpart Dc | Volatile Organic Compounds (VOC) | P | COMPLIANCE BY USING NATURAL GAS | 0.0026 | LB/MMBTU |  |  |  |  | 0.0026 | LB/MMBTU
MN-0054 | MANKATO ENERGY CENTER |  | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2003-12-04 | 2003 | COMBINED CYCLE GAS TURBINE ELECTRIC POWER PLANT. TWO IDENTICAL GE FRAME F7A GAS TURBINES EACH WITH HRSG W/DUCT BURNERS FEEDING STEAM TO COMMON STEAM TURBINES. PRIMARY FUEL IS NG, NO. 2 VERY LOW SULFUR DISTILLATE OIL FOR BACKUP. ALSO, AUX. BOILER, DIESEL E | BOILER, COMMERCIAL | 13.31 | NATURAL GAS | 70 | MMBTU/H | NATURAL GAS ONLY | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION | 0.007 | LB/MMBTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S50/B50, 60 MMBTU/H | 13.31 | NATURAL GAS | 60 | MMBTU/H | NATURAL GAS / PROPANE | Volatile Organic Compounds (VOC) | P | NATURAL GAS / PROPANE, GOOD COMBUSTION CONTROLS | 0.0054 | LB/MMBTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S51/B51, 80 MMBTU/H | 13.31 | NATURAL GAS | 80 | MMBTU/H | NAT. GAS / PROPANE | Volatile Organic Compounds (VOC) | P | NAT. GAS / PROPANE; GOOD COMBUSTION CONTROL | 0.0054 | LB/MMBTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S52/B52, 11 MMBTU/H | 13.31 | NATURAL GAS | 11 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | NATURAL GAS / PROPANE; GOOD COMBUSTION CONTROL | 0.0054 | LB/MMBTU
WI-0207 | ACE ETHANOL - STANLEY | ACE ETHANOL, LLC | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-01-21 | 2004 |  | BOILER, S53 / B53, 34 MMBTU/H | 13.31 | NATURAL GAS | 34 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | NATURAL GAS / PROPANE; GOOD COMBUSTION CONTROL | 0.0054 | LB/MMBTU
OK-0097 | QUAD GRAPHICS OKC FAC | QUAD GRAPHICS INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2004-02-03 | 2004 | COMMERCIAL PRINTING | BOILERS, NATURAL GAS, STEAM GENERATORS | 13.31 | NATURAL GAS | 600 | HP | Throughput for each boiler. Boilers produce steam for solvent recovery. Natural gas is primary fuel, propane used for emergencies, limited to 336 h/yr, each boiler. | Volatile Organic Compounds (VOC) | P | MAINTENANCE/OPERATION PER MANUFACTURER''S SPECIFICATIONS | 0.52 | LB/H | NONMETHANE HYDROCARBONS | 1.722 | T/YR | NONMETHANE HYDROCARBONS |  |  |  | LIMITS ARE FOR NONMETHANE HYDROCARBONS.
NV-0037 | COPPER MOUNTAIN POWER | SEMPRA ENERGY RESOURCES | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2004-05-14 | 2004 | A 600 MW COMBINED CYCLE ELECTRICAL GENERATION FACILITY CONSISTING OF TWO COMBUSTION TURBINE GENERATORS WITH HEAT RECOVERY STEAM GENERATORS, ONE STEAM TURBINE GENERATOR, AND ONE AUXILIARY BOILER. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 60 | MMBTU/H |  | Volatile Organic Compounds (VOC) | B | EFFECTIVE COMBUSTION SYSTEM DESIGN, 10:1 TURNDOWN CAPABILITY AND LOW NOX BURNER TECHNOLOGY | 0.4 | LB/H
CO-0058 | CHEYENNE STATION | CHEYENNE PLAINS GAS PIPELINE COMPANY | CO | COLORADO DEPT OF HEALTH - AIR POLL CTRL | 2004-06-12 | 2004 | COMPRESSOR STATION | HEATERS | 13.31 | NATURAL GAS | 45 | MMBTU/H | TWO HOT OIL HEATERS RATED AT 45 MMBTU/HR AND ONE UTILITY HEATER RATED AT 16 MMBTU/HR. THE HEATERS ARE INCLUDED IN PERMIT 03WE0913. | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.016 | LB/MMBTU | 1-HR AVERAGE |  |  |  | 0.016 | LB/MMBTU
WI-0223 | LOUISIANA-PACIFIC HAYWARD | LOUISIANA-PACIFIC CORPORATION | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-06-17 | 2004 | OSB MILL | THERMAL OIL HEATER, GTS ENERGY, S31, B31 | 13.31 | NATURAL GAS | 32 | MMBTU/H | STACK S31; BOILER B31 - GTS ENERGY THERMAL OIL HEATER RATED AT 32.0 MILLION BTU PER HOUR WHEN BURNING NATURAL GAS AND 30.0 MILLION BTU PER HOUR WHEN BURNING DISTILLATE FUEL OIL | Volatile Organic Compounds (VOC) | P | USE OF NATURAL GAS / DISTILLATE OIL, W/ RESTRICTION ON OIL USAGE | 0.18 | LB/H
WI-0223 | LOUISIANA-PACIFIC HAYWARD | LOUISIANA-PACIFIC CORPORATION | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-06-17 | 2004 | OSB MILL | THERMAL OIL HEATER, GTS ENERGY, S32, B32 | 13.31 | NATURAL GAS | 32 | MMBTU/H | STACK S32; BOILER B32 - GTS ENERGY THERMAL OIL HEATER RATED AT 32.0 MILLION BTU PER HOUR WHEN BURNING NATURAL GAS AND 30.0 MILLION BTU PER HOUR WHEN BURNING DISTILLATE FUEL OIL. | Volatile Organic Compounds (VOC) | P | USE OF NATURAL GAS / DISTILLATE OIL, W/ RESTRICTION ON OIL USAGE | 0.18 | LB/H
NE-0026 | NUCOR STEEL DIVISION | NUCOR STEEL CORP. | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2004-06-22 | 2004 |  | NNII REHEAT FURNACE | 13.31 | NATURAL GAS | 143 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N |  | 0.0055 | LB/MMBTU
NE-0026 | NUCOR STEEL DIVISION | NUCOR STEEL CORP. | NE | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | 2004-06-22 | 2004 |  | NNII BILET POST-HEATER | 13.31 | NATURAL GAS | 6.8 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N |  | 0.0055 | LB/MMBTU
MN-0053 | FAIRBAULT ENERGY PARK | MN MUNICIPAL POWER AGENCY | MN | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | 2004-07-15 | 2004 | LARGE COMBUSTION TURBINE ELECTRIC POWER PLANT - INITIAL OPERATION IN SIMPLE CYCLE AND CONVERSION TO COMBINED CYCLE IN THE FUTURE. | BOILER, NATURAL GAS (1) | 13.31 | NATURAL GAS | 40 | MMBTU/H | AUXILIARY BOILER. | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION. | 0.006 | LB/MMBTU | 3 HOUR AVERAGE
AR-0077 | BLUEWATER PROJECT | STEELCORR, INC. | AR | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | 2004-07-22 | 2004 | THE FACILITY IS A NEW SPECIALTY STEEL MILL PRODUCING VARIOUS HOT ROLLED, COLD ROLLED AND GALVANIZED PRODUCTS FOR VARIOUS END USE MARKETS. AFIN: 47-00541 | BOILERS | 13.31 | NATURAL GAS | 22 | MMBTU/H | ENTRY INCLUDES TWO BOILERS. THE 22 MMBTU/H PICKLE LINE BOILER, 51 MMBTU/H VACUUM DEGASSER BOILERS. | Volatile Organic Compounds (VOC) | P | NATURAL GAS COMBUSTION ONLY | 0.0055 | LB/MMBTU
LA-0186 | WEST MONROE PACKAGING PLANT | GRAPHIC PACKAGING INTERNATIONAL, INC. | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2004-09-14 | 2004 | FACILITY MANUFACTURES BEVERAGE CARRIERS FROM PAPERBOARD. PROCESSES CONSIST OF PRINTING, CUTTING, FOLDING, AND GLUING. PROJECT INVOLVES INSTALLATION OF ONE PACKAGING ROTOGRAVURE PRESS AND ASSOCIATED DRYER. | DRYER BURNER (13.3 MM BTU/H) | 13.31 | NATURAL GAS | 13.3 | MMBTU/H | DRYER ASSOCIATED WITH ROTOGRAVURE PRESS. | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES CONSISTING OF USE OF PIPELINE NATURAL GAS AND PROPER OPERATING AND MAINTENANCE TECHNIQUES. | 0.095 | LB/H | HOURLY MAXIMUM | 0.32 | T/YR | ANNUAL MAXIMUM | 0.007 | LB/MMBTU | ANNUAL AVERAGE
WI-0227 | PORT WASHINGTON GENERATING STATION | WE ENERGIES (WEPCO) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-13 | 2004 | ELECTRIC GENERATION | NATURAL GAS FIRED AUXILLIARY BOILER | 13.31 | NATURAL GAS | 97.1 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | NATURAL GAS FUEL, GOOD COMBUSTION PRACTICES | 0.53 | LB/H |  |  |  |  | 0.0055 | LB/MMBTU | *SEE NOTES | * CACULATED STANDARD NUMERIC LIMIT
WI-0227 | PORT WASHINGTON GENERATING STATION | WE ENERGIES (WEPCO) | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-13 | 2004 | ELECTRIC GENERATION | GAS HEATER (P06, S06) | 13.31 | NATURAL GAS | 10 | MMBTU/H | GAS CONDITIONING HEATER | Volatile Organic Compounds (VOC) | P | NATURAL GAS FUEL | 0.06 | LB/H |  |  |  |  | 0.006 | LB/MMBTU | CALCULATED
WI-0228 | WPS - WESTON PLANT | WISCONSIN PUBLIC SERVICE | WI | WISCONSIN DEPT OF NATURAL RESOURCES | 2004-10-19 | 2004 | ELECTRICAL UTILITY | B63, S63; B64, S64 - NATURAL GAS STATION HEATER 1 AND 2 | 13.31 | NATURAL GAS | 0.75 | MMBTU/H | EMISSION LIMITS ARE THOSE FOR EACH UNIT. | Volatile Organic Compounds (VOC) | P | NATURAL GAS | 0.004 | LB/H | [7 empty] | (LIMIT IS FOR EACH UNIT)
AZ-0047 | WELLTON MOHAWK GENERATING STATION | DOME VALLEY ENERGY PARTNERS | AZ | ARIZONA DEPT OF ENV QUAL, OFC OF AIR QUA | 2004-12-01 | 2004 | COMBINED CYCLE GAS-FIRED ELECTRICITY GENERATING STATION | AUXILIARY BOILER | 13.31 | NATURAL GAS | 38 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N |  | 0.0033 | LB/MMBTU | BASED ON HIGHER HEATING VALUE OF FUEL
OK-0108 | NOMACO OKLAHOMA CITY FACILITY | NOMACO INC | OK | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | 2004-12-03 | 2004 | POLYETHYLENE FOAM EXTRUSION PLANT | COMBUSION UNITS (ENGINE/HEATERS) | 13.31 | NATURAL GAS |  |  | COMBUSTION UNITS ARE: 200 HP FIRE PUMP, 290 HP EMERGENCY GENERATOR, AND 10.1 MMBTU/H (TOTAL) PROCESS HEATERS. ALL UNITS, COMBINED, EXPECTED TO EMIT ONLY 0.05% OF THE TOTAL VOC. | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION DESIGN FOR THE TWO ENGINES AND BOILERS |  |  | SEE NOTE | [6 empty] | BACT IS GOOD DESIGN. NO EMISSION RATE LIMITS.
OH-0252 | DUKE ENERGY HANGING ROCK ENERGY FACILITY | DUKE ENERGY HANGING ROCK, LLC | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2004-12-28 | 2004 | FOUR NATURAL GAS (NG) FIRED COMBUSTION TURBINES, WITH DUCT BURNERS; COMBINED CYCLE, EACH 172 MW | BOILERS (2) | 13.31 | NATURAL GAS | 30.6 | MMBTU/H | LIMITS ARE FOR EACH BOILER INDIVIDUALLY. THE MAXIMUM FUEL HEAT INPUT SHALL NOT EXCEED 91,500 MMBTU/ROLLING 12-MONTHS FOR EACH BOILER. | Volatile Organic Compounds (VOC) | N |  | 0.49 | LB/H | EACH BOILER | 0.74 | T/ROLLING 12-MONTHS | EACH BOILER | 0.016 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER
LA-0192 | CRESCENT CITY POWER | CRESENT CITY POWER, LLC | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-06-06 | 2005 | NEW 600 MW NATURAL GAS-FIRED COMBINED CYCLE POWER PLANT | FUEL GAS HEATERS (3) | 13.31 |  | 19 | MMBTU/H |  | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 0.1 | LB/H | HOURLY MAXIMUM | 0.04 | T/YR | *SEE NOTES. ANNUAL MAXIMUM | 0.005 | LB/MMBTU | ANNUAL AVERAGE | *TPY LIMIT FOR ALL 3 HEATERS. AGGREGATE HEAT INPUT IS LIMITED TO 14,250 MM BTU/YR. ONLY 2 OF THE 3 HEATERS ARE ALLOWED TO OPERATE AT ANY GIVEN TIME.
LA-0203 | OAKDALE OSB PLANT | MARTCO LIMITED PARTNERSHIP | LA | LOUISIANA DEPARTMENT OF ENV QUALITY | 2005-06-13 | 2005 | PSD FOR A NEW ORIENTED STRAND BOARD (OSB) MANUFACTURING FACILITY CAPABLE OF PRODUCING 900,000 MSF 3/8 INCH OSB PER YEAR. | AUXILIARY THERMAL OIL HEATER | 13.31 | NATURAL GAS | 66.5 | MMBTU/H | OPERATING TIME = 500 HR/YR. | Volatile Organic Compounds (VOC) | P | USE OF NATURAL GAS AS FUEL AND GOOD COMBUSTION PRACTICES | 0.43 | LB/H | HOURLY MAXIMUM
MD-0035 | DOMINION | DOMINION COVE POINT LNG, L.P. | MD | MARYLAND DEPARTMENT OF THE ENVIRONMENT | 2005-08-12 | 2005 | LNG FACILITY | VAPORIZATION HEATER | 13.31 | NATURAL GAS |  |  | SEVEN VAPORIZATION HEATERS; RATED HEAT INPUT IS 88.4 MMBTU/H FOR EACH UNIT; EMISSION LIMITS APPLY TO EACH UNIT | Volatile Organic Compounds (VOC) |  | NATURAL GAS COMBUSTION AND A CATALYTIC OXIDATION | 0.002 | LB/MMBTU
MD-0035 | DOMINION | DOMINION COVE POINT LNG, L.P. | MD | MARYLAND DEPARTMENT OF THE ENVIRONMENT | 2005-08-12 | 2005 | LNG FACILITY | EMERGENCY VENT HEATER | 13.31 | NATURAL GAS |  |  | ONE 1.3 MMBTU/HR EMERGENCY VENT HEATER | Volatile Organic Compounds (VOC) | P | BURN NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.0054 | LB/MMBTU | 3-HOUR AVERAGE
MD-0036 | DOMINION | DOMINION COVE POINT LNG, L.P. | MD | MARYLAND DEPARTMENT OF THE ENVIRONMENT | 2006-03-10 | 2006 | LNG FACILITY | FUEL GAS PROCESS HEATER | 13.31 | NATURAL GAS |  |  | ENGINEERING TECH NO. IDHLE 1.0; 0.93 MMBTU/HR | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PRACTICES | 143 | PPMVD | 3-HOUR AVERAGE | [6 empty] | 143 PPMVD (CORRECTED TO 3% O2)
*NV-0046 | GOODSPRINGS COMPRESSOR STATION | KERN RIVER GAS TRANSMISSION COMPANY | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2006-05-16 | 2006 | THE FACILITY IS A COMPRESSOR STATION ON AN INTER-STATE PIPELINE FOR TRANSPORTING NATURAL GAS. THE FACILITY IS A MAJOR STATIONARY SOURCE FOR NITROGEN OXIDES IN A NON-ATTAINMENT AREA FOR OZONE AIR QUALITY. | COMMERCIAL/INSTITUTIONAL BOILER | 13.31 | NATURAL GAS | 3.85 | MMBTU/H | THE UNIT'S MODEL IDENTIFICATION IS PEERLESS 724 FDA WU. | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION PROCESS | 0.0052 | LB/MMBTU |  | 0.09 | T/YR
NV-0044 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S ENTERTAINMENT | NV | CLARK CO. DEPT. OF AIR QUALITY AND ENVIRONMENTAL MANAGEMENT | 2007-01-04 | 2007 | THE FACILITY IS A NEW MAJOR STATIONARY SOURCE FOR NITROGEN OXIDES AS A RESULT OF CONSOLIDATING SIX LARGE HOTEL/CASINO RESORTS, WHICH ARE HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. | COMMERCIAL/INSTITUTIONAL-SIZE BOILERS | 13.31 | NATURAL GAS | 35.4 | MMBTU/H | THE BACT DETERMINATIONS REPORTED HERIN ARE SPECIFICALLY FOR THE TWO HURST BOILERS INSTALLED AT CAESAR'S PALACE. EACH OF THEM HAS A RATED HEAT INPUT OF 35.4 MMBTU/HR. THE PERMITTING ACTION ALSO APPROVED THE INSTALLATION OF A NUMBER OF SMALL BOILERS, ALL OF | Volatile Organic Compounds (VOC) | P | GOOD COMBUSTION DESIGN | 0.005 | LB/MMBTU |  | 0.18 | LB/H |  | 0.005 | LB/MMBTU |  | THE DATA PERTAIN TO EITHER ONE OF THE HURST BOILERS, WHICH RATED HEAT INPUT IS 35.4 MMBTU/H.
MS-0085 | DART CONTAINER CORPORATION LLC | DART CONTAINER CORPORATION LLC | MS | MISSISSIPPI DEPT OF ENV QUALITY | 2007-01-31 | 2007 | EPS CONTAINER MANUFACTURING USING STEAM PRE-EXPANDER AND STEAM CHEST MOLDING PROCESSES | NATURAL GAS FIRED BOILER | 13.31 | NATURAL GAS | 33.5 | MMBTU/h |  | Volatile Organic Compounds (VOC) | N |  | 0.81 | TONS/YR |  | 0.19 | LB/H |  | 0.0055 | LB/MMBTU
OH-0309 | TOLEDO SUPPLIER PARK- PAINT SHOP | DAIMLER CHRYSLER CORPORATION | OH | OHIO ENVIRONMENTAL PROTECTION AGENCY | 2007-05-03 | 2007 | THIS IS A MODIFICATION TO A PREVIOUSLY ISSUED PERMIT TO DAIMLER CHRYSLER CORPORATION RBLC#OH-0280. AREA IS NON-ATTAINMENT FOR OZONE SO NOX AND VOC ARE BOTH CONSIDERED NON-ATTAINMENT AND NOX IS ALSO PSD. NOX HAS ONLY BEEN CHECKED AS LAER (WITH ONLY ONE CHO | BOILER (2), NATURAL GAS | 13.31 | NATURAL GAS | 20.4 | MMBTU/H | TWO BOILERS WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION. WITH #2 OIL BACKUP TWO SET OF LIMITS, THIS ONE FOR NATURAL GAS | Volatile Organic Compounds (VOC) | N |  | 0.11 | LB/H |  | 0.5 | T/YR |  | 0.0054 | LB/MMBTU |  | LIMITS ARE FOR EACH BOILER.
*AL-0231 | NUCOR DECATUR LLC | NUCOR CORPORATION | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-06-12 | 2007 | THE FACILITY PRODUCES STEEL COILS PRIMARILY FROM STEEL SCRAP USING THE ELECTRIC ARC FURNACE (EAF) PROCESS. | VACUUM DEGASSER BOILER | 13.31 | NATURAL GAS | 95 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N |  | 0.0026 | LB/MMBTU |  | 0.25 | LB/H
*AL-0231 | NUCOR DECATUR LLC | NUCOR CORPORATION | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-06-12 | 2007 | THE FACILITY PRODUCES STEEL COILS PRIMARILY FROM STEEL SCRAP USING THE ELECTRIC ARC FURNACE (EAF) PROCESS. | GALVANIZING LINE FURNACE | 13.31 | NATURAL GAS | 98.7 | MMBTU/H |  | Volatile Organic Compounds (VOC) | N |  | 0.0055 | LB/MMBTU |  | 0.54 | LB/H
IA-0088 | ADM CORN PROCESSING - CEDAR RAPIDS | ARCHER DANIELS MIDLAND | IA | IOWA DEPARTMENT OF NATURAL RESOURCES | 2007-06-29 | 2007 | CONSISTS OF THREE DISTINCT OPERATIONS: CORN WET MILL, CORN DRY MILL AND BOILERHOUSE | INDIRECT-FIRED DDGS DRYER | 13.31 | NATURAL GAS | 93.7 | MMBTU/H | PROJECT INCLUDES THE INSTALLATION OF EIGHT IDENTICAL DDGS DRYERS. PERMITS 07-A-546-P, 547, 548, 549, 550, 557, 558 AND 559. THE COMBUSTION CHAMBER AND THE FEED CHAMBER ARE SEPERATED BY A HEAT EXCHANGER. THE DRYERS CAN FIRE NATURAL GAS, BIOGAS FROM THE WWT | Volatile Organic Compounds (VOC) | A | ROUTE PROCESS OFF-GASSES THROUGH THE DRYERS COMBUSTION CHAMBER. | 98 | % REDUCTION | AVERAGE OF 3 TEST RUNS | 3.16 | LB/H | AVERAGE OF 3 TEST RUNS |  |  |  | THE LIMITS ARE WRITTEN AS 98% REDUCTION ACROSS THE DRYER COMBUSTION CHAMBER AND 3.16 LB/HR AT THE OUTLET OF THE DRYER. THE POUND PER HOUR LIMIT IS MEASURED AS THE SUM OF THE METHOD 18 OR METHOD 320 RESULTS.
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED BATCH ANNEALING FURNACE (535) | 13.31 | NATURAL GAS | 99 | MMBTU/H | THIS PROCESS IS COVERED UNDER 503-0095-X005. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Volatile Organic Compounds (VOC) | N |  | 0.0055 | LB/MMBTU |  | 0.55 | LB/H
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED PASSIVE ANNEALING FURNACE (LO41) | 13.31 | NATURAL GAS | 27.2 | MMBTU/H | THIS PROCESS IS COVERED UNDER 503-0095-X013. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Volatile Organic Compounds (VOC) | N |  | 0.0055 | LB/MMBTU |  | 0.15 | LB/H
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | NATURAL GAS-FIRED BATCH ANNEALING FURNACES (LA63, LA64) | 13.31 | NATURAL GAS | 33.4 | MMBTU each | THIS PROCESS IS COVERED UNDER 503-0095-X014. PLEASE SEND ANY QUESTIONS TO CHARLES KILLEBREW, ADEM PERMIT ENGINEER. | Volatile Organic Compounds (VOC) | N |  | 0.0055 | LB/MMBTU |  | 0.18 | LB/H
*AL-0230 | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | THYSSENKRUPP STEEL AND STAINLESS USA, LLC | AL | ALABAMA DEPT OF ENVIRONMENTAL MGMT | 2007-08-17 | 2007 | A NEW CARBON STEEL AND STAINLESS STEEL MILL TO PRODUCE VARIOUS GRADES AND/OR TYPES OF STEEL IN VARIOUS FORMS (COILS, SLITS, SHEETS, ETC.) | 3 NATURAL GAS-FIRED BOILERS WITH ULNB & EGR (537-539) | 13.31 | NATURAL GAS | 64.9 | MMBtu each | THIS PROCESS IS COVERED UNDER 503-0095-X026. | Volatile Organic Compounds (VOC) | N |  | 0.0055 | LB/MMBTU |  | 0.36 | LB/H
| NOX | Number | lb/mmbtu
1997 | 1.2144 | 26 | 0.046708
1998 | 0.99998 | 14 | 0.071427
1999 | 1.1578 | 20 | 0.05789
2000 | 1.6164 | 34 | 0.04754
2001 | 3.9188 | 52 | 0.075362
2002 | 2.38 | 43 | 0.055349
2003 | 2.0398 | 26 | 0.078454
2004 | 2.5371 | 29 | 0.087487
2005 | 0.545 | 9 | 0.060556
2006 | 0.101 | 4 | 0.02525
2007 | 0.687 | 11 | 0.062455
268